## Slide 1: Design of water and wastewater networks for the neighborhood of Rawabi city
Prepared by:
Shatha Zaid Rahaf Bsharat
Ashraf Taha Noor Surakji
Submitted to:
Dr.Abdel-Haleem Khader

## Slide 2: Outline
Objectives
Introduction
Methodology
Result & Conclusion
Modeling , Analyzing & Design
Study area

## Slide 3: Introduction
Water take a great importance to humans in everyday life most of the activities we do need water. So that demand is continuously increasing, this means increasing the wastewater production, where wastewater constitutes about (80%-90%) of water demand

## Slide 4: Objectives
Design of Wastewater collection network that have life period of 30 years.
Design of Water distribution network that have life period of 30 years.

## Slide 5
Study Area

## Slide 6: Location

## Slide 7: Population
According to master plan from Municipality the neighborhood consists of 10 buildings, with 379 apartments, which are planned for 5 persons for each.
Total population = No. of apartment * No. of capita per apartment
= 379 * 5
= 1895 capita

## Slide 8: Land Use
The land use patterns in this neighborhood is residential
Climate
The city is characterized by its Mediterranean climate, In summer, the average temperature is about 22 degree, with a humidity percentage of 55%. On the other hand, the average temperature drops to 8.5 degree in winter
Rawabi has an average annual precipitation of 600 mm

## Slide 9
Topography
The elevation of the neighborhood is within 645 m to 675 m above mean sea level.
Water resources
Rawabi city take water from the reservoir existing in the south of the city, which is far 1240 meters from the neighborhood .

## Slide 10: MODELING , ANALYSIS AND DESIGN

## Slide 11: Thirdly, we drew the nodes, manholes and pipes of the networks on the map. Fourthly, we inserted the elevation of nodes and manholes manually in the programs. Finally, we calculated the demand for each node and manhole, and then we inserted these values in programs
The procedure steps of design water & wastewater network
first of all we start the WaterCad & SewerCad program and import all the files necessary for design
for the analysis of watercad network we used the pressure found in the entrance of the neighborhood and we designed based on it instead of the reservoir.

## Slide 12: Water demand represents the necessary minimum amount of water sufficient to meet the basic needs for drinking and residential water losses

## Slide 13: From master plan and some assumption; • The neighborhood has 10 buildings with number of floors & apartments. • Total number of apartments = 379 • Each apartment has population equal 5 capita. • Total population = No. of apartment * No. of capita per apartment = 379 * 5 = 1895 capita • The consumption per capita equal 120 L/capita.day including all losses in the network • Maximum hour factor in WaterCad = 1.8

## Slide 14: Total demand for WDN = Total population * 120 L/c. d * maximum hour factor = 1895 * 120 * 1.8 * 10^(-3) = 409.32 m^3/day Peak factor in SewerCad (PK) = (3-4) (PK) =5/P^(1/6) P: population in thousands = 4.49 > 4 so we take PK = 4

## Slide 15: Return fraction of wastewater (RF) = (0.8-0.85), we take 0.85 Infiltration rate (IR) = 20% Total demand for WWCN = (Total population *120 L/c. d * RF* PF +Total population*120 L/c. d * RF * IR) * 10^(-3) = 1895 * 120 * 0.85 * 4 + 1895 * 120 * 0.85 * 0.2 = 811.818 m^3/day

## Slide 16: Wastewater collection network

## Slide 17: Water distribution network

## Slide 18: Water distribution network

## Slide 19: Results and Conclusions
Water Distribution Network:
- Pressure:
Allowable Range:
(20-100) m H2O
Chart: 
| J-1 | J-2 | J-3 | J-4 | J-5 | J-6 | J-7 | J-8
 | 86 | 89 | 91 | 89 | 94 | 94 | 93 | 90

## Slide 20: Results and Conclusions
Water Distribution Network:
- Velocity:
Allowable Range:
(0.3-3) m/s
Chart: Pipes


Y-Values | 0.46 | 0.94 | 1.53 | 1.16 | 0.96 | 0.7 | 0.45 | 0.3

## Slide 21: Results and Conclusions
Wastewater Network:
- Velocity:
Allowable Range:
(0.6-3) m/s
Chart: Conduits



Y-Values | 0.68 | 0.86 | 0.97 | 0.8 | 1.05 | 1.05 | 1.08 | 1.38 | 2.09 | 1.02 | 0.91 | 0.86 | 0.94 | 0.89

## Slide 22: Results and Conclusions
Wastewater Network:
- Slope:
Allowable Range:
(1-15) %
Chart: Conduits




Y-Values | 3.28 | 3.421 | 3.354 | 1.476 | 2.681 | 2.624 | 2.543 | 4.596 | 15 | 1.786 | 7.631 | 1 | 1 | 1

## Slide 23: Results and Conclusions
Wastewater Network:
- Cover depth:
Allowable Range:
(0.5-5) m
Chart: Conduits





Y-Values | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 2.67 | 0.5 | 0.76 | 0.63 | 1.005 | 0.89

## Slide 24: Results and Conclusions
Changing the diameters Adjusting the pressure, velocity, slope and cover depth.
Our design is applicable and serviceable for the selected design period: around 30 years.
We recommended going ahead with this project.