## Slide 1: An-Najah National University Faculty of Engineering
Graduation Project Report II
SEISMIC DESIGN OF ALBEZREH BUILDING IN NABLUS
Supervisor: Dr. Riyad Awad
Prepared by:
Ahmad Ismail
Mohammad Issa
Hazem qaisi

## Slide 2: Outline:
Introduction.
3D model.
SEISMIC Design.
Design of shear wall.
Design of Stairs.
Design of Mat foundation .

## Slide 3: Introduction
Our building (Nihad Albezre building) is located in Nablus city.
The building is composed of two blocks. (Block1 & Block2)
Each block has 12 stories.
The total area of the structure is approximately 12300 .

## Slide 5: Project description. (Storage story)

## Slide 6: Project description. (Exhibition story)

## Slide 7: Project description. (Apartments story)

## Slide 8: Description of stories
Story | Elevation (m) | Area (𝑚2)
4th Basement | -13.8 | 1414.25
3rd Basement | -10 | 1414.25
2nd Basement | -3.00 | 1271.10
1st Basement | 0.00 | 1271.10
Ground Floor | +3.5 | 1013.09
String Floor | +6.5 | 1195.28
1st Floor | +9.75 | 1013.09
2nd Floor | +13.00 | 1013.09
3rd Floor | +16.25 | 1050.17
4th Floor | +19.50 | 1050.17
5th Floor | +22.75 | 1050.17
6th Floor | +26.50 | 851.38
Stairs floor | +29.50 | 109.73
Summation |  | 12302.62

## Slide 9: Introduction:
Geotechnical information:
Soil layers are close to be soft stone so the design bearing capacity is
Codes and Standards:
  IBC 2012 (International Building Code)
  ACI 318M-14 (American Concrete Institute) Building code requirements for structural concrete
  UBC 97 (European Building Code)

## Slide 10: Introduction:
Materials:
Rebar Steel: Yielding strength of used steel (fy) = 420MPa.
Concrete: strength: 30 MPa

## Slide 11: Introduction:
Programs:
1- ETABS 2016
2- Safe
3- AutoCAD
4- Excel

## Slide 12: DRAW 3D MODEL, AND CHECKS

## Slide 13: Thickness of slab:
Thickness for Solid slab = 27 cm
Thickness for Ribbed slab = 30 cm

## Slide 14: Section of ribbed slab:

## Slide 15: properties and details of the 1st block slabs:
Story | Height | Elevation | Area | Type of slab | Thickness of Slab | Function
 | m | m | m2 |  | mm | 
Story 13 | 3.5 | 43.2 | 34.68 | Solid | 150.00 | Stairwell
Story 12 | 3.25 | 39.7 | 457.55 | Ribbed | 300.00 | Apartments
Story 11 | 3.25 | 36.45 | 457.55 | Ribbed | 300.00 | Apartments
Story 10 | 3.25 | 33.2 | 457.55 | Ribbed | 300.00 | Apartments
Story 9 | 3.25 | 29.95 | 457.55 | Ribbed | 300.00 | Apartments
Story 8 | 3.25 | 26.7 | 457.55 | Ribbed | 300.00 | Apartments
Story 7 | 3.25 | 23.45 | 456.96 | Solid | 270.00 | Exhibition
Story 6 | 3 | 20.2 | 456.96 | Solid | 270.00 | Stowage
Story 5 | 3.5 | 17.2 | 456.96 | Solid | 270.00 | Stowage
Story 4 | 3 | 13.7 | 604.43 | Solid | 270.00 | Garage
Story 3 | 3.2 | 10.7 | 604.43 | Solid | 270.00 | Garage
Story 2 | 3.8 | 7.5 | 709.71 | Solid | 270.00 | Garage
Story 1 | 3.7 | 3.7 | 709.71 | Solid | 270.00 | Garage

## Slide 16: properties and details of the 2nd block slabs:
Story | Height | Elevation | Area | Type of slab | Thickness of Slab | Function
 | m | m | m2 |  | mm | 
Story 13 | 3.5 | 43.2 | 32.34 | Solid | 150.00 | Stairwell
Story 12 | 3.25 | 39.7 | 697.72 | Ribbed | 300.00 | Apartments
Story 11 | 3.25 | 36.45 | 691.19 | Ribbed | 300.00 | Apartments
Story 10 | 3.25 | 33.2 | 691.19 | Ribbed | 300.00 | Apartments
Story 9 | 3.25 | 29.95 | 691.19 | Ribbed | 300.00 | Apartments
Story 8 | 3.25 | 26.7 | 691.19 | Ribbed | 300.00 | Apartments
Story 7 | 3.25 | 23.45 | 634.81 | Solid | 270.00 | Exhibition
Story 6 | 3 | 20.2 | 546.80 | Solid | 270.00 | Stowage
Story 5 | 3.5 | 17.2 | 634.55 | Solid | 270.00 | Stowage
Story 4 | 3 | 13.7 | 769.06 | Solid | 270.00 | Garage
Story 3 | 3.2 | 10.7 | 719.99 | Solid | 270.00 | Garage
Story 2 | 3.8 | 7.5 | 719.99 | Solid | 270.00 | Garage
Story 1 | 3.7 | 3.7 | 308.49 | Solid | 270.00 | Garage

## Slide 17: Frame Sections:
Name | Material | Shape | t3 | t2 | Area
 |  |  | mm | mm | cm²
Beam 15*30 | 30MPa | Concrete Rectangular | 150 | 300 | 450
Beam 15*70 | 30MPa | Concrete Rectangular | 150 | 700 | 1050
Beam 27*25 | 30MPa | Concrete Rectangular | 270 | 250 | 675
Beam 27*40 | 30MPa | Concrete Rectangular | 270 | 400 | 1080
Beam 27*50 | 30MPa | Concrete Rectangular | 270 | 500 | 1350
Beam 27*60 | 30MPa | Concrete Rectangular | 270 | 600 | 1620
Beam 27*70 | 30MPa | Concrete Rectangular | 270 | 700 | 1890
Beam 27*90 | 30MPa | Concrete Rectangular | 270 | 900 | 2430
Beam 30*25 | 30MPa | Concrete Rectangular | 300 | 250 | 750
Beam 30*60 | 30MPa | Concrete Rectangular | 300 | 600 | 1800
Beam 60*40 | 30MPa | Concrete Rectangular | 600 | 400 | 2400
Beam 60*50 | 30MPa | Concrete Rectangular | 600 | 500 | 3000
Beam 60*60 | 30MPa | Concrete Rectangular | 600 | 600 | 3600
Beam 60*70 | 30MPa | Concrete Rectangular | 600 | 700 | 4200
Beam 60*80 | 30MPa | Concrete Rectangular | 600 | 800 | 4800
Beam 60*90 | 30MPa | Concrete Rectangular | 600 | 900 | 5400
Beam 70*50 | 30MPa | Concrete Rectangular | 700 | 500 | 3500
Beam 70*60 | 30MPa | Concrete Rectangular | 700 | 600 | 4200
Beam 70*70 | 30MPa | Concrete Rectangular | 700 | 700 | 4900
Beam 70*80 | 30MPa | Concrete Rectangular | 700 | 800 | 5600
Beam 80*100 | 30MPa | Concrete Rectangular | 800 | 1000 | 8000
Beam 80*60 | 30MPa | Concrete Rectangular | 800 | 600 | 4800
Column100 | 30MPa | Concrete Circle | 1000 |  | 7854
Column 100*30 | 30MPa | Concrete Rectangular | 1000 | 300 | 3000
Column 70*40 | 30MPa | Concrete Rectangular | 700 | 400 | 2800
Column 70*60 | 30MPa | Concrete Rectangular | 700 | 600 | 4200

## Slide 18: Modifiers for Slabs, Beams and Columns:
Name | A Modifier | AS2 Modifier | AS3 Modifier | J Modifier | I22 Modifier | I33 Modifier | Mass Modifier | Weight Modifier
Solid Slab | 1 | 1 | 1 | 0.25 | 0.0025 | 0.0025 | 1 | 1
Ribbed Slab | 1 | 1 | 1 | 0.25 | 0.25 | 0.0025 | 1 | 1
Beam | 1 | 1 | 1 | 0.35 | 0.35 | 0.35 | 1 | 1
Column | 1 | 1 | 1 | 0.7 | 0.7 | 0.7 | 1 | 1

## Slide 19: 3D model:
Block1

## Slide 20: 3D model:
Block2

## Slide 21: 3D model:
Checks
1- Compatibility check:

## Slide 22: 3D model:
Checks for block1.
2- equilibrium check: ETABS Z-direction forces reactions.

## Slide 23: 3D model:
Checks
2- Hand calculations of forces reactions, and errors. Live load: 30622.5 KN
SD: 16065 KN
Dead load: 76393.2 KN

## Slide 24: 3D model:
Checks
3- stress strain check:

## Slide 25: 3D model:
Checks
4- Deflection check:
The long-term deflection = 25.6 mm.
The allowable deflection = 32.7 mm.
32.7 mm > 25.6 mm. OK

## Slide 26: DEFINE SEISMIC PARAMETERS IN “ETABS” PROGRAM, AND CHECKS

## Slide 27: Determination of seismic parameters:
Seismic Zone factor (Z) :
Nablus city which is in Zone 2B, and has Z = 0.2 g

## Slide 28: Determination of seismic parameters:
Site classifications :
bearing capacity as 250 KN/m2 >> soil is classified as Sc

## Slide 29: Determination of seismic parameters:
Determine seismic coefficients Ca and Cv:
Ca = 0.24 Cv = 0.32

## Slide 30: Determination of seismic parameters:
Determine seismic importance factor, I:
Use I = 1.00

## Slide 31: Determination of seismic parameters:
Determination of Response Modification Coefficient, R:
Use R= 5.5

## Slide 32: Define Response Spectrum Function at Etabs:

## Slide 33: Define mass source:

## Slide 34: Define load case’s (Earthquake) for Block1:
Scale Factor
= gI/R = 9810 * 1 /5.5
= 1783.63

## Slide 35: Define load case’s (Earthquake) for Block1:

## Slide 36: Check Modal Participation Mass Ratio

## Slide 37: Period check
Method A:
1.133 sec < 1.1512 sec that’s OK
Method B (Etabs result):

## Slide 38: Base Shear check:
 | T | V | Etabs Result | OK or NOT
x-direction | 0.882 | 5866.21 | 6126.92 | OK
y-direction | 1.133 | 4566.63 | 5169.77 | OK

## Slide 39: Check drift:
Allowable drift
= story hight / 500
Min. high = 3.25 m
Allowable drift = 3.25/500
= 0.0065
As shown, Max. drift
= 0.0021 < 0.0065 >>> OK

## Slide 40: Design Frames for the two Blocks

## Slide 41: Design Code

## Slide 42: Frame type

## Slide 43: Combination used

## Slide 44: Design result for Block1

## Slide 45: Design result for Block2

## Slide 46: Typical Concrete Beam

## Slide 47: Typical Concrete Column

## Slide 48: Design Slabs for Block1

## Slide 49: Design of slabs:
Strips properties for solid slab.
at x-direction
at y-direction

## Slide 50: Design of slabs:
Strips properties for ribbed slab.
at x-direction
at y-direction

## Slide 51: Strips A and B for story1 (solid slab)

## Slide 52: Strips A and B for story8 (ribbed slab)

## Slide 53: Flexure design for story1 slab (solid slab)

## Slide 54: Shear design for story1 slab (solid slab)

## Slide 55: Flexure design for story8 slab (ribbed slab)

## Slide 56: Flexure design for story8 slab (ribbed slab)

## Slide 57: Cross sections for solid and ribbed slabs

## Slide 58: Design of shear wall

## Slide 59: Location of the shear wall to be designed. (SW1)

## Slide 60: Shear wall dimensions. Length = 5200mm. Thickness = 200mm Ultimate Internal Forces from ETABS Mmajor = 1170KN.m, Pu = 1476 KN Mminor = 55 KN.m, Vumajor = 327 KN, Vuminor =42 KN

## Slide 61: Total Area of rebar = 5025mm2 (2512.5mm2 in each layer).
Longitudinal bars of diameter Ø12mm are used.
Spacing = Use 1Ø12/200mm in each layer

## Slide 62
As shown in , the ultimate major bending moment (Mu=1170KN) and ultimate axial force (Pu=1476KN) lies inside the interaction curve, which means the design is safe and no additional reinforcement is required in longitudinal direction.

## Slide 63: Cross section of shear wall

## Slide 64: Design of Stairs

## Slide 65: Design of landing
1 Ø12 /20 cm bottom steel
1 Ѳ12 /25 cm top steel

## Slide 66: Design of soffit
1 Ø10 /20 cm bottom steel
1 Ѳ 8 /15 cm top steel

## Slide 67: Cross section of stairs

## Slide 68: Design of Mat foundation by Safe

## Slide 69: Plan view

## Slide 70: Check for deflection

## Slide 71: Check for soil pressure

## Slide 72: Check footing thickness based on punching shear

## Slide 73: Design for shear
No need for shear reinforcement

## Slide 74: Design for flexure

## Slide 75: Thanks