## Slide 1: Power factor correction by Static Variable Compensator (SVC) Supervised by: Dr. Kamel Saleh

## Slide 2
* Overview
* Project overall
* PF meter
* Calculation of firing angle
* Generation of firing angle
* Results
* Comparison
* Problems
Content

## Slide 3: * Overview

## Slide 4: * Overview
This method uses only one capacitor bank and we control the PF by changing the RMS voltage applied to the capacitor other than controlling capacitance value.

## Slide 5: Overview

## Slide 6: Project overall
The project consists of two main parts : 1 – Power Factor Meter.
2 – Compensation controller.

## Slide 8: PF meter
* There is two main ways to calculate the PF
* first method use the real and reactive power as shown in the following equation
* the second method use the time shift between the the current and the voltage

## Slide 9: PF meter
In our project the first mission is to find the phase shift between the voltage and the current
We could achieve this step using help of Zero Crossing Detector

## Slide 10: PF meter
Zero Crossing Detector

## Slide 11: PF meter
The zero cross detection is a circuit that gives a pulse as indication when the input voltage waveform crosses the zero axis
Zero Crossing Detector

## Slide 12: PF meter
The zero cross detection output for both voltage and current will be the inputs for the Arduino microcontroller to calculate the power factor of the load
Zero Crossing Detector

## Slide 13: PF meter
The arduino program performs the following tasks
1- counting the time between Voltage and Current pulses of zero crossing detector
2- determines the phase shift from the counted time
3- determines the PF from the phase shift
Arduino

## Slide 14: Calculation of firing angle
*firing angle should be the output of the controller, so it should be calculated
* Open loop method is used
*We made some assumptions which are
-Pload -Vbus -Qload are constants

## Slide 15: Calculation of firing angle
Procedures of determining the value of alfa

## Slide 16: Calculation of firing angle
*Numerical method which is Bi-sectional Method use number of iteration to find the value of alfa until the different between the previous value and the current value will be less than the specific value
* This method is very practical in our situation because it can reach a good value of alfa after 10 iterations with very low
percentage of error
Numerical method
Number of iterations | Max Error (%) | Max Error (degree)
1 | 50 | 90
10 | 0.097 | 0.1746

## Slide 17: Calculation of firing angle
* In this method the measured PF of the load is divided
into intervals
*according to each interval, a specific firing angle is determined
* When number of intervals is increased, the accuracy of determining the value of alfa is increased
* The compiler takes too small time to perform this method with respect to the numerical method
Intervals methods

## Slide 18: Generation of firing angle
*From the calculated firing angle we transform this angle to a time value
*The time of firing angle should be related to the to the instant time when the voltage cross the zero axis
*So the generated firing angle to the triac should be synchronized with the zero crossing detector pulse of the voltage

## Slide 20: Results
The results of the project will be shown in videos

## Slide 21: Comparison
problems in the ordinary method do not exist in our method
* improvement of PF in steps
* Life time is decreased by increasing the voltage
* As the V  Qc  V
*As the V  Qc  V

## Slide 22: Comparison
After achieving the technical requirements, there is the economical advantages compared with the ordinary method :-
* Less cost of the capacitor banks
* No contactors requires
* Easy maintenance

## Slide 23: Closed loop system
*Our project can be simply done by closed loop method
*The close loop controller is much easier than open loop
*In this method we only need PF meter which is built in this semester

## Slide 24: Closed loop system
* System keeps adjusting the value of alfa until the measured PF of the load equal to reference PF , then means we don’t have to make any assumption to any value and the response will be more accurate
*No need to know the real power, reactive power or voltage at the bus of the load
*Simulation of close loop method was done last semester

## Slide 25: Problems
Problems we faced:
*We could not use a closed loop system because we couldn’t find potential and current transformers
*We couldn’t find PF meter so we built one

## Slide 26: Problems
Problems may the project face:
The main problem is the harmonics
* harmonics might be a problem for certain loads
*harmonics is a problem to the capacitor bank itself

## Slide 27: *Full Simulation of the project