## Slide 1
Design of a Rehabilitation Center for People
with Special Needs in Nables city.
AN-Najah National University
Building Engineering Department
Group members:
Zaid Bozeyeh Bara Kabaha
Mahmoud Soleiman Mohammad Ameen
Supervisor Name: - Haitham Sawalha
Faculty of Engineering & Information Technology
1

## Slide 2
Introduction
1
Site analysis
2
Architectural aspects
Structural aspects
Environmental aspects
3
4
5
6
Mechanical aspects
Electrical aspects
7
8
Quantity surveying
Table of Contents
2

## Slide 3
In most of the designs for buildings in our community, the special needs category was ignored. In the west bank we have approximately 1500 people with special need , the project idea came to serve largest possible number of them .
Chart: percentage of special needs category
| special needs category in the West Bank 5.1% | Palestinian society
percentage of special needs category | 5.1 | 94.9
Introduction
3

## Slide 4
Location : It is located in East of Nables city near the Hesgham Hejawi Collage
and Shaikh Khalefa Training Center.
Site Area : 19000 m2.
4
Site analysis

## Slide 5
5
Site analysis

## Slide 6
Architectural aspects
6

## Slide 7
First floor
5700 m2
second floor area
7000 m2
Third floor area
5200 m2
Forth floor area
5200 m2
Ground floor area
6700 m2
Basement
2300 m2
- 5 floors, in addition to basement
as a parking
- serves 800 people
- Total area of the building equals
to 32100 m2
7
Architectural aspects
Project Description

## Slide 8
8
Architectural aspects
Project plans
Basement Floor plan
Ground Floor plan

## Slide 9
9
First floor plan
Second floor plan
Architectural aspects
Project plans

## Slide 10
Third floor plan
Fourth floor plan
Architectural aspects
Project plans
10

## Slide 11
Architectural aspects
Project plans
Site plan
11

## Slide 12
East elevation
West elevation
12
Architectural aspects
Project Elevations

## Slide 13
North elevation
South elevation
13
Architectural aspects
Project Elevations

## Slide 14
Section A-A
Section B-B
14
Architectural aspects
Project Sections

## Slide 15
Section C-C
Section D-D
15
Architectural aspects
Project Sections

## Slide 16
Section E-E
Section F-F
16
Architectural aspects
Project Sections

## Slide 17
Width : for normal people 2.5m , for special needs 3.5m
Number of parking : 89 parking spaces shown in basement and site plan
17
Architectural aspects
Parking
Interior Parking in Basement plan
Exterior Parking in Site plan

## Slide 18
Structural Elements
Mat foundation
Shear walls
Columns
Slabs
Beams
Stairs and Ramps
Retaining walls
Water tanks
Structural aspects
18

## Slide 19
Structural aspects
Materials:
Concrete with compressive strength f`c=28 MPa.
Yield Strength of Steel Fy= 420 MPa.
Bearing capacity of soil = 150 KN/m².
Loads:
Live load = 5 𝐾𝑁/m².
SI.Dead load = 4 𝐾𝑁/m²
External wall load = 26 KN/m
Standards/Codes:
→ The American concrete institute code ACI 318-08
for reinforced concrete design
→ The Uniform Building Code -UBC-97
for seismic design and its load combinations
19
General Information

## Slide 20
Structural aspects
Seismic analysis:
Seismic zone : 2B with (Z = 0.20) .
Soil profile : SD.
Acceleration-dependent seismic coefficients Ca=0.28.
Velocity-dependent seismic coefficients Cv= 0.40.
Importance factor I=1.
Force reduction factor R=5.5
20

## Slide 21
Structural aspects
Due to the size of the building, the building will be divided it into eight parts to create an expansion joints.
21

## Slide 22
ETABS Model
Structural aspects
ETABS Model for Block C
ETABS Model for Block D
ETABS Model for Block E
22

## Slide 23
ETABS Checks
To ensure that the calculation is done correctly from ETABS; some checks are required :
ETABS Checks
Compatibility check
Internal force check
Deflection check
Drift check
Period check
Equilibrium check
(MPMR) check
Base Shear check
Structural aspects
23

## Slide 24
ETABS Checks
Compatibility check
Structural aspects
24
The whole structural elements move as one body
3D model for Block C
3D model for Block D
3D model for Block E

## Slide 25
ETABS Checks
Equilibrium check
Structural aspects
25
 | Column | Beam | Slab
For Block C | 6.52% | 4.21% | 16.80%
For Block D | 8.07% | 15.34% | 10.39%
For Block E | 4.77% | 1.89% | 5.64%
Internal force check
 | Dead load | Live load | SID load
For Block C | 3.61% | 0.02% | 2.35%
For Block D | 4.45% | 0.04% | 1.02%
For Block E | 0.02% | 0.01% | 0.01%
This check done for Dead, SID and Live load within difference less than 5 %.
This check done for columns, beams and slabs within difference less than 10 %.
Table 1: Equilibrium check with error %
Table 2: Internal force check with error %

## Slide 26
ETABS Checks
Deflection check
Structural aspects
26
Max deflection |  |  | 
 | ETABS | Limit | 
For Block C | 17.7 mm | 37.5 mm | 
For Block D | 37 mm | 60 mm | 
For Block E | 61.5 mm | 62.5 mm | 
Long-term deflection limit = L/240
Period check
T method A =Ct
T limit = 1.4 * T method A
ETABS in x and y- Axes should not exceed UBC code limit
 | T Method A | 1.4 x T Method A | T ETABs x-axis | T ETABs y-axis
Period for Block C | 0.504 sec | 0.7056 sec | 0.686 sec | 0.572 sec
Period for Block D | 0.504 sec | 0.7056 sec | 0.691 sec | 0.521 sec
Period for Block E | 0.504 sec | 0.7056 sec | 0.686 sec | 0.572 sec
Table 3: Deflection check
Table 4: Period check

## Slide 27
ETABS Checks
Drift check
Structural aspects
27
Story | Height | Displacement in X- axis | Displacement in Y- axis | Drift X | Drift Y | Delta X | Delta Y | Delta Limit
0 | 0 | 0 | 0 |  |  |  |  | 
1 | 4500 | 1.52 | 1.27 | 1.52 | 1.27 | 5.86 | 4.9 | 90
2 | 4500 | 4.03 | 3.28 | 2.5 | 2.01 | 15.5 | 12.64 | 90
3 | 4500 | 7.41 | 5.46 | 3.38 | 2.18 | 28.53 | 21.03 | 90
4 | 4500 | 10.88 | 7.97 | 3.47 | 2.51 | 41.88 | 30.7 | 90
5 | 4500 | 13.97 | 10.27 | 3.09 | 2.3 | 53.77 | 39.54 | 90
ΔM (Drift) =0.7 * R * Δ s
Drift limitation = 2 % times the story height.
Table 5: Drift check for Block C

## Slide 28
ETABS Checks
Modal mass participate ratio check (MPMR) check
Structural aspects
28
The MMPR check according to UBC code must be greater than 90% to use response spectrum analysis.
Case | Mode | Period | UX | UY | UZ | Sum UX | Sum UY | Sum UZ
 |  | sec |  |  |  |  |  | 
Modal | 1 | 0.64 | 0.7 | 0.04 | 0 | 0.7 | 0.04 | 0
Modal | 2 | 0.5 | 0.04 | 0.73 | 0 | 0.74 | 0.76 | 0
Modal | 3 | 0.38 | 0.02 | 0 | 0 | 0.76 | 0.76 | 0
Modal | 4 | 0.36 | 0 | 0 | 0 | 0.76 | 0.77 | 0
Modal | 5 | 0.29 | 0 | 0 | 0 | 0.76 | 0.77 | 0
Modal | 6 | 0.28 | 0 | 0 | 0 | 0.76 | 0.77 | 0
Modal | 7 | 0.27 | 0 | 0 | 0 | 0.76 | 0.77 | 0
Modal | 8 | 0.24 | 0 | 0 | 0 | 0.76 | 0.77 | 0
Modal | 9 | 0.21 | 0 | 0 | 0 | 0.76 | 0.77 | 0
Modal | 10 | 0.17 | 0.15 | 0.01 | 0 | 0.91 | 0.78 | 0
Modal | 11 | 0.16 | 0 | 0.03 | 0 | 0.91 | 0.81 | 0
Modal | 12 | 0.15 | 0.01 | 0.07 | 0 | 0.92 | 0.88 | 0
Modal | 13 | 0.15 | 0 | 0 | 0 | 0.92 | 0.88 | 0
Modal | 14 | 0.14 | 0 | 0.01 | 0 | 0.93 | 0.89 | 0
Modal | 15 | 0.13 | 0 | 0 | 0 | 0.93 | 0.89 | 0
Modal | 16 | 0.13 | 0 | 0.02 | 0 | 0.93 | 0.91 | 0
Table 6: MPMR check for Block C

## Slide 29
ETABS Checks
Base Shear check
Structural aspects
29
Axis | Period T (sec) | Period limit (sec) | Period use (sec) | Weight (kN) | V manual | V ETABs | Old S.F | new S.F
X-axis | 0.641 | 0.7056 | 0.641 | 117687.8 | 13352.75 | 9957.92 | 1783 | 2390.85
Y-axis | 0.499 | 0.7056 | 0.499 | 117687.8 | 14978.45 | 11031.3 | 1783 | 2420.98
Axis | Period T (sec) | Period limit (sec) | Period use (sec) | Weight (kN) | V manual | V ETABs | Old S.F | new S.F
X-axis | 0.691 | 0.7056 | 0.691 | 112592.9 | 11850.3 | 8807.4 | 1783 | 2399.03
Y-axis | 0.521 | 0.7056 | 0.521 | 112592.9 | 14330 | 9039.3 | 1783 | 2826.59
Axis | Period T (sec) | Period limit (sec) | Period use (sec) | Weight (kN) | V manual | V ETABs | Old S.F | new S.F
X-axis | 0.686 | 0.7056 | 0.686 | 30239.2 | 3205.852 | 3027.064 | 1783 | 1888.31
Y-axis | 0.572 | 0.7056 | 0.572 | 30239.2 | 3844.78 | 2025.312 | 1783 | 3384.78
For this check make sure base shear from response spectrum cases equal or more than base shear from equivalent static method through modifying scale factor.
Table 9: Base Shear check for Block E
Table 8: Base Shear check for Block D
Table 7: Base Shear check for Block C

## Slide 30
Design of structural elements
1. Slabs:
Structural aspects
30

## Slide 31
Design of structural elements
1. Slabs:
Structural aspects
31

## Slide 32
Design of structural elements
2. Beams:
Structural aspects
32
Section Name | material | Type
Frame 1 | Concrete 28Mpa | Hidden Beam
Frame 2 | Concrete 28Mpa | Hidden Beam
Frame 3 | Concrete 28Mpa | Drop and Hidden Beam
Frame 4 | Concrete 28Mpa | Drop and Hidden Beam
Frame 5 | Concrete 28Mpa | Drop and Hidden Beam
Frame 6 | Concrete 28Mpa | Drop and Hidden Beam
Frame 7 | Concrete 28Mpa | Hidden Beam
Frame 8 | Concrete 28Mpa | Hidden Beam
Frame 9 | Concrete 28Mpa | Hidden Beam
Frame 10 | Concrete 28Mpa | Drop and Hidden Beam
Table 10: Beam located in Block C

## Slide 33
Design of structural elements
2. Beams:
Structural aspects
33

## Slide 34
Design of structural elements
3. Columns:
Structural aspects
34

## Slide 35
Design of structural elements
3. Columns:
Structural aspects
35
Section Name | material | bars | stirrups | 
 |  |  | both sides area | central area
Column 900*600 | Concrete 28Mpa | 18ф20 | 2Ф10@100mm | 2Ф10@160mm
Column 800*600 | Concrete 28Mpa | 20ф18 | 3Ф10@100mm | 3Ф10@150mm
Column 700*700 | Concrete 28Mpa | 20ф18 | 3Ф10@100mm | 3Ф10@150mm
Column 600*500 | Concrete 28Mpa | 10ф20 | 2Ф10@100mm | 2Ф10@100mm
Table 11: columns located in Block C

## Slide 36
Design of structural elements
4. Shear walls:
Structural aspects
36

## Slide 37
Design of structural elements
6. retaining wall:
Structural aspects
37

## Slide 38
Design of structural elements
7. Mat foundation:
Structural aspects
38
Top reinforcement |  | Bottom reinforcement | 
in X-axis | in Y-axis | in X-axis | in Y-axis
1Ф25 @ 200 mm | 1Ф25 @ 150 mm | 1Ф25 @ 150 mm | 1Ф25 @ 150 mm

## Slide 39
Design of structural elements
7. Mat foundation:
Structural aspects
39
Top reinforcement |  | Bottom reinforcement | 
in X-axis | in Y-axis | in X-axis | in Y-axis
1Ф25 @ 200 mm | 1Ф25 @ 150 mm | 1Ф25 @ 150 mm | 1Ф25 @ 150 mm

## Slide 40
Design of structural elements
8. Stairs:
Structural aspects
40

## Slide 41
Design of structural elements
9. Ramps:
Structural aspects
41

## Slide 42
Design of structural elements
10. Water tank:
Structural aspects
42

## Slide 43
Environmental aspects
Material properties
Thermal behavior and
solar radiation
Acoustical design
Daylighting factor
Shading design
Ventilation
43

## Slide 44
Environmental aspects
Material properties
External Wall
Roof material
Internal wall
Glass type
44

## Slide 45
Environmental aspects
External Wall
Roof material
Internal wall
Glass type
45
Material properties

## Slide 46
Environmental aspects
Daylight Factor (DF)check:
For Fourth Floor:
Before Modification
After Modification
46

## Slide 47
Cooling load and heating load
Amount of Energy consumption in the building
Before Treatment
48
Environmental aspects
Thermal behavior and solar radiation:

## Slide 48
After Treatment
49
Environmental aspects
Thermal behavior and solar radiation:

## Slide 49
solar radiation for East Elevation
Before
50
Environmental aspects
Thermal behavior and solar radiation:

## Slide 50
Solar radiation for East Elevation
After
51
Environmental aspects
Thermal behavior and solar radiation:

## Slide 51
solar radiation for South Elevation
52
Environmental aspects
Thermal behavior and solar radiation:
= = 25 cm

## Slide 52
53
Environmental aspects
Ventilation and wind direction:

## Slide 53
In this project we solve the shading effects in summer and winter semester at three part of day (8:00 AM, 12:00PM, 4:00PM) as can see:
Shading in summer at 8:00AM
Shading in winter at 8:00AM
54
Environmental aspects
Shadow analysis:

## Slide 54
Shading in winter at 12:00PM
Shading in summer at 12:00PM
Shading in winter at 4:00PM
Shading in summer at 4:00PM
55
Environmental aspects
Shadow analysis:

## Slide 55
STC (Sound Transmission Class )
Internal partition
56
Acoustical design:
Environmental aspects

## Slide 56
STC (Sound Transmission Class )
External Wall
76 - 80 dBA
Where the outdoor background noise level is between 76 dBA and 80 dBA, then the OITC should be not less than 50
57
Acoustical design:
Environmental aspects

## Slide 57
IIC (Impact insulation Class )
FLOOR
IIC ratings for floor-ceiling assemblies above core learning spaces should be at least IIC-45 and preferably IIC-50 (measured without carpeting on the floor).
58
Acoustical design:
Environmental aspects

## Slide 58
Class room
 | SABINE
FREQ. | RT(60)
63Hz | 0.56 sec
125Hz | 0.59 sec
250Hz | 0.49 sec
500Hz | 0.60 sec
1kHz | 0.68 sec
2kHz | 0.69 sec
4kHz | 0.60 sec
8kHz | 0.43 sec
16kHz | 0.42 sec
Reverberation time (0.45-0.85 s)
59
Acoustical design:
Environmental aspects
 | SABINE
FREQ. | RT(60)
100Hz | 1.14 sec
125Hz | 1.14 sec
160Hz | 1.10 sec
200Hz | 1.06 sec
250Hz | 1.02 sec
315Hz | 1.03 sec
400Hz | 1.03 sec
500Hz | 1.04 sec
630Hz | 1.07 sec
800Hz | 1.10 sec
1000Hz | 1.12 sec
1250Hz | 1.13 sec
1600Hz | 1.14 sec
2000Hz | 1.15 sec
2500Hz | 1.14 sec
3150Hz | 1.11 sec
4000Hz | 1.07 sec
5000Hz | 1.00 sec
6300Hz | 0.91 sec
8000Hz | 0.84 sec
Reverberation time (0.8- 1.20 s)
Auditorium

## Slide 59
Class room
Recommendation AL for class room = < 7 %
Auditorium
Articulation loss(AL) :
Recommendation AL for Auditorium = < 7 %
61
Articulation loss(AL) :
Frequency | Articulation Loss
400Hz | 3.09
500Hz | 3.09
630Hz | 3.09
800Hz | 3.09
1000Hz | 3.09
1250Hz | 3.09
1600Hz | 3.09
2000Hz | 3.09
2500Hz | 3.09
Acoustical design:
Environmental aspects

## Slide 60
Mechanical aspects
60
Water system
Fire fighting system
Drainage system
HVAC System

## Slide 61
VRF system is used in this project
The below table give design capacity ,flow rate ,number of fan for all project.
63
Mechanical aspects
HVAC System

## Slide 62
Mechanical aspects
62
HVAC System
  Out door unit
  Fan coil unit
TOSHIBA selected company

## Slide 63
Mechanical aspects
63
HVAC System
  Diffuser
  Grilles

## Slide 64
Mechanical aspects
64
HVAC System
  Duct diameter for class room
  Table give Duct velocity, diameter and volumetric flow rate for fan coil and diffuser.

## Slide 65
Mechanical aspects
65
HVAC System
Diffuser and mechanical ventilation for ground floor

## Slide 66
Mechanical aspects
66
HVAC System
Diffuser and mechanical ventilation for first floor

## Slide 67
Diffuser and mechanical ventilation for second floor
Mechanical aspects
67
HVAC System

## Slide 68
Diffuser and mechanical ventilation for third floor
Mechanical aspects
68
HVAC System

## Slide 69
Diffuser and mechanical ventilation for fourth floor
Mechanical aspects
69
HVAC System

## Slide 70
 | Diameter (in)
Vertical | 2''
Horizontal | 1.5''
Meter | 2''
Branch | 3/4''
Mechanical aspects
71
Water system
The consumption of water based on ASHREA code = 43.1m3.

## Slide 71
type of pipes | Pipes Diameter (in) | Slope %
horizontal (sewer) | 2" | 2
horizontal (sewer) | 4" | 1
vertical (stack) | 4" | 0
vertical (vent) | 4" | 0
Mechanical aspects
72
Drainage system

## Slide 72
Calculation of pipes diameter for drainage water (waste water):
Mechanical aspects
Drainage system
73

## Slide 73
Mechanical aspects
74
Drainage system

## Slide 74
Sprinkler
Smoke Detector
House station
Fire Extinguisher (CO2)
Heat Detector
Fire fighting For Fourth plan
Mechanical aspects
75
Fire fighting system

## Slide 75
Mechanical aspects
75
Escape route for first floor

## Slide 76
Electrical Design
76
Distributions of Sockets
Lighting System
Loudspeakers

## Slide 77
Electrical Design
77
Lighting System:
DIALux program was used to design lighting system in project.
Arlight company used to selection luminaires .

## Slide 78
Electrical Design
78
Lighting System:
Room name | Uniformity | Required | Lux | Required | UGR
 |  | Uniformity |  | Lux | 
children play area | 0.74 | 0.33 | 334 | 300 | 20.9 < 22
secretary | 0.63 | 0 | 121 | 100 | 15.7 < 19
Archive | 0.64 | 0 | 103 | 100 | 14.4 < 25
offices | 0.6 | 0.33 | 177 | 150 | 16.9 < 19
printing | 0.64 | 0 | 104 | 100 | 15.1 < 19
human resources | 0.74 | 0.33 | 169 | 150 | 12.8 <19
volunteer unit | 0.74 | 0.33 | 170 | 150 | 12.7< 19
research unit | 0.74 | 0.33 | 170 | 150 | 12.6<19
financial unit | 0.74 | 0.33 | 171 | 150 | 12.6<19
director & meeting | 0.68 | 0.66 | 380 | 300 | 16.3<19
pharmacy | 0.73 | 0.33 | 306 | 300 | 16<19
product shop | 0.73 | 0.33 | 132 | 100 | 17.8<19
souvenir shop | 0.72 | 0.33 | 173 | 150 | 18 < 22
corridor bath | 0.57 | 0.5 | 122 | 100 | 13.3<25
baths | 0.78 | 0.5 | 160 | 150 | 10 < 25
corridor | 0.18 | 0.4 | 127 | 100 | 21<25
Inquiry | 0.71 | 0.5 | 186 | 150 | 17.1<19
Room name | Uniformity | Required | Lux | Required | UGR
 |  | Uniformity |  | Lux | 
store | 0.7 | 0.4 | 134 | 100 | 16.4<25
massage training | 0.62 | 0.6 | 345 | 300 | 17.4<19
trainer room | 0.63 | 0.6 | 306 | 300 | 13.4<19
tutorial room | 0.71 | 0.6 | 369 | 300 | 16<19
corridor bath | 0.57 | 0.5 | 122 | 100 | 13.3<25
baths | 0.78 | 0.5 | 160 | 150 | 10 < 25
corridor | 0.18 | 0.4 | 127 | 100 | 21<25
Room name | Uniformity | Required | Lux | Require | UGR
 |  | Uniformity |  | Lux | 
activity room | 0.4 | 0.33 | 419 | 400 | 18.8<19
tutorial room | 0.71 | 0.6 | 300 | 369 | 16<19
praying | 0.53 | 0.33 | 151 | 150 | 14.6<22
abolition | 0.42 | 0.33 | 114 | 100 | 13.9<22
back stage | 0.43 | 0.33 | 99 | 75 | 18.7<22
staff offices | 0.6 | 0.33 | 197 | 150 | 15.2<19
meeting | 0.69 | 0.66 | 340 | 300 | 16.3<19
corridor | 0.18 | 0.4 | 127 | 100 | 21<25
corridor bath | 0.57 | 0.5 | 122 | 100 | 13.3<25
baths | 0.78 | 0.5 | 160 | 150 | 10 < 25
Ground Floor
First Floor
Second Floor

## Slide 79
Electrical Design
79
Lighting System:
Third Floor
Fourth Floor
Room name | Uniformity | Required Uniformity | Lux | Required Lux | UGR
bed room | 0.64 | 0.4 | 141 | 100 | 15.1<22
laundry | 0.68 | 0.33 | 304 | 300 | 18.1<22
corridor bath | 0.57 | 0.5 | 122 | 100 | 13.3<25
baths | 0.78 | 0.5 | 160 | 150 | 10 < 25
corridor | 0.18 | 0.4 | 127 | 100 | 21<25
living | 0.46 | 0.1 | 124 | 100 | 18.4<22
bed room | 0.73 | 0.4 | 145 | 100 | 15.3<22
baths | 0.7 | 0.5 | 165 | 150 | 10 < 25
Room name | Uniformity | Required Uniformity | Lux | Required Lux | UGR
mobility training | 0.69 | 0.6 | 587 | 500 | 18.5<19
vip lounge | 0.48 | 0.4 | 69.7 | 50 | 19.1<22
tutorial room | 0.71 | 0.6 | 300 | 369 | 16<19
staff offices | 0.6 | 0.33 | 197 | 150 | 15.2<19
corridor bath | 0.57 | 0.5 | 122 | 100 | 13.3<25
baths | 0.78 | 0.5 | 160 | 150 | 10 < 25
light room | 0.71 | 0.33 | 129 | 100 | 19.4<22
speak training | 0.67 | 0.33 | 523 | 500 | 20<22
corridor | 0.18 | 0.4 | 127 | 100 | 21<25

## Slide 80
Electrical Design
80
Lighting System:

## Slide 81
Electrical Design
81
Distributions of Sockets
#Floor | #Socket | Power (KW)
ground | 37 | 20.8
First | 28 | 15.2
Second | 55 | 26
Third | 45 | 22
Fourth | 83 | 41.2
Total | 242 | 125.2
The power of sockets is estimated by 400 Watt for normal socket.
The power of Sockets is estimated by 2400 Watt for special load socket.

## Slide 82
Electrical Design
82
Distributions of Sockets

## Slide 83
Electrical Design
83
Calculation for drop voltage
Name | power | I L (Amp) | ρ (Ω.m) | L (m) | R(Ω) | drop voltage | % drop voltage
L1 | 421.9 | 2.02 | 1.68*108 | 44.4 | 0.50 | 1.01 | 0.46
L2 | 429.6 | 2.44 | 1.68*108 | 79 | 0.88 | 2.16 | 0.98
L3 | 429.6 | 2.44 | 1.68*108 | 69 | 0.77 | 1.89 | 0.86
L4 | 257.4 | 1.46 | 1.68*108 | 52.3 | 0.59 | 0.86 | 0.39
L5 | 458.4 | 2.60 | 1.68*108 | 62.4 | 0.70 | 1.82 | 0.83
L6 | 624 | 3.55 | 1.68*108 | 48.6 | 0.54 | 1.93 | 0.88
L7 | 312 | 1.77 | 1.68*108 | 73.4 | 0.82 | 1.46 | 0.66
L8 | 312 | 1.77 | 1.68*108 | 57.4 | 0.64 | 1.14 | 0.52
L9 | 214.8 | 1.22 | 1.68*108 | 144.2 | 1.62 | 1.97 | 0.90
L10 | 214.8 | 1.22 | 1.68*108 | 130 | 1.46 | 1.78 | 0.81
L11 | 179 | 1.02 | 1.68*108 | 112.4 | 1.26 | 1.28 | 0.58
L12 | 220.8 | 1.25 | 1.68*108 | 101.8 | 1.14 | 1.43 | 0.65
L13 | 400.4 | 2.28 | 1.68*108 | 80.6 | 0.90 | 2.05 | 0.93
L14 | 420 | 2.39 | 1.68*108 | 58.7 | 0.66 | 1.57 | 0.71
Drop voltage: The drop voltage should not exceed a certain value (usually 1%)
The cross sectional area for cable that use in lighting is 1.5 mm2.
Name
S2.D.B.G
S1.D.B.G

## Slide 84
Electrical Design
84
Drop voltage calculation
Drop voltage: The drop voltage should not exceed a certain value (usually 1%)
The cross sectional area for cable that use in sockets is 2.5 mm2.
Name | I load (Amp) | I actual | ρ (Ω.m) | L (m) | R(Ω) | drop voltage | % drop voltage
P1 | 8.00 | 2.40 | 1.72*108 | 62.2 | 0.43 | 1.03 | 0.47
P2 | 10.00 | 3.00 | 1.72*108 | 55.4 | 0.38 | 1.14 | 0.52
P3 | 10.00 | 3.00 | 1.72*108 | 68.5 | 0.47 | 1.41 | 0.64
P4 | 12.00 | 12.00 | 1.72*108 | 24.1 | 0.17 | 1.99 | 0.90
P5 | 10.00 | 3.00 | 1.72*108 | 45.4 | 0.31 | 0.94 | 0.43
P6 | 8.00 | 2.40 | 1.72*108 | 40.5 | 0.28 | 0.67 | 0.30
P7 | 8.00 | 2.40 | 1.72*108 | 44.9 | 0.31 | 0.74 | 0.34
P8 | 8.00 | 2.40 | 1.72*108 | 42.1 | 0.29 | 0.70 | 0.32
P9 | 12.00 | 12.00 | 1.72*108 | 26.4 | 0.18 | 2.18 | 0.99
P10 | 6.00 | 1.80 | 1.72*108 | 36.3 | 0.25 | 0.45 | 0.20
P11 | 12.00 | 12.00 | 1.72*108 | 16.1 | 0.11 | 1.77 | 0.81
Name
S1.D.B.G
S2.D.B.G

## Slide 85
Electrical Design
85
Circuit breaker
Name | selection I CB (Amp) | selection cross sectional area (mm2)
M.D.B.G | 500 | 500
M.D.B.F1 | 80 | 35
M.D.B.F2 | 100 | 50
M.D.B.F3 | 100 | 50
M.D.B.F4 | 160 | 70

## Slide 86
Electrical Design
86
Circuit breaker
Name | I CB (Amp) sockets | Selection I CB (Amp) | I cable (Amp) | selection cross sectional area (mm2) | I CB (Amp) lighting | Selection I CB (Amp) | I cable (Amp) | selection cross sectional area (mm2)
S1.D.B.G | 23.46 | 25 | 26.979 | 6 | 15.1432 | 16 | 17.415 | 4
S2.D.B.G | 46 | 50 | 52.9 | 25 | 10.442 | 16 | 12.008 | 2.5
Name | I CB (Amp) | selection I CB (Amp) | I cable (Amp) | selection cross sectional area (mm2)
S1.D.B.G | 38.6032 | 40 | 44.39 | 6
S2.D.B.G | 56.442 | 63 | 64.91 | 25

## Slide 87
Electrical Design
87
Loudspeakers
The converge angle for loudspeakers = 111֠
Coverage area = 13 m²

## Slide 88
Electrical Design
88
Loudspeakers

## Slide 89
Systems integration
93
False Ceiling for Ground floor

## Slide 90
Systems integration
92
False Ceiling for First floor

## Slide 91
Systems integration
91
False Ceiling for Second floor

## Slide 92
Systems integration
90
False Ceiling for Third floor

## Slide 93
Systems integration
89
False Ceiling for Fourth floor

## Slide 94
Cost Estimation
94
 |  | Materials Cost |  | Laber Cost |  | Equipment |  | 
Work Items No. | Description / Detials | Total Cost (NIS) |  | Total Cost (NIS) |  | Total Cost (NIS) |  | Total Cost (NIS)
Total cost for Block C in project |  |  |  |  |  |  |  | 9,535,847
Total unit cost for Block C in project |  |  |  |  |  |  |  | 1,907.17
1.1 | Earth works | 5,200 |  | 360 |  | 138,500.00 |  | 144,060
1.2 | Structural Works | 3,112,253 |  | 816,976 |  | - |  | 3,929,229
1.3 | Finishing Works | 2,353,987 |  | 623,889 |  | - |  | 4,249,966
1.4 | Mechanical Works | 173,716 |  | 35,650 |  | - |  | 1,169,516
1.5 | Electrical Works | 26,815 |  | 16,260 |  | - |  | 43,075
The total cost of block C was found to be 9,535,846 NSI, which equals 2 ,724,527 $.
The cost of establishing one square meter is equal to 1907.17 NIS, which equals 545 $.
The total area of the project reached 32100 m2
Depend on this information the total cost of this project equal 61,220,157 NIS which equals 17,491,473 $.

## Slide 95
95
Thank you for listening