## Slide 2: Outline
1. Introduction
2. Preliminary Dimensions
3. Three Dimensional Analysis and Design

## Slide 3: 1. Introduction
This project deals with the structural analysis and design of one of Iben Sina Hospital buildings in Jenin city

## Slide 4: 1.1 :Project Description
-The hospital is nine floors with a total base area of 3290 m2
-Two expansion joints divide the building into three blocks A, B and C

## Slide 5: 1.1 :Project Description

## Slide 6
Architectural plan for the second floor in bock C

## Slide 7
Architectural plan for the third floor in bock C

## Slide 8: 1.1 :Project Description
-The building base is 175 m AMSL , whereas it has a total height of 39.7 m
-The base has a height of 4.5 m, and other stories are 4 m heights

## Slide 9: 1.1: Project Description
Usage | Total | Block C | Block A+B | Story
Examination rooms and waiting hall | 3291.3877 | 1215.261 | 2076.1265 | Basement
Reception, cafeteria, pharmacy, and waiting hall | 2987.15 | 1302.5 | 1684.65 | Ground
Rest areas, recovery rooms and conference hall | 2339.7362 | 655.0862 | 1684.65 | 
Patient rooms and labs | 2767.702 | 1083.052 | 1684.65 | 
Isolation rooms and patient rooms | 2733.4629 | 1048.813 | 1684.65 | 
Incubators and patient rooms | 2734.3381 | 1049.688 | 1684.65 | 
Physiotherapy, gym, and cardiology | 1817.4557 | 812.6574 | 1004.7983 | 
Elevator rooms | 1893.6233 | 208.9736 | 1684.6497 | 
Staff residence | 1313.4596 | 319.201 | 994.2586 | Roof
- | 21878.3155 | 7695.232 | 14183.0831 | Total

## Slide 10: 1.1 :Project Description
-The site of the building contains law bearing capacity soils
-Swelling, settlement, and high water table may encountered in the area

## Slide 11: 1.1 :Project Description
-Exterior walls are built from: glass, reinforced concrete, and masonry stone
-Interior walls are built from gypsum boards

## Slide 12: 1.2 : Methodology
-Determining loads
-Setting initial dimensions
-Modeling the structure
-Verification the model
-Checking the dimensions
-Studying internal forces
-Setting reinforcement

## Slide 13: 1.3 : Codes and Standards
- ACI 318-11: American Concrete Institute’s Building Code Requirements for Structural Concrete.
- ASCE 7-10: Minimum Design Loads for Buildings and Other Structures (American Society of Civil Engineers).
- IBC 2012: International Building Code
- Israeli Code for Seismic Design SI-413
- Jordanian Code for Loads – 2006.

## Slide 14: 1.4 : Materials
1-Concrete: the main material resisting compression in sections of structural members
Element | Concrete Compressive Strength, | Modulus of Elasticity
Slabs and beams | 28 MPa | 24870 MPa
Columns and walls | 32 MPa | 26587 MPa
Footings | 32 MPa | 26587 MPa

## Slide 15: 1.4 : Materials
2- Reinforcing steel: the main tension-resisting material
in reinforced concrete sections
-Provides ductility, and cracks' controlling for sections
- ASTM A615Gr60 steel with 420 MPa yield strength and 620 MPa tensile strength is used

## Slide 16: 1.4 : Materials
3- Materials in Nonstructural Elements:
-Their weights are added to super imposed dead loads.
-Their stiffness and strength are not considered.

## Slide 17: 1.4 : Materials
Material | Unit Weight (KN/m3) | Material | Unit Weight (KN/m3)
Masonry Stone | 27.5 | Tiles | 27
Blocks | 12 | Mortar | 23
Gypsum | 29 | Filling materials- gravel | 18
Aluminium | 27.5 | Plastering | 23
Glass | 26 |  | 

## Slide 18: 1.5: Loads
Dead Load
Superimposed dead load
Live Load
Roof Live Load
Rain Load
Snow Load
Seismic Load

## Slide 19: 1.5: Loads
Dead Load: is the self-weight of the structural
Superimposed dead load: is the self-weight of the non-structural elements.

## Slide 20: 1.5: Loads
-Slab super imposed dead load:
The slab section show the materials causing loads on the slab

## Slide 21: 1.5: Loads
-Slab super imposed dead load:
From non-structural materials weights, WSD = 3.4
Material | Unit weight KN/ | Thickness (mm) | Weight per unit Area KN/
Tiles | 27 | 30 | 0.81
Mortar | 23 | 20 | 0.46
Filling Materials | 18 | 100 | 1.8
False ceiling | - | - | 0.15
Electrical and mechanical connections | - | - | 0.15

## Slide 22: 1.5: Loads
-Weight of partitions : Aluminium frames and gypsum boards

## Slide 23: 1.5: Loads
-Weight of partitions :
Gypsum walls weight = 3.30 KN/m

## Slide 24: 1.5: Loads
- Shear wall imposed dead load:
The shear wall section show the materials causing loads on the wall

## Slide 25: 1.5: Loads
- Shear wall imposed dead load:
From materials weights, WSD = 4.30
Material | Unit weight | Thickness (mm) | Weight per unit Area
stone | 27 | 40 | 1.08
Mortar | 25 | 60 | 1.5
Isolation | 0.3 | 30 | 0.009
Block | 12 | 100 | 1.2
Plastering | 23 | 20 | 0.46

## Slide 26: 1.5: Loads
- Exterior wall imposed dead load:
The exterior wall section shows the materials causing loads on the wall

## Slide 27: 1.5: Loads
- Exterior wall imposed dead load:
From materials weights, WSD = 25 KN/m
Material | Unit weight | Thickness | Weight per unit Area
stone | 27 | 50 | 1.35
Plain concrete | 25 | 100 | 2.5
Isolation | 0.3 | 30 | 0.009
Block | 12 | 100 | 1.2
Plastering | 23 | 20 | 0.46

## Slide 28: 1.5: Loads
- Curtain walls weight:
From curtain wall section, Curtain wall weight =2 KN/m

## Slide 29: 1.5: Loads
Live Load : movable loads that may vary with time
ASCE 7-10 suggests live load values for different occupancies
Occupancy | Load (KN/m2) | Occupancy | Load (KN/m2)
Patient Rooms | 1.92 | Waiting Room | 5
Operating rooms, laboratories | 2.87 | Slab Subjected to Vehicles | 5
Corridors above first floor | 3.83 | Restaurant | 3.83

## Slide 30: 1.5: Loads
Roof Live Load: resulting from not occupancy related processes, and features .
Based on ASCE 7-10, A value of 0.96 KN/ is proper loads

## Slide 31: 1.5: Loads
Snow Load: caused by cumulating of snow on the exposed surfaces
It may vary due to the:
a- height of the structure
b- ground snow loads
c- snow unit weight
d-inclination of the surface

## Slide 32: 1.5: Loads
Snow Load
ASCE-7-10 predicts design snow loads as follow:

## Slide 33: 1.5: Loads
Snow Load:
- ASCE7-10 suggests values for pg different locations in USA, and it indicates that ground snow loads for other sites shall be determined by the authority having jurisdiction
- Jordanian Code for Loads-2006 is used as a local code.

## Slide 34: 1.5: Loads
Snow Load :
Jordanian Code for Loads-2006 gives pg value as follow:
Building Height Above Mean Sea Level (h) (meters) | Snow Load (S0) (KN\m2)
h<250 | 0
250<h<500 | (h-250)/800
500<h<1500 | (h-400)/320

## Slide 35: 1.5: Loads
Snow Load :
-a suggested roof snow load of 1 KN/ is a logically proper one

## Slide 36: 1.5: Loads
Rain Load: caused by cumulating of rain water on roofs when drainage systems are blocked.
- ASCE 7-10 states that when determining the amount of rain on the roof, deflections from different loads shall not be considered

## Slide 37: 1.5: Loads
Rain Load:
ASCE 7-10 determines rain loads for un-deflected roofs as follow:

## Slide 38: 1.5: Loads
Rain Load:
- A deep understanding of the law can guide us to substitute the value of by the height of the parapet which equals 250 mm
- As a result, rain load can equal:
R= 0.0098 * 250 = 2.45 KN

## Slide 39: 1.5: Loads
Seismic Load :
Dead sea fault is the main cause of earthquakes in the west bank
Codes deal with a lot of parameters in order to predict the seismic forces

## Slide 40: 1.5: Loads
Seismic Load
Ss: maximum considered earthquake spectral response acceleration for short period (0.2 sec)
- From SI413 Maps:
Ss= 0.8 m2\s

## Slide 41: Loads 1.5:
Seismic Load
S1: maximum considered earthquake spectral response acceleration for long periods (1 sec)
- From SI413 Maps:
S1= 0.16 m2\s

## Slide 42: 1.5: Loads
Seismic Load
TL : Long period transition period
- From SI413 Maps:
TL= 7 seconds

## Slide 43: 1.5: Loads
Seismic Load
Site class based on the soil properties is D

## Slide 44: 1.5: Loads
Seismic Load
Based on ASCE7-10, The site coefficient Fa is determined to be 1.18

## Slide 45: 1.5: Loads
Based on ASCE7-10, The site coefficient Fv is determined to be 2.16

## Slide 46: 1.5: Loads
Based on ASCE7-10, The importance factor, Ie, is determined to be 1.5

## Slide 47: 1.5: Loads
Seismic Design Category is D

## Slide 48: 1.5: Loads

## Slide 49: 1.5: Loads
Response spectrum analysis is permitted to be used

## Slide 50: 1.5: Loads
Seismic Load
Table 1.4 shows the period seismic parameters

## Slide 51: 1.5: Loads
Seismic Load

## Slide 52: 1.6: Load Combinations
D: Dead load + Super imposed dead load
L: Live load
F: Fluid load
H: Soil lateral load
Lr: Roof live load
S: Snow load
R: Rain load
E: Earthquake load
W: Wind load

## Slide 53: 1.6: Load Combinations
From IBC 2012, ultimate load combinations are
1.4(D +F)
1.2(D + F) + 1.6(L + H) + 0.5(Lr or S or R)
1.2(D + F) + 1.6(Lr or S or R) + 1.6H + (ƒ1L or0.5W)
1.2(D + F) + 1.0W + ƒ1L + 1.6H + 0.5(Lr or S or R)
1.2(D + F) + 1.0E + ƒ1L + 1.6H + ƒ2S
0.9D+ 1.0W+ 1.6H

## Slide 54: 1.6: Load Combinations
Service load combinations are:
D + F
D + H + F + L
D + H + F + (Lr or S or R)
D + H + F+ 0.75(L) + 0.75(Lr or S or R)
D + H + F + (0.6W or 0.7E)
D + H + F + 0.75(0.6W) + 0.75L + 0.75(Lr or S or R)
D + H + F + 0.75 (0.7 E) + 0.75 L + 0.75 S
0.6D + 0.6W+H
0.6(D + F) + 0.7E+H
0.9(D + F) + 1.0E+ 1.6H

## Slide 55: 1.6: Load Combinations
From IBC-2012:

## Slide 56: 1.6: Load Combinations
From IBC-2012:

## Slide 57: 1.6: Load Combinations
Then, Ultimate load combination are:
U1= 1.4 D+1.4 SID
U2= 1.2 D +1.2 SID +1.6
U3= 1.326 D+1.326 SID + 1.3 Ex +0.39 Ey + L
U4= 1.326 D+1.326 SID + 0.39Ex +1.3 Ey + L
U5= 0.774 D+0.774 SID + 1.3 Ex +0.39 Ey
U6= 0.774 D+0.774 SID + 0.39 Ex +1.3 Ey

## Slide 58: 1.6: Load Combinations
Then, Service load combination are:
S1= 1.0 D+1.0 SID
S2= 1.0 D +1.0 SID +1.0 L
S3= 1.088 D+1.088 SID + 0.71 Ex +0.273 Ey
S4= 1.088 D+1.088 SID + 0.273Ex +0.71 Ey
S5= 1.066 D+1.066 SID + 0.683 Ex +0.205 Ey+0.75 L
S6= 1.066 D+1.066 SID + 0.205Ex +0.683 Ey+0.75 L
S7= 0.512 D+0.512 SID + 0.910 Ex +0.273Ey
S8= 0.512 D+0.512 SID + 0.273 Ex +0.910 Ey

## Slide 59: 1.7: Geotechnical Investigation
The soil class is D for seismic design.
Unit weight | Bearing Capacity | Soil Type
20 KN/m2 | 180 KN/m2 | Stiff Soil

## Slide 60: 2. Preliminary Design
Chapter 2 contains:
Lateral and Gravity Forces Resisting Systems.
Slabs Structural Systems.
Preliminary dimensions for Beams.
Preliminary Thickness of Slabs.
Preliminary Dimensions of Columns.

## Slide 61: 2.1: Lateral and Gravity Forces Resisting Systems
The expected seismic systems are:
Seismic Design Category | Lateral Force Resisting System | Response Modification Factor R | Over Strength Factor | Deflection Amplification Factor
D | Bearing wall system with special shear wall | 5 | 2.5 | 5
D | Building frame system with special shear wall | 6 | 2.5 | 5
D | Dual System with Special Shear Walls | 7 | 2.5 | 5.5
D | Dual System with Intermediate Frames (special shear wall) | 6.5 | 2.5 | 5

## Slide 62: 2.2: Slabs Structural Systems
Solid slab with drop beams between all supports is used due to several factors including:
-High section shear capacity
-High section moment of inertia
-Not containing brittle elements such as concrete blocks.

## Slide 63: 2.3.1: Preliminary Dimensions for Beams
According to ACI 318-11, the preliminary thickness of beams can be calculated based on deflection laws
Member | Minimum thickness |  |  | 
 | Simply supported | One end continuous | Two ends continuous | Cantilever
Solid one-way slab |  |  |  | 
Beams or ribbed one-way slab |  |  |  | 

## Slide 64: 2.3.1:Preliminary dimensions for Beams
Four main types of beams were found in the project based on spans lengths.
Beam Type | Span length | Thickness | Width
B1 | About 8.30 | 0.60 | 0.35
B2 | 5.00 - 7.20 | 0.50 | 0.35
B3 | 4.00-5.00 | 0.35 | 0.35
B4 | Short Spans And limited width | 0.35 | 0.30

## Slide 65: 2.3.2: Preliminary Thickness of Slabs

## Slide 66: 2.3.2: Preliminary Thickness of Slabs

## Slide 67: 2.3.2: Preliminary Thickness of Slabs
h=0.17m
Check

## Slide 68
Structural plan for the third story

## Slide 69: 2.3.3: Preliminary Dimensions of Columns
From ACI 318-11, The axial strength of the column is:

## Slide 70: 2.3.3: Preliminary Dimensions of Columns Load on column F17 from slabs loads
Story | Tributary Area |  | Slab Own weight |  | SID | Total Dead Load | Live load | 
 | Calculation | Answer | Slab Thickness | Weight |  |  | live load | Total Live
Basement | 0.5*(7.2+7.2) *0.5*(4.55+4.2) | 31.5 | 0.17 | 4.25 | 3.4 | 240.98 | 5 | 157.5
Ground | 0 | 0 | 0.17 | 4.25 | - | - | - | -
1 | 0.5*(7.2+7.2) *0.5*(6.8+4.2) | 39.6 | 0.2 | 5 | 5.1 | 399.96 | 4 | 158.4
2 | 0.5*(7.2+7.2) *0.5*(6.8+4.2) | 39.6 | 0.2 | 5 | 5.1 | 399.96 | 4 | 158.4
3 | 0.5*(7.2+7.2) *0.5*(6.8+4.2) | 39.6 | 0.2 | 5 | 5.1 | 399.96 | 4 | 158.4
4 | 0.5*(7.2+7.2) *0.5*(6.8+4.2) | 39.6 | 0.2 | 5 | 4.4 | 372.24 | 4 | 158.4
5 | 0.5*(7.2+7.2) *0.5*(6.8+4.2) | 39.6 | 0.2 | 5 | 3.4 | 332.64 | 1 | 39.6
6 | 0 | 0 | - | - | - |  | - | -
7 | 0 | 0 | - | - | - |  | - | -
Sum |  |  |  |  |  | 2145.74 |  | 830.7

## Slide 71: 2.3.3: Preliminary Dimensions of Columns
Story | Beam in X Direction |  |  | Beam in Y Direction |  | 
 | length | Section Area | Volume | length | Section Area | Volume
Base | 0.5*(7.2+7.2) | 0.35*0.5 | 1.08 | 0.5*(4.55+4.2) | 0.35*0.35 | 0.54
Ground | 0 | 0 | 0 | 0 | 0 | 0
1 | 0.5*(7.2+7.2) | 0.35*0.5 | 1.08 | 0.5*(6.8+4.2) | 0.35*0.6 | 1.15
2 | 0.5*(7.2+7.2) | 0.35*0.5 | 1.08 | 0.5*(6.8+4.2) | 0.35*0.6 | 1.15
3 | 0.5*(7.2+7.2) | 0.35*0.5 | 1.08 | 0.5*(6.8+4.2) | 0.35*0.6 | 1.15
4 | 0.5*(7.2+7.2) | 0.35*0.5 | 1.08 | 0.5*(6.8+4.2) | 0.35*0.6 | 1.15
5 | 0.5*(7.2+7.2) | 0.35*0.5 | 1.08 | 0.5*(6.8+4.2) | 0.35*0.6 | 1.15
6 | 0 | 0 | 0 | 0 | 0 | 0
7 | 0 | 0 | 0 | 0 | 0 | 0
Sum |  |  | 162.75 |  |  | 158.03
Load on F17 from beams weights:

## Slide 72: 2.3.3 : Preliminary Dimensions of Columns

## Slide 73: 2.3.3 : Preliminary Dimensions of Columns .
Dimensions (mm) | Shape | Column Section
C1 | Circular | 700 Diameter
C2 | Circular | 600 Diameter
C3 | Circular | 400 Diameter
C4 | Rectangular | 
C5 | Rectangular | 
The used column sections

## Slide 74: 3. THREE-DIMENSIONAL Analysis and Design
Chapter 3 contains:
3D-Modeling.
Verification of Structural Analysis.
Seismic force-resisting system.
Serviceability.
Wide beam shear check.
Structural Irregularity.
Verification of Structural Design.

## Slide 75: 3.1: 3D-Modeling:
First story plan

## Slide 76: 3.1.1: 3D-Modeling:
3D views

## Slide 77: 3.1.2: Modifiers
Slab modifiers
Beam modifiers

## Slide 78: 3.1.2: Modifiers
Column modifiers
Wall modifiers

## Slide 79: 3.1.3: Load Patterns
Load Patterns

## Slide 80: 3.1.4: Functions
Response Spectrum

## Slide 81: 3.1.5: Load Cases

## Slide 82: 3.1.5: Load Cases
Earthquake Load case (Response Spectrum) in X- direction

## Slide 83: 3.1.6: Diaphragms

## Slide 84: 3.1.7: Mass Source
Mass Source

## Slide 85: 3.2: Verification of Structural Analysis
Compatibility.
Equilibrium check.
Stress-strain relation relationship.
Modal participating mass ratios.
Period Check.
Seismic Base shear computation.

## Slide 86: 3.2.1: Compatibility

## Slide 87: 3.2.2: Equilibrium Check:
In order to verify that loads modelled are representative of that affecting the building, hand calculations of different loads are compared to that resulted by Etabs 16.2. A maximum difference of 5% is acceptable.
Dead Loads.
Live load.
superimposed dead load.

## Slide 88: 3.2.2: Equilibrium Check
Dead Loads Check (The thickness of all Slabs is 180mm)
Weight per floor (KN) | Number of columns |  |  |  |  |  | Total Beams length (m) |  |  |  | Total areas |  | Number of floors
 | C5 |  | C4 | C3 | C2 | C1 | B4 | B3 | B2 | B1 | walls | slab | 
12731 | 0 |  | 1 | 6 | 2 | 14 | 12.8 | 93.3 | 364 | 0 | 478.2 | 1179.6 | Base
7950 | 0 |  | 1 | 6 | 0 | 12 | 14.7 | 27.9 | 207 | 0 | 388.4 | 572.5 | Ground
10350 | 0 |  | 1 | 0 | 0 | 12 | 22.2 | 11.4 | 207 | 101 | 338.4 | 973.0 | 1st
10350 | 0 |  | 1 | 0 | 0 | 12 | 22.2 | 11.4 | 207 | 101 | 338.4 | 973.0 | 2nd
10350 | 0 |  | 1 | 0 | 0 | 12 | 22.2 | 11.4 | 207 | 101 | 338.4 | 973.0 | 3rd
10350 | 0 |  | 1 | 0 | 0 | 12 | 22.2 | 11.4 | 207 | 101 | 338.4 | 988.2 | 4th
7505 | 0 |  | 1 | 0 | 0 | 12 | 22.2 | 7.5 | 61 | 68.8 | 338.4 | 735.4 | 5th
3476 | 2 |  | 1 | 0 | 0 | 2 | 20.9 | 4.0 | 93 | 29.5 | 108.2 | 265.3 | 6th
2732 | 4 |  | 1 | 0 | 0 | 2 | 6.4 | 8.1 | 66 | 56.9 | 88.8 | 243.9 | 7th
75796 |  |  |  |  |  |  |  |  |  |  |  |  | Sum
Weight per floor (KN) | Number of columns |  |  |  |  |  | Total Beams length (m) |  |  |  |  |  | Number of floors
 | C5 |  | C4 | C3 | C2 | C1 | B4 | B3 | B2 | B1 | walls | slab | 
12731 | 0 |  | 1 | 6 | 2 | 14 | 12.8 | 93.3 | 364 | 0 | 478.2 | 1179.6 | Base
7950 | 0 |  | 1 | 6 | 0 | 12 | 14.7 | 27.9 | 207 | 0 | 388.4 | 572.5 | Ground
10350 | 0 |  | 1 | 0 | 0 | 12 | 22.2 | 11.4 | 207 | 101 | 338.4 | 973.0 | 1st
10350 | 0 |  | 1 | 0 | 0 | 12 | 22.2 | 11.4 | 207 | 101 | 338.4 | 973.0 | 2nd
10350 | 0 |  | 1 | 0 | 0 | 12 | 22.2 | 11.4 | 207 | 101 | 338.4 | 973.0 | 3rd
10350 | 0 |  | 1 | 0 | 0 | 12 | 22.2 | 11.4 | 207 | 101 | 338.4 | 988.2 | 4th
7505 | 0 |  | 1 | 0 | 0 | 12 | 22.2 | 7.5 | 61 | 68.8 | 338.4 | 735.4 | 5th
3476 | 2 |  | 1 | 0 | 0 | 2 | 20.9 | 4.0 | 93 | 29.5 | 108.2 | 265.3 | 6th
2732 | 4 |  | 1 | 0 | 0 | 2 | 6.4 | 8.1 | 66 | 56.9 | 88.8 | 243.9 | 7th
75796 |  |  |  |  |  |  |  |  |  |  |  |  | Sum

## Slide 89: 3.2.2: Equilibrium Check
Live load:
Weight per floor (KN) | Area per used live load (KN/m2) |  |  |  | Number of floors
 | 2.5 | 2 | 4 | 5 | 
5302.7 | - | - | 397.7 | 742.4 | Base
2430.8 | - | - | 231.1 | 301.3 | Ground
2671.2 | - | 538.5 | 398.5 | - | 1st
2671.2 | - | 538.5 | 398.5 | - | 2nd
2671.2 | - | 538.5 | 398.5 | - | 3rd
3643.7 | 252.8 | - | 398.5 | 283.5 | 4th
2038.4 | 492.7 | - | 201.7 | - | 5th
600.9 | - | 266.5 | 17 | - | 6th
504.9 | 174.8 | 0 | 17 | - | 7th
22535 |  |  |  |  | Sum

## Slide 90: 3.2.2: Equilibrium Check
super imposed dead load:
Weight per floor (KN) | Length per used SSD load |  | Area per used SSD load (KN/m2) |  |  |  |  | Number of floors
 | 2 | 25 | 3.5 | 6.4 | 5.1 | 4.4 | 3.4 | 
5231.8 | 70 | 28.1 | 133 | 47.42 | - | 180.9 | 911.8 | Base
2262.0 | 89 | 45.0 | 28 | - | - | - | 532.4 | Ground
735.5 | 24 | 88.4 | 28 | - | 790.0 | - | 147.1 | 1st
9209.5 | 24 | 88.4 | 28 | - | 790.0 | - | 147.1 | 2nd
9209.5 | 24 | 88.4 | 28 | - | 790.0 | - | 147.1 | 3rd
9349.7 | 51 | 28.8 | 28 | - | - | 535.1 | 399.8 | 4th
7505.4 | 0 | 27.9 | 28 | - | 266.5 | 54.6 | 639.7 | 5th
85.0 | 12 | 33.4 | - | - | - | - | 17.0 | 6th
1232.1 | 0 | - | - | - | - | - | 246.4 | 7th
40326 |  |  |  |  |  |  |  | Sum

## Slide 91: 3.2.2: Equilibrium Check
The total reactions in Etabs 16.2.
=
All differences are less than 5%, So equilibrium is obtained.

## Slide 92: 3.2.3: Stress-strain relation relationship

## Slide 93: 3.2.3: Stress-strain relation relationship
The checked frame
is on the first Story
So,
w=5KN/m2(live load).
L=4.37m
=6.8m
Then,

## Slide 94: 3.2.3: Stress-strain relation relationship
Section cut to obtain the negative moment at the left end

## Slide 95: 3.2.3: Stress-strain relation relationship
Section cut to obtain the positive moment at the middle

## Slide 96: 3.2.3: Stress-strain relation relationship
Section cut to obtain the negative moment at the right end

## Slide 97: 3.2.3: Stress-strain relation relationship

## Slide 98: 3.2.3: Modal participating mass ratios
According to ASCE 7-10 the Response Spectrum Method is possible to be used; such that the modes accumulate a modal mass participating ratio larger than 90% in all directions.

## Slide 99: Modal participating mass ratios:
Mode | Period | Sum UX | Sum UY | Sum RZ | Mode | Period | Sum UX | Sum UY | Sum RZ
 | sec |  |  |  |  | sec |  |  | 
1 | 1.372 | 0.4251 | 0.0757 | 0.1343 | 25 | 0.081 | 0.9153 | 0.8819 | 0.842
2 | 0.945 | 0.5189 | 0.6116 | 0.1344 | 26 | 0.08 | 0.9202 | 0.8825 | 0.846
3 | 0.729 | 0.6234 | 0.6303 | 0.6207 | 27 | 0.08 | 0.9202 | 0.8825 | 0.846
4 | 0.42 | 0.6347 | 0.6657 | 0.6211 | 28 | 0.08 | 0.9202 | 0.8825 | 0.8462
5 | 0.369 | 0.7635 | 0.6664 | 0.6246 | 29 | 0.08 | 0.9202 | 0.8825 | 0.8463
6 | 0.243 | 0.7702 | 0.6966 | 0.6833 | 30 | 0.08 | 0.9207 | 0.8828 | 0.8473
7 | 0.188 | 0.7837 | 0.8274 | 0.7094 | 31 | 0.079 | 0.9213 | 0.8834 | 0.8505
8 | 0.17 | 0.8575 | 0.8298 | 0.7579 | 32 | 0.079 | 0.9213 | 0.8834 | 0.8505
9 | 0.145 | 0.86 | 0.8298 | 0.7769 | 33 | 0.079 | 0.9231 | 0.8834 | 0.8505
10 | 0.135 | 0.8728 | 0.8323 | 0.7966 | 34 | 0.078 | 0.9259 | 0.8834 | 0.8514
11 | 0.113 | 0.8803 | 0.8352 | 0.7966 | 35 | 0.078 | 0.9262 | 0.8834 | 0.8515
12 | 0.101 | 0.8847 | 0.8558 | 0.8 | 36 | 0.077 | 0.9266 | 0.8835 | 0.8516
13 | 0.098 | 0.8913 | 0.8596 | 0.8017 | 37 | 0.076 | 0.9619 | 0.8842 | 0.8598
14 | 0.092 | 0.8951 | 0.8728 | 0.8314 | 38 | 0.072 | 0.9623 | 0.8874 | 0.8607
15 | 0.09 | 0.896 | 0.8796 | 0.8317 | 39 | 0.071 | 0.9654 | 0.904 | 0.869
16 | 0.082 | 0.8962 | 0.8797 | 0.8322 | 40 | 0.07 | 0.9669 | 0.9051 | 0.8872
17 | 0.082 | 0.8963 | 0.88 | 0.8322 | 41 | 0.065 | 0.967 | 0.9054 | 0.8875
18 | 0.082 | 0.9025 | 0.88 | 0.8327 | 42 | 0.065 | 0.971 | 0.9073 | 0.8893
19 | 0.082 | 0.9027 | 0.8801 | 0.8327 | 43 | 0.063 | 0.9712 | 0.911 | 0.8911
20 | 0.081 | 0.9028 | 0.8802 | 0.8327 | 44 | 0.061 | 0.9789 | 0.9292 | 0.9098
21 | 0.081 | 0.903 | 0.881 | 0.8362 | 45 | 0.059 | 0.9815 | 0.9298 | 0.9215
22 | 0.081 | 0.9092 | 0.8819 | 0.8415 | 46 | 0.059 | 0.9823 | 0.93 | 0.939
23 | 0.081 | 0.9153 | 0.8819 | 0.842 | 47 | 0.056 | 0.9828 | 0.9349 | 0.9398
24 | 0.08 | 0.9202 | 0.8825 | 0.846 | 48 | 0.056 | 0.9832 | 0.9354 | 0.9407

## Slide 100: 3.2.4: Period Check

## Slide 101: 3.2.4: Period Check

## Slide 102: 3.2.4: Period Check
From Etabs: Tx=1.37 sec > upper period limit.
From Etabs: Ty=0.954 sec < upper period limit.
Two result :
The base shear in X-direction is calculated using a structure period value of 1.13 sec.
The base shear in Y-direction is calculated using a structure period value of 0.954 sec.

## Slide 103: 3.2.5: Seismic Base shear computation
From ASCE 7-10, the seismic base shear is:
V = Cs W
Where:
V: Base shear
W: Effective seismic weight.
Cs: Seismic response coefficient.

## Slide 104: 3.2.5: Seismic Base shear computation

## Slide 105: 3.2.5: Seismic Base shear computation

## Slide 106: 3.2.5: Seismic Base shear computation

## Slide 107: 3.2.5: Seismic Base shear computation

## Slide 108: 3.2.5: Seismic Base shear computation

## Slide 109: 3.2.5: Seismic Base shear computation

## Slide 110: 3.2.5: Seismic Base shear computation
The total reactions resulted by Etabs from dead, live, super imposed dead, response spectrum earthquake load cases, and earthquake load patterns.

## Slide 111: 3.3: Seismic force-resisting system:

## Slide 112: 3.3: Seismic force-resisting system:

## Slide 113: 3.3: Seismic force-resisting system:
A section cut is taken the base story in order to find the percentage of vertical load resisted by walls

## Slide 114: 3.3: Seismic force-resisting system:
Deflection Amplification Factor | Over Strength Factor | Response Modification Factor R | Lateral Force Resisting System | Seismic Design Category
5 | 2.5 | 5 | Bearing wall (special reinforced concrete shear wall). | D

## Slide 115: 3.3: Deflection Computations
1- Immediate deflection.
2-Long-term deflection.

## Slide 116: 3.3.1: Long term deflection

## Slide 117: 3.3.1: Long term deflection

## Slide 118: 3.3.1: Long term deflection

## Slide 119: 3.3.1: Long term deflection
long-term deflection in store 6.

## Slide 120: 3.3.1: Long term deflection

## Slide 121: 3.4.2: Drift Calculations
It is the difference between the lateral deflection of the centre of mass at both the top and bottom of the story

## Slide 122: 3.4: Drift Calculations
Based on IBC-2012, the intended deflection is:

## Slide 123: 3.4: Drift Calculations
Based on IBC-2012:
the allowable drift to story height ratio is 0.01

## Slide 124: 3.4: Drift Calculations
Table 3.10 : the drift values in X-directions
Story | Story Height (mm) | Elastic Displacement (mm) | Non-Elastic Drift (mm) | Allowable Drift (mm)
Base | 0 | 0 | 0 | 0
1 | 3900 | 1.60 | 5.32 | 39
2 | 4500 | 5.40 | 12.70 | 45
3 | 4500 | 10.84 | 18.12 | 45
4 | 4500 | 17.60 | 22.54 | 45
5 | 4500 | 24.87 | 24.24 | 45
6 | 4500 | 32.40 | 25.10 | 45
7 | 4500 | 40.00 | 25.34 | 45
8 | 4500 | 48.89 | 29.61 | 45
9 | 4500 | 52.86 | 13.23 | 45

## Slide 125: 3.4: Drift Calculations
Table 3.11 : the drift values in Y-directions
Story | Height (mm) | Elastic Displacement (mm) | Non-Elastic Drift (mm) | Allowable Drift (mm)
Base | 0 | 0 | 0 | 0
1 | 3900 | 1.23 | 4.11 | 39
2 | 4500 | 7.88 | 22.15 | 45
3 | 4500 | 15.21 | 24.44 | 45
4 | 4500 | 24.79 | 31.94 | 45
5 | 4500 | 34.99 | 33.99 | 45
6 | 4500 | 45.25 | 34.20 | 45
7 | 4500 | 45.15 | -0.32 | 45
8 | 4500 | 31.72 | -44.77 | 45
9 | 4500 | 40.41 | 28.95 | 45

## Slide 126: 3.5: Wide beam shear check
- In order to avoid shear reinforcement in the slab, the ultimate shear applied on the slab mustn't exceed the
shear capacity of the concrete
- A 1 m width unit is taken to find the slab shear capacity

## Slide 127: 3.5: Wide beam shear check
According to ACI 318-11, the section shear capacity is :

## Slide 128
Figure 3.21 : story 1shear V13 using a range of

## Slide 129: 3.5: Wide beam shear check
- No shear reinforcement in the slab

## Slide 130: 3.6: Structural Irregularity
Weight (mass) irregularity
the effective mass of a story > 150 % of the effective mass of an adjacent storey

## Slide 131: 3.6: Structural Irregularity
Weight (mass) irregularity
Table shows storey mass to above one ratios.
Story | Effective Mass(Ton) | Ratio to Above
Story1 | 1968.62 | 1.72
Story2 | 1144.06 | 0.62
Story3 | 1836.42 | 1.00
Story4 | 1837.86 | 1.00
Story5 | 1841.92 | 1.10
Story6 | 1669.17 | 1.30
Story7 | 1285.10 | 2.04
Story8 | 629.23 | -
Story9 | 375.02 | -

## Slide 132: 3.6: Structural Irregularity
Weight (mass) irregularity
From Table 3.12:
- Each of stories 3 and 1 has an effective mass larger than 1.5 times that of storey2.
- Story7 has an effective mass larger than 1.5 times that of story8.
.As a result, the building has mass irregularity

## Slide 133: 3.6: Structural Irregularity
Stiffness Irregularity :
According to IBC 2012, stiffness irregularity is defined to exist where:
- Story stiffness < 70 % stiffness of 1 above
- Story stiffness < 80 % av. stiffness of 3 above

## Slide 134: 3.6: Structural Irregularity
Stiffness Irregularity :
Figure ‎3.27 shows
Storeys stiffness
against EQx

## Slide 135: 3.6: Structural Irregularity
Stiffness Irregularity :
Figure ‎3.28 shows
Storeys stiffness
against EQy

## Slide 136: 3.6: Structural Irregularity
: Diaphragm discontinuity
Diaphragm discontinuity in one of :
- The effective diaphragm stiffness of a story>50 % of that of adjacent story
- Open areas or cutout > 50 % of diaphragm

## Slide 137: 3.6: Structural Irregularity
: Diaphragm discontinuity
Figure ‎3.29 shows Diaphragm opening in storey 2

## Slide 138: 3.6: Structural Irregularity
: Diaphragm discontinuity
From Figure 3.29:
- Story2 has a large opening of area 243, which form a 25.5% of the total enclosed area of story 1 which equals 952.
- As a result, the building has no diaphragm discontinuity.

## Slide 139: 3.6: Structural Irregularity
In-plan discontinuity lateral-force-resisting elements
- It is defined to exist where there is an in-plane offset of the offset of an element resisting lateral
load larger than it’s length.
- No in-plane offsets in the shear walls.

## Slide 140: 3.6: Structural Irregularity
: Vertical Geometric Irregularity
- It is defined to exist where the horizontal dimension of the seismic force-resisting system in any story is .more than 130% of that in an adjacent story
- Six shear walls have a change in length in Y-direction, such that each has a length of 4.04 m in both of the base storey1, and story2, whereas the length decreases to 1.77 m in story3,4,5,6, and 7. Note that the first length is 228% of the second one

## Slide 141: 3.6: Structural Irregularity
: Vertical Geometric Irregularity
Figure ‎3.30 shows the vertical geometric irregularity in story 2&3

## Slide 142: 3.6: Structural Irregularity
: Out-of-plane offsets
-It is defined to exist where there is a discontinuity in the lateral force-resistance path
- No out-of-plan offset irregularity in the building.

## Slide 143: 3.6: Structural Irregularity
Re-entrant Corners Irregularity
- it is defined to exist where both plan projections of the structure beyond a re-entrant corner are greater than 15% of the plan dimension of the structure in the given direction.
-Story2 has a projection
of 21.34 m in X-direction,
which form 62% of the
X-dimension which equals
34.45 m

## Slide 144: 3.6: Structural Irregularity
Re-entrant Corners Irregularity :
Figure 3.31 shows the re-entrant corner in story 2

## Slide 145: 3.6: Structural Irregularity
Re-entrant Corners Irregularity
From Figure 3.32 :
Story 8 has a projection of
5.75 m in X-direction which forms 40% of the X-dimension which equals 14.25 m.

## Slide 146: 3.6: Structural Irregularity
:Weak Story Irregularity
- It is defined to exist where the story lateral strength
is less than 80% of that in the story above.
- In this project, no shear wall has increasing dimensions with height. No weak storey in the building.

## Slide 147: 3.6: Structural Irregularity
Torsional Irregularity:
- It is defined to exist where the maximum story drift at one end of the structure transverse to an axis is more than 1.2 times the average of the story drifts at the two ends of the structure.

## Slide 148: 3.6: Structural Irregularity
Torsional Irregularity:
- For Structures assigned to Seismic Design Category C, D, E, or F, having torsional irregularity or extreme torsional irregularity, and having rigid or semi rigid diaphragms, ASCE 7-10 requires amplifying the effects of accidental torsion by multiplying the assumed 5% eccentricity at each level by a torsional amplification factor (Ax).

## Slide 149: 3.6: Structural Irregularity
Torsional Irregularity:
The torsional amplification factor (Ax) determined as follow:

## Slide 150: 3.6: Structural Irregularity
Torsional Irregularity:
Table ‎3.13: Torsional irregularity calculations in X-direction
story | δmax /δav | Ax factor | New Eccentricity
1 | 1.74 | 2.11 | 0.11
2 | 1.32 | 1.21 | 0.06
3 | 1.32 | 1.20 | 0.06
4 | 1.32 | 1.21 | 0.06
5 | 1.32 | 1.22 | 0.06
6 | 1.33 | 1.22 | 0.06
7 | 1.33 | 1.23 | 0.06
8 | 1.30 | 1.18 | 0.06
9 | 1.21 | 1.01 | 0.05

## Slide 151: 3.6: Structural Irregularity
Torsional Irregularity:
Table ‎3.14: Torsional irregularity calculations in Y-direction.
Story | δmax /δav | Ax factor | New Eccentricity
1 | 1.72 | 2.06 | 0.10
2 | 1.43 | 1.42 | 0.07
3 | 1.49 | 1.55 | 0.08
4 | 1.48 | 1.51 | 0.08
5 | 1.46 | 1.48 | 0.07
6 | 1.45 | 1.46 | 0.07
7 | 1.35 | 1.26 | 0.06
8 | 1.09 | 1.00 | 0.05
9 | 1.13 | 1.00 | 0.05

## Slide 152: 3.6: Structural Irregularity
Nonparallel system Irregularity :
resisting lateral loads system are not symmetric

## Slide 153: 3.6: Structural Irregularity
Nonparallel system Irregularity :
-When vertical lateral force-resisting elements are not parallel to the major orthogonal axes of the seismic force-resisting system.
- In this project, all shear walls are parallel to X and Y-axes. So, it not existed in the building.

## Slide 154: 3.6: Structural Irregularity
Table ‎3.15: Horizontal Irregularities.
Irregularity | Existence
Torsional Irregularity | Yes
Extreme Torsional Irregularity | Yes
Reentrant Corner Irregularity | Yes
Diaphragm Discontinuity | Yes
Out-of-Plane Offset Irregularity | No
Nonparallel System Irregularity | No

## Slide 155: 3.6: Structural Irregularity
Irregularity | Existence
Soft Story Irregularity | No
Extreme Soft Story Irregularity | No
Mass Irregularity | Yes
Vertical Geometric Irregularity | Yes
In-Plane Discontinuity in Vertical Lateral Force Resisting Element | No
Weak Story Irregularity | No
Extreme Weak Story Irregularity | No
Table ‎3.16: Vertical Irregularities.

## Slide 156: 3.7: P-delta Effect

## Slide 157: 3.7: P-delta Effect
From ASCE7-10, P-delta effects are neglected when the stability coefficient (θ) is less than or equal to 0.10

## Slide 158: 3.7: P-delta Effect
From ASCE7-10, P-delta effects are neglected when the stability coefficient (θ) is less than or equal to 0.10

## Slide 159: 3.7: P-delta Effect
The maximum stability coefficient is determined as follows:

## Slide 160: 3.7: P-delta Effect
Table ‎3.17: P-Δ calculations in X-direction.
Story | Height (mm) | Non-Elastic Drift (mm) | P (KN) | Vx (KN) | Theta
1 | 3900 | 5.32 | 137716.57 | 7642.26 | 0.005
2 | 4500 | 12.70 | 114736.68 | 6852.54 | 0.015
3 | 4500 | 18.12 | 101180.12 | 6128.23 | 0.020
4 | 4500 | 22.54 | 81060.05 | 4836.70 | 0.024
5 | 4500 | 24.24 | 60895.76 | 3879.45 | 0.024
6 | 4500 | 25.10 | 40605.57 | 3277.56 | 0.019
7 | 4500 | 25.34 | 21574.40 | 2809.23 | 0.013
8 | 4500 | 29.61 | 9419.76 | 2308.20 | 0.010
9 | 4500 | 13.23 | 3161.62 | 1250.97 | 0.005

## Slide 161: 3.7: P-delta Effect
Table ‎3.18: P-Δ calculations in Y-direction.
Story | Height (mm) | Non-Elastic Drift (mm) | P (KN) | Vy (KN) | Theta
1 | 3900 | 4.11 | 137716.57 | 7639.79 | 0.005
2 | 4500 | 22.15 | 114736.68 | 7282.53 | 0.021
3 | 4500 | 24.44 | 101180.12 | 6761.61 | 0.020
4 | 4500 | 31.94 | 81060.05 | 5748.23 | 0.023
5 | 4500 | 33.99 | 60895.76 | 4837.92 | 0.019
6 | 4500 | 34.20 | 40605.57 | 3946.94 | 0.012
7 | 4500 | 0.32 | 21574.40 | 2772.16 | 0.000
8 | 4500 | 44.77 | 9419.76 | 1517.91 | 0.006
9 | 4500 | 28.95 | 3161.62 | 703.46 | 0.009

## Slide 162: 3.8: Verification of Structural Design
- Etabs 16.2 designs beams, columns, and shear walls automatically.
- Hand design is done for a beam, column, and shear wall chosen randomly.

## Slide 163: 3.8.1 Verification of beam design
Beams are not designated as part of the seismic force

## Slide 164: 3.8.1 Verification of beam design
Based on ACI 318-11, flexural steel percentage is:
Where: = Rebar percentage.
= Specified compressive strength of concrete.
= Specified yield strength for non-pre-stressed reinforcement.
= Factored moment.
= Width of compression face of member.
= Effective depth of reinforced concrete section.

## Slide 165: 3.8.1 Verification of beam design
Based on ACI 318-11, minimum flexural steel percentage is:
Where: = Rebar percentage.
= Specified compressive strength of concrete.
= Specified yield strength for non-pre-stressed reinforcement.

## Slide 166: 3.8.1 Verification of beam design
Based on ACI 318-11, shear capacity of beam sections is:
Where: = Nominal shear strength provided by concrete.
= Capacity reduction factor.
= light weight concrete Modification factor.

## Slide 167: 3.8.1 Verification of beam design
Based on ACI 318-11, minimum design shear is:
Where: Ve: Minimum design shear, KN.
Mpr: Maximum probable moment at beam end.
Ln: Clear span of the beam.
Wu: Load per unit length caused by 1.2D+L load combination.

## Slide 168: 3.8.1 Verification of column design
Figure 3.33 shows beam design shear form ACI 318-11

## Slide 169: 3.8.1 Verification of beam design
Based on ACI 318-11, for frames not designated as part of the seismic force resisting system:
is neglected where both of the following conditions are satisfied:
The factored axial compressive force, Pu, is less than Ag×fc′ /20
Ve= is larger than V/2

## Slide 170: 3.8.1 Verification of beam design
According to ACI 318-11, the shear resisted by steel is :
Where: nominal shear strength provided by shear reinforcement
factored shear force at section.
= nominal shear strength provided by concrete.
= capacity reduction factor.

## Slide 171: 3.8.1 Verification of beam design
According to ACI 318-11, Also, shear reinforcing ratio is:
Where:
Area of shear reinforcement within spacing.
S = Center-to-center spacing of items.

## Slide 172: 3.8.1 Verification of beam design
Based on ACI 318-11, minimum shear reinforcing ratio is:
Where:
= Minimum shear reinforcement per unit length.

## Slide 173: 3.8.2 Verification of beam design
Figure 3.34 shows the
layout of Beam B1
in the sixth floor

## Slide 174: 3.8.1 Verification of beam design
Table 3.15 shows the properties of the beam B1.

## Slide 175: 3.8.1 Verification of beam design
Figure 3.35 shows internal force diagrams of Beam B1.

## Slide 176: 3.8.1 Verification of beam design
Flexural Design Verification
Rebar percentage can be obtained as follow:
= 0.0027
- This value is compared to the lower limit calculated as follow:
0.00333
Then, use

## Slide 177: 3.8.1 Verification of beam design
Flexural Design Verification
Figure 3.36 shows flexural rebar percentage for Beam B1 from Etabs

## Slide 178: 3.8.1 Verification of beam design
Shear Design Verification :
For flexural As=5φ16=1000 mm2 (top steel at beam ends):
Mpr1 =1.25AsFy(d-a/2) = 374 KN.m
Then, Mpr2=0.5×MPr1=187 KN.m
VE== 86.3 KN

## Slide 179: 3.8.1 Verification of beam design
Shear Design Verification :
Figure 3.37 shows shear diagrams from gravity and earthquake.

## Slide 180: 3.8.1 Verification of beam design
Shear Design Verification :
From Figure 3.37, Ve= VE= 116 KN
From Figure 3.35, Vu=202 KN.
So, use Vdesign= 202 KN

## Slide 181: 3.8.1 Verification of beam design
Shear Design Verification :
Check ignoring Vc:
From Figure 3.35, axial force Pu= 10 KN <Ag×f’c/20=448 KN
VE== 86.3 KN<Vdesign/2=101 KN
So, Vc is not neglected.

## Slide 182: 3.8.1 Verification of beam design
Shear Design Verification :
-Calculating Av/s:
=156.6 KN < Vdesign
Then, shear reinforcement is required.
Vs=Vdesign/Փ-Vc =72.3kN
mm2/m

## Slide 183: 3.8.1 Verification of beam design
Shear Design Verification:
-Calculating Av/s:
Table 3.16 shows shear reinforcement ratio from Etabs.

## Slide 184: 3.8.1 Verification of beam design
Torsion Design Verification:
Beams are designed for compatibility torsion (4Tth )in this model
According to ACI 318-11, threshold torsion is:
Where: Փ: Torsion reduction factor
Acp: Area enclosed by outside perimeter of concrete cross section, mm2
Pcp: Outside perimeter of concrete cross section, mm

## Slide 185: 3.8.1 Verification of beam design
Torsion Design Verification:
Based on ACI 318-11, dimensions of beams must satisfy the following:
Where: Ph: Perimeter of centerline of outermost stirrup, mm
Aoh: Area enclosed by centerline of the stirrup, mm2

## Slide 186: 3.8.1 Verification of beam design
Torsion Design Verification:
According to ACI 318-11, Torsion transfer steel ratio is:
Where: Ao: Gross area enclosed by torsional shear flow path, mm2
Ao=0.85 Aoh
Tn: Nominal torsional moment strength, N·mm

## Slide 187: 3.8.1 Verification of beam design
Torsion Design Verification:
Torsion longitudinal steel is calculated as follow:
Where: fyt: specified yield strength of transverse reinforcement, Mpa.

## Slide 188: 3.8.1 Verification of beam design
Torsion Design Verification:
This longitudinal steel is compared to minimum limit calculated as follow:

## Slide 189: 3.8.1 Verification of beam design
Torsion Design Verification:
Taking the same beam (Beam B1 in Story 6) as an example, then:
Vu=202 KN, Tu=0 KN
Acp=bw×h=320000 mm2
Pcp= 2(b+h) =2400
Assuming Փ12 mm stirrups, and 40 mm cover, then:
A0h= (bw-2× (40+12/2)) × (hw-2× (40+12/2)) =218046 mm2
Ph=2× (bw-2× (40+12/2)) +2× (hw-2× (40+12/2)) =2032 mm
A0=0.85× A0h=185354.8 mm2
Tth= 14.11 KN

## Slide 190: 3.8.1 Verification of beam design
Torsion Design Verification:
Table 3.17 shows torsion parameters used by Etabs for Beam B1.

## Slide 191: 3.8.2 Verification of column design
The ultimate loads applied on the column is compared to the calculated column capacity, and they should satisfy the following:
(Equation 3.56)
(Equation 3.57)
(Equation 3.58)

## Slide 192: 3.8.2 Verification of column design
Column C4 in story 4 is chosen to be checked manually.
Figure 3.38 shows column C4.
Section dimensions:
bw=300 mm and h=800 mm

## Slide 193: 3.8.2 Verification of column design
Columns are designed according to ACI 318-14, Section 18.14, such that columns shall satisfy almost special column requirements.
Table 3.18 shows the axial force and biaxial moment of column C4, that imported from Etabs.

## Slide 194: 3.8.2 Verification of column design
Design as beam or column ?!
ACI 318-14, Section 18.7.5 provide the minimum axial load to design as column.
Where:
        : Factored axial force.
        : Concrete compressive strength.
        Gross area of concrete section.

## Slide 195: 3.8.2 Verification of column design
By substituting in the Equation 3.5, 768 KN
So, based on Table 3.18, 860.7 KN > 786 KN.
>>>the member is design as column.
  From Table 3.18, =0.01
  Then, =

## Slide 196: 3.8.2 Verification of column design
Axial and Moment strength
Bressler reciprocal method
Where:
  Axial load capacity of a column under biaxial bending with eccentricity of .
  Axial load capacity when only eccentricity y e is present ( = 0).
  Axial load capacity when only eccentricity x e is present ( =0).
  Axial load capacity of the column loaded concentrically.

## Slide 197: 3.8.2 Verification of column design
= 20.80 KN.m >> =3876 KN

## Slide 198: 3.8.2 Verification of column design
= 36.00 KN.m >> =3876 KN

## Slide 199: 3.8.2 Verification of column design
Axial load capacity of the column loaded concentrically is obtained as follow:
Where:
      = Strength reduction factor.
      Ultimate load for concentrically loaded column.
      : Factor to consider minimum eccentricity
      : Concrete compressive strength.
      : Steel yield strength.
      : Gross area of concrete section.
      : Area of longitudinal reinforcement.

## Slide 200: 3.8.2 Verification of column design
Based on , =3884.80 KN
S0, =3867.26 KN>OK

## Slide 201: 3.8.2 Verification of column design
Shear strength
According to ACI-18-11, section 18.6.7.1, the design shear can be determined based on equation 3.62:
The shear in direction 3 is taken as sample of calculation to compare with Etabs.

## Slide 202: 3.8.2 Verification of column design
calculate
≈1.23×
T

## Slide 203: 3.8.2 Verification of column design
calculate
Where:
H: Distance between
the inflection points

## Slide 204: 3.8.2 Verification of column design
Figure 3.42 shows reinforcement of beams jointing to column C4.

## Slide 205: 3.8.2 Verification of column design
Section dimensions-beam: bw=400mm and h=800mm

## Slide 206: 3.8.2 Verification of column design
71.4KN
Table 3.19 shows the design forces for column C4 imported from Etabs. So, , its ok

## Slide 207: 3.8.3.1 Verification of pier design
ACI 318-11 gives different design provisions for vertical wall segments based on their geometric aspect ratios (lw/bw) and (hw/lw).
Where:
lw: Length of wall pier considered in direction of shear force.
bw: Wall thickness.
hw: Clear height of wall segment or wall pier considered

## Slide 208: 3.8.3.1 Verification of pier design
Table ‎3.20 shows governing design provisions of vertical wall segments in ACI 318-11

## Slide 209: 3.8.3.1 Verification of pier design
Based on the same provisions, pier design shear is:
Where: Mpr top: Maximum probable moment at the top end
Mpr bottom: Maximum probable moment at the bottom end
hw: Clear height of wall segment or wall pier considered

## Slide 210: 3.8.3.1 Verification of pier design
Based on the same provisions, pier minimum design shear is:
Where: Mpr top: Maximum probable moment at the top end
Mpr bottom: Maximum probable moment at the bottom end
hw: Clear height of wall segment or wall pier considered

## Slide 211: 3.8.3.1 Verification of pier design
Based on ACI 318-11, Boundary elements are used when:
Where: C: the largest neutral axis depth consistent with δu.
u: design displacement
δu /hw ≥ 0.007
The maximum extreme fiber compressive stress, corresponding to load combinations including earthquake effects, E, exceeds Stress limit = 0.2fc′

## Slide 212: 3.8.3.1 Verification of pier design
Based on ACI 318-11, the horizontal length of the boundary element is :
(Equation 3.70)
Where: LB: Horizontal length of boundary elements
C: the largest neutral axis depth consistent with δu.

## Slide 213: 3.8.3.1 Verification of pier design
Edge members design forces

## Slide 214: 3.8.3.1 Verification of pier design
Uniform reinforcing pier section:
Where: LB: the length of the boundary element.
P: the design axial force for the boundary element.

## Slide 215: 3.8.3.1 Verification of pier design
Simplified compression and tension pier section:

## Slide 216: 3.8.3.1 Verification of pier design
Wall F in story 1 is taken as an example. Table 3.21 shows the wall properties.

## Slide 217: 3.8.3.1 Verification of pier design
Table 3.22 shows the design loads and steel ratio from Etabs.
Table 3.23 shows the boundary element check done by Etabs.

## Slide 218: 3.8.3.1 Verification of pier design
Boundary element check
The applied compression stress is calculated as follow:
Where: Ag = Wall section gross area, mm2
I = Wall section moment of inertia, mm4
Compression stress= +

## Slide 219: 3.8.3.1 Verification of pier design
Boundary element check
Compression stress limit = 0.2fc′ = 6.4 Mpa, edge members are needed
The length of the boundary elements is :
= 545 mm

## Slide 220: 3.8.3.1 Verification of pier design
Pier shear design
Table 3.24 shows shear steel calculations from Etabs for wall F
From figure 3.24, Vu=1430.74 KN
Vc = kN > Vu
Then, Vs = 0, use = 0.0025×500×1000=1250 mm2/m

## Slide 221: 3.8.3.2 Spandrel design verification
In order to verify from Etabs results, spandrel S11 in grid B in Story 7 is chosen to be designed manually. Spandrel properties are shown in Table 3.25.
The length of the Spandrel (L)=1.2m.

## Slide 222: 3.8.3.2 Spandrel design verification
Flexural reinforcement:
Table 2.26 shows the steel area, and designed value for moment.
d=2030mm.
=32Mpa
= 1117 KN.m
- =0.0025
So, a=60mm

## Slide 223: 3.8.3.2 Spandrel design verification
For singly reinforcement, the maximum allowable depth of the rectangular compression block, , is given according to ACI 318-14, Section 22.2:
Where: is calculated as follows:

## Slide 224: 3.8.3.2 Spandrel design verification
Based on Equation 3.79,
Then,
So,
a<, no need to doubly reinforcement
The reinforcement percentage from Figure 3.34,
The reinforcement percentage from Etabs approximately equal to results manually.

## Slide 225: 3.8.3.2 Spandrel design verification
Shear reinforcement:
According to ACI 318-14, Section 18.10.7, the coupling beams with (/h) < 2 and with ≥ 2 shall be reinforced with two intersecting groups of diagonally placed bars symmetrical about the midspan.

## Slide 226: 3.8.3.2 Spandrel design verification
- L/H ratio=1.2/2.1=0.57 <2.
Then, Vlimit= 2=1530 < Vu.
So, the diagonal reinforcement is mandatory

## Slide 227: 3.8.3.2 Spandrel design verification
The nominal shear strength,, for group of diagonal bars can be determined as follows:
Where:
= Total area of reinforcement in each group of diagonal bars in a diagonally reinforced coupling beam.
= Angle defining the orientation of reinforcement.

## Slide 228: 3.8.3.2 Spandrel design verification
- .
- Vu = 1587 KN
The area of steel in Table 3.27,
So, the difference in Etabs results and
manually results is very small.

## Slide 229: 3.9.1 Mat foundation
1m thickness mat
20 piles under
small part of the mat

## Slide 230: 3.9.1.1 Pile capacity
Based on Meyerhof method:
Pile capacity =skin resistance + end point bearing
It depends on: - pile length
- pile section
- concrete type
- soil properties

## Slide 231: 3.9.1.1 Pile capacity
Based on Meyerhof method:
Qp=9CuAg (Equation 3.85)
Where: Qp : Pile point end bearing capacity, KN
Cu: Soil undrained cohesion, KN/m2
Ap: Pile gross section area, m2

## Slide 232: 3.9.1.1 Pile capacity
Based on ꬰ Method:
Qs= P L f (Equation 3.86)
Where: P: Pile perimeter, m
L: Pile embedded length, m
f: Pile skin resistance, KN/m2

## Slide 233: 3.9.1.1 Pile capacity
Based on ꬰ Method:
f= ꬰCu (Equation 3.87)
Where: f: Pile skin resistance, KN/m2
Cu: Soil undrained cohesion, KN/m2
ꬰ: Empirical adhesion factor
from Table 3.28

## Slide 234: 3.9.1.1 Pile capacity
Total settlement of piles is calculated as follow:
Se=Se1+Se2+Se3 (Equation 3.88)
Where: Se: Total Pile settlement, mm
Se1: Elastic Settlement of pile, mm
Se2: Pile settlement by load at the pile tip, mm
Se3: Pile settlement by load along the pile, mm

## Slide 235: 3.9.1.1 Pile capacity
Elastic settlement of piles is calculated as follow:
Where: ξ : Factor (0.5 - 0.67)depend on varying of friction
Ap: Pile gross section area, m2
L: Pile embedded length, m
Ep: Modulus of elasticity of the pile material
Qwp: load carried at the pile under working load conditions=Qs/Factor of Safety
Qws: load carried by skin resistance under working load =Qs/Factor of Safety

## Slide 236: 3.9.1.1 Pile capacity
Pile settlement by load at the pile tip is as follow:
Where: D: Pile diameter, m
qwp: Point load per unit area at the pile point = Qwp/Ap
Es: Soil Modulus of elasticity at or below the pile point
μs: Soil poisson’s ratio
Iwp : Influence factor = 0.85

## Slide 237: 3.9.1.1 Pile capacity
Pile settlement by load along the pile is as follow:
Where: P: Pile perimeter, m
L: Pile embedded length, m
Iws: Influence factor

## Slide 238: 3.9.1.1 Pile capacity
Using Vesic empirical equation, Influence factor is :
Iws = 2+ 0.35× (Equation 3.92)
Where: Iws: Influence factor
L: Pile embedded length, m
D: Pile diameter, m

## Slide 239: 3.9.1.1 Pile capacity
Consider a pile having the characteristics shown in Table 3.29.
Consider a soil having the characteristics shown in Table 3.30

## Slide 240: 3.9.1.1 Pile capacity
Qp =9CuAg
= 9×90×0.785
= 635.85 KN
Cu/Pa=90/100=0.9
ꬰ==0.51
f= ꬰCu = 0.51×90 =45.9 KN/m2
Qs= P L f = 3.14×13×45.9=1873.64 KN

## Slide 241: 3.9.1.1 Pile capacity
Considering factors of safety of 1.5 for friction and 3 for bearing, the capacities of the pile at working loads conditions is:
Qws= 1249 KN
Qwp= 212 KN
Then, the total pile capacity at service loads is
Q=1249+212=1460 KN

## Slide 242: 3.9.1.1 Pile capacity
Figure 3.50 shows the reactions
of pile springs in SAFE 2012
All reactions are less than
pile capacity at service loads
which is 1460 KN

## Slide 243: 3.9.1.1 Pile capacity
The settlement of the pile is:
Se1= = =0.59 mm
Se2= (1-μs2) Iwp = (1-0.252) ×0.8= 2.89 mm
Iws = 2+ 0.35× = 2+0.35× =3.26
Se3= (1-μs2)Iws = (1-0.252)×3.26 = 1.34 mm

## Slide 244: 3.9.1.1 Pile capacity
Total Pile settlement is:
Se= Se1+Se2+Se3
= 0.59+2.89+1.34
= 4.82 mm
Pile stiffness factor is:
K=== 303 KN/mm

## Slide 245: 3.9.1.2 Soil pressure check
B.C=180 KN/m2
All values of the applied
stress are within the
acceptable range.

## Slide 246: 3.9.1.3 Mat foundation one-way shear check
The shear strength of a 1m wide section of the mat foundation is calculated as follow:
ՓVc= Փ bw d (Equation 3.93)
= 0.75× × 1000×960 /1000
= 670KN/m

## Slide 247: 3.9.1.3 Mat foundation one-way shear check
Figure ‎3.52 : Mat foundation shear in X-direction

## Slide 248: 3.9.1.3 Mat foundation one-way shear check
Figure ‎3.53: Mat foundation shear in Y-direction

## Slide 249: 3.9.1.4 Mat foundation punching shear check
Two-way shear strength provided by concrete, Vcp, for two-way slabs as follow:
(Equation 3.94)
Where:
: Perimeter of critical section for two-way shear in slabs and footings.
= Scale factor based on the location of the critical section. 40 for
interior columns.
= Ratio of the maximum to the minimum dimensions of the critical section.

## Slide 250: 3.9.1.4 Mat foundation punching shear check
Column C1 shown in Figure 3.54 is chosen to be checked for punching manually.

## Slide 251: 3.9.1.4 Mat foundation punching shear check
- Vu=3000 KN
- 0mm
-
-
-
Then,
=.
So,
Vc/Vu= 0.4<1, its ok

## Slide 252: 3.10.1 Design of beams
According to ACI 318-11, development length for deformed bars in tension, Ldt is:
Where: Ldt : Development length in tension of headed deformed bars
This value is increased by 30% for beams of effective depth, d>300 mm

## Slide 253: 3.10.1 Design of beams
When hooks are used for tension steel, Ldt is reduced to Ldh as follow:
Where: Ldh: development length in tension of deformed bars with
standard hooks
Splicing extends a minimum distance, Lds , as follow:
Lds=1.3 Ldt (Equation 3.97)
Where: Lds: Minimum splicing length

## Slide 254: 3.10.1 Design of beams
Figure 3.57 shows flexural steel for beam B1 from Etabs.
From Figure 3.57, Reinforcement can be taken as follow:
Top steel= 972 mm2= 5Փ16
Bottom steel= 771 mm2= 4Փ16

## Slide 255: 3.10.1 Design of beams
Lds=1.3 Ldt = 1000 mm

## Slide 256: 3.10.1 Design of beams
According to ACI 3188-11:
Stirrups spacing shouldn’t exceed d/2
In seismic design:
Minimum stirrups bar is10 mm
Seismic hooks are used in stirrups

## Slide 257: 3.10.1 Design of beams
For torsion stirrups, spacing shouldn’t exceed the following limit:
Where: Ph: Perimeter of centerline of outermost closed stirrup, mm

## Slide 258: 3.10.1 Design of beams
Table 3.16 shows shear reinforcement ratio from Etabs.
From Figure 3.D, = 0.248 mm2/mm

## Slide 259: 3.10.1 Design of beams
Vu=202 KN, Tu=0 KN
Acp=bw×h=320000 mm2
Pcp= 2(b+h) =2400
Assuming Փ12 mm stirrups, and 40 mm cover, then:
A0h= (bw-2× (40+12/2)) × (hw-2× (40+12/2)) =218046 mm2
Ph=2× (bw-2× (40+12/2)) +2× (hw-2× (40+12/2)) =2032 mm
A0=0.85× A0h=185354.8 mm2
Based on Equation3.51, Tth = 14.11 KN
Compatibility torsion = 4×14.11= 56.44 KN.m

## Slide 260: 3.10.1 Design of beams
Then, the dimensions are proper.

## Slide 261: 3.10.1 Design of beams
Transfer steel:
/m
Longitudinal steel:

## Slide 262: 3.10.1 Design of beams
Combining Torsion and Shear Stirrups:
Where: : Torsion and shear transfer steel ratio
n: Number of stirrups legs

## Slide 263: 3.10.1 Design of beams
According to ACI 318-11, minimum transfer steel is:
( )min = max (Equation 3.100)
For Beam B1:
= 1200 mm2/m
( )min =333 mm2/m < 967 , Use 1200 mm2/m

## Slide 264: 3.10.1 Design of beams
Assuming 1Փ10 stirrup, Av+t=2×78.5= 157mm2
Then, the spacing= 157/1200= 130 mm
= 250 mm> 188 mm
Use 1/100 mm

## Slide 265: 3.10.1 Design of beams
Combining Torsion and Flexural Longitudinal Steel:
Figures 3.58 shows Beam B1 detailing done using AutoCAD software

## Slide 266: 3.10.1 Design of beams
Combining Torsion and Flexural Longitudinal Steel:
Figures 3.59 shows Beam B1 detailing done using AutoCAD software

## Slide 267: 3.10.2 Design of columns
According to ACI 318-14, section 18.7, and based on the column information in the verification structural analysis section, this column has been chosen to be designed.

## Slide 268: 3.10.2 Design of columns
Transverse reinforcement
Transverse reinforcement over the lengths , shall be designed to resist shear assuming shear strength provided by concrete ) = 0 when both (a) and (b) occur:
(a) The earthquake-induced shear force, calculated in accordance with 18.7.6.1, is at least one-half of the maximum required shear strength within .
(b) The factored axial compressive force including earthquake force less than .

## Slide 269: 3.10.2 Design of columns
Length ℓo shall be at least the greatest of (a) through (c):
(a) The depth of the column at the joint face or at the section where flexural yielding is likely to occur, h.
(b) One-sixth of the clear span of the column, H/6.
(c) 450 mm
Then,
Vc >> design as column
mm
So,

## Slide 270: 3.10.2 Design of columns
Table 3.31 shows the Rebar area for hoops.
But there is a transverse reinforcement required for the special column

## Slide 271: 3.10.2 Design of columns
Spacing of transverse reinforcement, S, shall not exceed the smallest of (a) through (c):
(a) One-fourth of the minimum column dimension, b/4.
(b) Six times the diameter of the smallest longitudinal bar, 6.
(c) , as calculated by:
(Equation 3.101)
, shall not exceed 150 mm and need not be taken less than 100 mm.
mm >>use =70mm

## Slide 272: 3.10.2 Design of columns
Seismic hooks
According to ACI 318-14, Table 25.3.2, The type of seismic hook used for hoops is 135-degree hook, the minimum inside bend diameter (R=4ds), and the straight extension (ℓext= 6ds).
So, the length of hook equal to 100 mm.(10mm hoops dimeter)

## Slide 273: 3.10.2 Design of columns
Sections Reinforcement:

## Slide 274: 3.10.3 Design of special wall piers
Boundary elements steel is calculated as follow:
Where:
Փ: Section capacity reduction factor
Փ =

## Slide 275: 3.10.3 Design of special wall piers
Figure 3.62 shows dimensions of the boundary elements.
From Figure 3.22, Mu= 7431 KN.m and Pu= 4394 KN

## Slide 276: 3.10.3 Design of special wall piers
= -6846 mm2, So no need for compression steel
As tension= 4038 mm2
Using Փ20 bars, As=13Փ20mm
In order to guarantee proper spacing between bars, use 15Փ20 m

## Slide 277: 3.10.3 Design of special wall piers
:
Ag= (4000-2×600) ×500= mm2
As compression=0
Use As min = 0.025×1.4×106 = 3500 mm2
= 1Փ12/200 mm at each side of the wall

## Slide 278: 3.10.3 Design of special wall piers
Shear design
The minimum length of condensation zone is:
l0= Min (Equation 3.104)
Where: hn: Wall clear height
L: Wall Length
b: Wall thickness

## Slide 279: 3.10.3 Design of special wall piers
Shear design
The maximum spacing in condensation zone is:
S= Min (Equation 3.105)
Where: db: Bar diameter, mm
S0= Min >= 100 mm (Equation 3.106)

## Slide 280: 3.10.3 Design of special wall piers
Shear design
Maximum spacing in zones other than condensation zones is :
S= Min (Equation 3.107)
Figure 3.63 shows shear steel ratio from Etabs for Wall F.
,

## Slide 281: 3.10.3 Design of special wall piers
Shear design
For boundary elements:
l0= 700 mm
S0= 150 mm
Spacing in condensation zoon, S = 120 mm
Spacing in other zones, S = 120 mm
As a result, use 1/100mm for all zones of the boundary elements.

## Slide 282: 3.10.3 Design of special wall piers
Shear design
Figure 3.64 shows the final reinforcement of wall F.

## Slide 283: 3.10.4 Design of special wall spandrel.
After compared between Etabs results and manual results, the same element was chosen in the previous section to complete the design and show details of the reinforcement.
The length of the Spandrel (L)=1.2m.
Section dimensions:

## Slide 284: 3.10.4 Design of special wall spandrel.
Requirements for shear reinforcement:
The transverse reinforcement in each diagonal group should not be less than the following:
Where:
S = Center-to-center spacing of transverse reinforcement.
bc = Cross-sectional dimension of member core measured to the outside
edges of the transverse reinforcement composing area Ash.

## Slide 285: 3.10.4 Design of special wall spandrel.
The transverse reinforcement having dimensions of at least bw/2 in the direction parallel to bw and bw/5 along the other sides and spacing of the hoops according to ACI-318-14, section 18.7.5.3. statement (c).
Use transverse reinforcement (0.200.20) m.

## Slide 286: 3.10.4 Design of special wall spandrel.
Based on section 3.2, (
Then,
use 8 Φ22 in each group.
S=min(6)
Where: 100mm<150 mm.
So, mm, So S=100mm.

## Slide 287: 3.10.4 Design of special wall spandrel.
Then,
So, use 1Φ10/100mm
The minimum area of horizontal and vertical shear reinforcing in the spandrel as follows:
So,

## Slide 288: 3.10.4 Design of special wall spandrel.
Figure 3.65 shows the
Spandrel reinforcement
and hoops detailing.

## Slide 289: 3.10.5 Design of mat foundation
Mat foundation shear design
Figure 3.66 shows the applied
shear on the foundation at grid F.

## Slide 290: 3.10.5 Design of mat foundation
- Vu=703 KN/m
- ՓVc= 665 KN/m
Then,
the shear resisted by steel, Vs= 50.7 KN/m
Also, Av/s= Vs/(fy×d) =50.7/(420×960)= 126 mm2/m
But (Av/s) min=0.35bw/fy=835mm2/m
So, Av/s= 835mm2/m.
Use 2 legs of Փ12 /30 cm spacing for 1.0 m wide in areas required.

## Slide 291: 3.10.5 Design of mat foundation
Flexural design of mat foundation
The minimum steel percentage for slabs is 0.18%.
Then,
As,min =0.0018×1000×1000= 1800 mm2 /m.
Use As,min = 5Փ22 = 1900 mm2/m

## Slide 292: 3.10.5 Design of mat foundation
Figure ‎3.67: Mat foundation bottom flexural steel in X-direction contour resulted
by SAFE.

## Slide 293: 3.10.5 Design of mat foundation
Figure ‎3.68: Mat foundation Top flexural steel in X-direction contour resulted by SAFE.
>>Minimum steel
is not sufficient

## Slide 294: 3.10.5 Design of mat foundation
References:
American Concrete Institute’s Building Code Requirements for Structural Concrete (ACI 318-14)
American Petroleum Institute (API 1987)
ASCE 7-10: Minimum Design Loads for Buildings and Other Structures (American Society of Civil Engineers).
IBC 2012: International Building Code.
Israeli Code for Seismic Design SI-413.
Jordanian Code for Loads – 2006.
Principles of Foundation Engineering, Eighth Edition Braja M. Das
Reinforced Concrete Mechanics and Design 7th Edition, James K. Wight
Response of Multistory Concrete Structures to Lateral Forces (ACI SP-36)