## Slide 1
An-Najah National University
Faculty of Engineering & Information Technology
Department of Building Engineering
Pharmaceutical factory
Suha Saleh
Abeer Ghannam
 Prepared by 
Lana Melhem
Rula Qaroot

## Slide 2
Architectural Design.
Environmental Design.
Structural Design.
Electrical design
Mechanical And Safety Design.
Quantity Survey And Cost Estimation.
Outline:

## Slide 3
Architectural Design

## Slide 4
Site Analysis
Total area is 8200m2
wind speed is 5.4 km/hour
The annual average humidity is 75%

## Slide 5
Site plan
N

## Slide 6
Factory Block

## Slide 7
Production floor

## Slide 8
Injection
Tablet
Liquid
Capsule
Semi solid
Drop

## Slide 9
1
2
3
4
Material flow

## Slide 10
Personnel flow
One way flow
Two way flow

## Slide 11
2. Laboratory floor

## Slide 12
Warehouse

## Slide 13
Administration

## Slide 16: Environmental Design

## Slide 17
Environmental Design

## Slide 18
External wall
Thermal Analysis
U-Value = 0.521 W/m2.k
Roof:
U-Value = 0.307 W/m2.k

## Slide 19
Energy simulation
Cooling Load = 103.4 kW
Heating Load = 98.24 kW

## Slide 20
Structural Design

## Slide 21
Structural blocks distribution

## Slide 22
Concrete structure(A)
.One way ribbed slab
Concrete Fʹc= 28 MPa for all elements
Allowable Bearing Capacity of Soil = 180kN/m²
Loads:
Super imposed load = 4 kN/m²
Live load = 5 kN/m²
Model from ETABS

## Slide 23
One way ribbed slab with 33 cm slab thickness
Main beam 700*330 and 400*330 for secondary beam
400*400 column section
      Primary dimensions

## Slide 24: Seismic Design Data
Importance factor, I = 1.5
Soil Profile Type is SD
R = 5.5
Ca = 0.28
Cv= 0.4
Location → Nablus
Zone =2B → Z=0.20

## Slide 25
Load type | Manual value (kN) | ETABS value (kN) | % error
Live load | 7297 | 7297 | 0
SID load | 13938 | 13893 | 0.3
Dead load | 14353 | 14530 | 1.2
      Model Validation
Compatibility
Equilibrium check
Local equilibrium checks
column | Manual force(kN) | ETABS value(kN) | % difference
C3 | 440 | 444 | 0.9
Beam | Manual moment(kN.m) | ETABS value(kN.m) | % difference
B1 | 340 | 353 | 2
slab | Manual moment(kN.m)/m | ETABS value(kN.m)/m | % difference
1 | 50 | 52 | 3.8

## Slide 26
Period check:
T calculated = 0.314 sec
From ETAB 0.3 sec
∆M =0.7*5.5*5 =19.25mm < 0.025 (5) *103 = 125mm
Drift check:
Where elastic deformation from ETAB 5mm
∆M =0.7R∆S < 0.025(h story)
      Seismic checks
Period from ETAB < 1.4 T manual

## Slide 27
      Results:

## Slide 28
Slab section

## Slide 29
Beam details

## Slide 30
Column details

## Slide 31
Stair details
Shear wall details

## Slide 32
Floating slab details

## Slide 33
Footing details
Combined footing
Isolated footing

## Slide 34: Structural Design of Store

## Slide 35: Design Criteria
Structure is designed to carry the following loads:
  Own weight of structural members and covering material
  Solar panels that will be mounted above the roof (approximately 50 kg/m2)
  AC units and HVAC system (approximately 50 kg/m2)
  Snow load (50 cm) and an accidental live load (2 kN/m2)
  Wind load considering the design wind speed is 120 km/hr
Double galvanized steel with 5 cm insulation (sandwich panel) 32 kg/m2
Grade 36 steel (Fy=250 MPa) is used for all structural steel members

## Slide 36: Modeling of store using SAP2000
Building is modelled using SAP2000
Preliminary analysis and design were performed using SAP2000
Five major groups of sections were selected
Model is checked manually for:
    Compatibility check (structure is compatible)
    Equilibrium check (Structure is under equilibrium)
    Joint Equilibrium (joints are under equilibrium)

## Slide 37: Final sections and grouping
Group | Section | Applied load/design strength ratio
Interior strip of columns | Tubo260X260X16 | 0.95
Exterior strips of columns | Tubo200X200X16 | 0.5
Top and interior truss members | Tubo120X120X8 | 0.87
Bottom chord members | Tubo200X140X12.5 | 0.7
Bracing and purlins | Tubo60X42X4 | 

## Slide 38: Manual Design and checks
The following manual design steps were performed to account for all possible failure:
    Fracture limit state
    Local buckling for all sections
    Deflection of truss
    Lateral bracing for trusses and frames
    Connections detailing
    Design of base plate and footings

## Slide 39: Truss and frame bracing

## Slide 40: Trusses bracing

## Slide 41: Connection of members

## Slide 42: Connection of frame and truss bracing

## Slide 43: Footing Detailing

## Slide 44: Solar system design
Type of distribution | Dimension | Area of module | # of modules | Total area | Production
Flat | (1.58*0.808) | 1.2766 | 600 | 765.96 | 144Mwh
Landscape | (1.58*0.706) | 1.11548 | 360 | 401.57 | 88.4Mwh
portrait | (1.38*0.808) | 1.11504 | 400 | 446.016 | 103Mwh

## Slide 45
22kwh /m2
20.2kwh /m2
Result
4.5

## Slide 46
safety system

## Slide 47
Electrical Design

## Slide 48: Manufacturing area
IP=65
Results
Surface | Finish marital | Reflection factor
Ceiling | Vinyl coated gypsum panels | 75%
Wall | Epoxy paint CMU | 50%
Floor | Epoxy | 25%

## Slide 49: Laboratory

## Slide 50
Warehouse

## Slide 51
Administration

## Slide 52
Energy consumption
Space | Energy consumption (kwh/m2/a)
Manufacturing area | 24
Laboratory | 15
Warehouse | 17
Administration | 22
In avg. energy consumption = 20.2 kwh /m2/a

## Slide 53
Mechanical Design

## Slide 55
3) HVAC system design
The mechanical design in our project is water to air system design ,by using the chilled water system, boiler feed water system,
and Supply Air Handling Systems.

## Slide 56
Heating System
.
Heating of primary air is accomplished using hot water .
Incoming ventilation air in colder climates is heated utilizing separate hot water system with a concentration of propylene glycol to prevent water system freezing.

## Slide 57
Cooling System
.
Cooling of facility systems is accomplished utilizing chilled water.
If the process does not require the lower temperatures of chilled water, condenser water can be a cost effective solution, as it does not require the additional energy of the mechanical refrigeration process .

## Slide 58
Design for pressure
.
Product contamination was controlled by the use of:
positive and negative pressurization utilizing airlocks.
Specific process step | Room classification
Processes including media and buffer prep | D or C
Purification | C
Product filling | B
Actual point of fill | A

## Slide 59
Design for cleanliness
.
In order to achieve specific cleanliness classifications, clean, HEPA filtered air is provided to the space.

## Slide 60
Quantity survey & cost estimation

## Slide 61
Item | Form work (m2) | Concrete (m3) | Steel Ton
T.B | 645.4 | 61.8 | 6.18
B | 1135 | 445.23 | 44.6
Sub total | 1780.4 | 506.63 | 50.78
Cost/ unit Nis | 25 | 300 | 2600
Total cost | 44510 | 151989 | 132028
Beams and tie beams:
Quantity survey & Cost estimation
Total cost of beams and tie beams = NIS 328527

## Slide 62
Shear walls and columns:
Quantity survey & Cost estimation
Item | Form work (m2) | Concrete (m3) | Steel Ton
Columns | 652.8 | 140 | 9.14
Shear Walls | 829.3 | 568 | 8.17
Sub total | 1482.1 | 708 | 17.31
cost / unit Nis | 25 | 300 | 2600
Total cost | 37052.5 | 212400 | 4500
Total cost of shear walls and columns= NIS 253952.5

## Slide 63
Slabs:
Quantity survey & Cost estimation
Item | Form work (m2) | Concrete (m3) | Steel Ton
Slab | 11680 | 1320 | 620
Sub total | 11680 | 1320 | 620
cost / unit NIS | 25 | 300 | 2600
Total cost | 290000 | 396000 | 1612000
Total cost of slab = NIS 22983000

## Slide 64
Footings:
Quantity survey & Cost estimation
Item | Steel Ton | Excavation (m3) | Concrete (m3) | Formwork
Footing | 6.98 | 636 | 634 | 563
cost / unit NIS | 2600 | 25 | 300 | 25
Total cost | 18148 | 1575 | 190200 | 14075
Total cost of footing = NIS 223998

## Slide 65
Finishing works:
Quantity survey & Cost estimation
Item | Quantity | Unit | Cost / unit Nis | Total cost
Plastering | 6540 | (M2) | 16 | 104640
Painting | 4180 | (M2) | 17 | 71060
Epoxy painting | 2360 | (M2) | 370 | 873200
Tiling | 5578 | (M2) | 50 | 278900
Stone | 3524 | (M2) | 110 | 387640
mortar | 5623 | (M2) | 20 | 112460
Total cost of slab = NIS 1827900

## Slide 66
Final quantity & cost for the blocks:
Quantity survey & cost estimation
Item | Quantity | Unit | Cost/NIS | Total cost
Concrete | 3216.63 | CM | 300 | 964989
Steel | 803.07 | Ton | 2600 | 2087982
Excavation | 636 | CM | 25 | 15900
Formworks | 50622.6 | SM | 25 | 1265565
Finishing work | 27805 | ----- | ------ | 1827900
photovoltaic | ------ | -------- |  | 430740
lighting |  |  |  | 1986685
Mechanic (chiller, air handling unit,duct ) |  | ---- | ----- | 6874363.2

## Slide 67
Total cost of the blocks = NIS 15960924.2
Final cost for the block:
Quantity survey & cost estimation