## Slide 1: An-Najah National University Faculty Of Engineering Civil Engineering Department Graduation Project II
Analysis and Redesigned of Water Distribution Network and Design of Wastewater Network for 'Illar Town
Prepared By :
Ameed Tayeh
Ahmad Kmail
Obada Zaid
Supervision of Dr. Anan Jayyousi

## Slide 2: Outline:
Objectives of the project.
Study area.
Questionnaire analysis.
Analyzing the water distribution network.
Redesign of water distribution network.
Design of wastewater collection network.
Summary.

## Slide 3: Objectives
Analyze the existing water network.
Redesign the water network in the town.
Design the Wastewater network in the town.

## Slide 4
Study area

## Slide 5: Study area
Location : 'Illar town is located 10 kilometers northeast of Tulkarm.
Climate : The annual average maximum temperature is 21.5Co and the annual average minimum is 14.4Co

## Slide 6: Study area
Population : The total population of the town was 7456 capita in 2017.
Water resources : 'Illar town have three main water resources and it sells water to the near villages .

## Slide 7
Well 1
Well 2
Zeeta village
Receiving tank
Main tank
Kufr Ra'I village
Seda village
town's houses

## Slide 8: Questionnaire analysis

## Slide 9: Questionnaire analysis
Per Capita Water Consumption Rate
Chart: Family size
| 4 | 4 | 4 | 10 | 5 | 5 | 5 | 5 | 8 | 5 | 9 | 6 | 6 | 2 | 8 | 7 | 3 | 2 | 4 | 9 | 10 | 6 | 5 | 3 | 7 | 5 | 7 | 2 | 7 | 8 | 8 | 7 | 3 | 5 | 3 | 3 | 7 | 6 | 3
 | 141.6667 | 108.3333 | 141.6667 | 83.3333 | 113.3333 | 100 | 46.6667 | 93.3333 | 137.5 | 0 | 92.5926 | 111.1111 | 111.1111 | 216.6667 | 83.3333 | 71.4286 | 100 | 250 | 166.6667 | 44.4444 | 110 | 66.6667 | 86.6667 | 366.6667 | 95.2381 | 66.6667 | 57.1429 | 250 | 142.8571 | 62.5 | 83.3333 | 166.6667 | 188.8889 | 200 | 433.3333 | 166.6667 | 47.619 | 177.7778 | 222.2222

## Slide 10: Questionnaire analysis
Sources of Water
Chart: 
| مياه بلديه | بئر مياه(بئر تجميع) | مياه بلديه وبئر تجميع
20 | 18 | 1 | 20

## Slide 11: Questionnaire analysis
Effect of Existing of Yard on Water Consumption
Chart: Exsisting of Yard
| Q13 | no | yes | yes | yes | yes | no | no | no | yes | yes | yes | yes | yes | yes | no | yes | no | yes | no | yes | yes | yes | no | yes | yes | no | no | yes | yes | yes | yes | yes | no | yes | yes | yes | yes | yes | no
 | 141.6667 | 108.3333 | 141.6667 | 83.3333 | 113.3333 | 100 | 46.6667 | 93.3333 | 137.5 | 0 | 92.5926 | 111.1111 | 111.1111 | 216.6667 | 83.3333 | 71.4286 | 100 | 250 | 166.6667 | 44.4444 | 110 | 66.6667 | 86.6667 | 366.6667 | 95.2381 | 66.6667 | 57.1429 | 250 | 142.8571 | 62.5 | 83.3333 | 166.6667 | 188.8889 | 200 | 433.3333 | 166.6667 | 47.619 | 177.7778 | 222.2222

## Slide 12: Questionnaire analysis
Chart: Quality of Water
| excllent | very good | good | bad
 | 14 | 7 | 15 | 3

## Slide 13: Questionnaire analysis
Chart: Main Water Problem
| cl | sand | rust
cl sand rust | 11 | 3 | 1

## Slide 14: Questionnaire analysis
Effect of Income on Water Consumption
Chart: Income *1000
| 3 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 3 | 2 | 1 | 1 | 1 | 1 | 2 | 1 | 2 | 2 | 1 | 2 | 1 | 1 | 2 | 1 | 1 | 3 | 2 | 1 | 2 | 2 | 3 | 1 | 2 | 2 | 2 | 2 | 3 | 2
 | 141.6667 | 108.3333 | 141.6667 | 83.3333 | 113.3333 | 100 | 46.6667 | 93.3333 | 137.5 | 0 | 92.5926 | 111.1111 | 111.1111 | 216.6667 | 83.3333 | 71.4286 | 100 | 250 | 166.6667 | 44.4444 | 110 | 66.6667 | 86.6667 | 366.6667 | 95.2381 | 66.6667 | 57.1429 | 250 | 142.8571 | 62.5 | 83.3333 | 166.6667 | 188.8889 | 200 | 433.3333 | 166.6667 | 47.619 | 177.7778 | 222.2222

## Slide 15: Analyzing the Network

## Slide 16: Modeling of WDN

## Slide 17
Number of Elements | Elements
1 | Reservoirs
218 | Nodes
243 | Pipes
2 | Valves (FCV)

## Slide 18: WDN
Design constraints:
Pressure at junction between (20-100) m.H2O.
Velocity in pipe (0.3-3.0) m/s.

## Slide 19: Result of analysis of WDN
Pressure at minimum demand (4:00 am).
Chart: Junction Number

## Slide 20
Pressure at maximum demand (2:00 pm).
Chart: Junction Number

## Slide 21: Result of analysis of WDN
Velocities at minimum demand (4:00 am).
Chart: Pipe Number

## Slide 22
Velocities at maximum demand (2:00 pm).
Chart: Pipe Number

## Slide 23: Redesign of WDN

## Slide 24: Data of future population
Future population in 2037 = 10822

## Slide 25: Model of WDN

## Slide 26: WDN
Number of Elements | Elements
1 | Reservoirs
206 | Nodes
231 | Pipes
14 | Valves (PRV)

## Slide 27: Design Criteria
Pressure criteria from 20 to 100 mH2O.
Velocity criteria from 0.3 to 3 m/sec.

## Slide 28: Results of WDN for Design
Pressure at minimum demand (4:00 am).
Chart: Junction Number

## Slide 29: Results of WDN for Design
Pressure at maximum demand (2:00 pm).
Chart: Junction Number

## Slide 30: Results of WDN for Design
Velocity at maximum demand (2:00 Pm).
Chart: Pipe Number

## Slide 31: Results of WDN for Design
Velocity at minimum demand (4:00 am).
Chart: Pipe Number

## Slide 32: Cost estimation
Diameter (in) | Length (m) | Unit Price /m |  | Total Price
1 | 14593 | 95 |  | 1386335
2 | 7732 | 115 |  | 889180
3 | 428 | 130 |  | 55640
4 | 314 | 211 |  | 66254
6 | 752 | 274 |  | 206048
8 | 21 | 330 |  | 6930
 |  |  | Total | 2610387
VULVE | NO. | COST/1VULVE | Total cost
PRV | 14 | 5000 | 70000
TOTAL COST | 2680387 NIS
TOTAL COST | 725000 $

## Slide 33: Design of Wastewater network

## Slide 34
WWCN
Conduites
Manholes
Outfalls
Length <=30
Diameter>=8in
Material (PVC)
n
Diameter
Drop Manhole
Material
Loads
Elevation
Location
Elevation
Slope

## Slide 35: Wastewater Generation
From the State Of Palestine Water Authority (PWA), the average municipal consumption is 120 L/C/Day.
Design period 35 years.
PF = so we take PF = 3.
85% of produced waste water from consumed water.
20% infiltration.
Total flow for the town 4867m3/day

## Slide 36: Design Criteria
The velocity : (0.6 – 3 m/sec)
The cover : (1-5m)
The slope : (1-12%)
The distance between manholes are less than 30 m.

## Slide 37: Model of the wastewater network

## Slide 38
Loads on manholes
So the load on each manhole is = = 6.446 m3/day.
The load was entered on the manholes equally through sanitary load control center in SewerCAD program.

## Slide 40: The Outfalls

## Slide 42: Abu Al-Nar Wadi

## Slide 43: Massin Wadi

## Slide 44: Results

## Slide 45: Slope Result
Chart: Number Of Conduate

## Slide 46: Velocity Result
Chart: Nomber Of Conduate

## Slide 47: Cover Result
Chart: Cover Start

## Slide 48: Cover Result
Chart: Cover Stop

## Slide 49: Profile

## Slide 50: Cost estimation

## Slide 51: Cost estimation
 | Unit | Quantity | Unit price ($) | Total price ($)
conduits cost | m | 15,455 | 40 | 618200
excavation and filling and paving cost | m | 15,455 | 30 | 463650
manholes cost | number | 755 | 650 | 490750
 |  |  | total cost | 1572600

## Slide 52: Summary

## Slide 53: Summary

## Slide 54: Cost sharing per house hold