## Slide 1: Structural Design for Host Mall

## Slide 2: Outline
location & Description.
Material properties.
Slab system & load transfer.
Preliminary design & Load calculations.
3D sap model.
Static design.
Dynamic analysis.
Final design.

## Slide 3: location & Description
The structure is a commercial building, It is located at Ramallah city.
with 12 stories.
The building has many functions:-
  parking lots
  shopping centers
  business offices.
Architectural plan.

## Slide 5: Material properties.
MATERIAL | TYPE | PROPERTIES
Reinforced con (beam &slab) | Structural | fc’ = 28MPa
Reinforced con (column) | Structural | fc’ = 35MPa
Reinforcement steel | Structural | fy = 420MPa
MATERIAL | TYPE | PROPERTIES
Sand | Non-structural | γ = 20
Plain concrete | Non-structural | γ = 24
Block | Non-structural | γ = 12
Stone | Non-structural | γ = 26
Tile | Non-structural | γ = 28
Mortar | Non-structural | γ = 23

## Slide 6: Structural System
To design the building we choose
  Two way solid slab.
to achieve best condition in load transfer.

## Slide 7: Load transfers

## Slide 8: Preliminary design & Load calculations
 | SS | OEC | TEC | CANT.
OWSS | L/20 | L/24 | L/28 | L/10
Beam Or OWRS | L/16 | L/18.5 | L/21 | L/8
min thickness for beam :
We use beam 60 X 40 cm

## Slide 9: Slab thickness
h min
we take hmin= 0.2 m
= 0.15m

## Slide 11: To check if the thickness is sufficient or not
 ∑αfm
αfm = =
= 3.61
check it for shear :
Maximum ultimate shear on slab
Vu=W (Ln/2 – d)
Vu =60 KN
Shear capacity for slab:
ɸVc= 1/6 x ɸ x x bw x d /1000
ɸVc =105.8 KN
So the thickness of slab is ok.

## Slide 12: Load calculations
Superimposed dead load = 0.025 x28 + 0.025 x23 +0.1 x20 = 3.3KN/m²
The own weight of slab = 25x0.2x1 = 5 KN/m²

## Slide 13
Partitions own weight = 1 KN/m²
Masonry wall own weight = 3.5 (0.1 x12 + 0.11 x24 +0.07x 26 +0.02 x23)
= 21KN/m run
Fall sealing = 0.2KN/m²
Live load = 4.79KN/m²

## Slide 14: Load combination
  For ultimate load we use :-
U = 1.4 D
U = 1.2 D + 1.6 L
U = 1.2 D + 1.0 E + 1.0 L
U = 0.9 D + 1.0 E

## Slide 15: SAP MODEL VERIFICATIONS :-
Compatibility
Compatibility is ok as the model move as a one unit.
Equilibrium
  TOTAL Building own weight by hand = 4637.92 KN
  TOTAL Building own weight from sap = 4674.492 KN KN
Error = (4637.92 – 4674.49)/4637.92 =0.788 %....ACCEPTED

## Slide 16: Stress-Strain relationship
Distributed load on the beam = 10.951KN/m
M= WL²/ 8 =11.3x6.25²/8 =53.473KN.m
The moment from SAP
Maximum Negative Moment From SAP
Maximum Positive Moment From SAP

## Slide 17
The moment from SAP = (44.3958/2)+29.0053
=51.203KN.m
Error calculation
Error =
= 4.24% < 5% OK

## Slide 18: Dynamic analysis
Structure period
We use two method to estimate the period :-
  T=
  = 1.20602 sec
  T=
  = 1.658741 sec
  Tsap = 1.31016 sec

## Slide 19: Seismic Hazard Map to Find Ss.

## Slide 20: Seismic Hazard Map to Find S1

## Slide 21: Site Soil type

## Slide 22: Value of Site coefficient Fa

## Slide 23: Value of Site coefficient Fv

## Slide 24: The Factors Used in the Analysis:
R=5.5
I = 1.00
Ss= 0.24
S1= 0.18
Site classification: B (Rock).
Fv= 1
Fa= 1
SMs= Fa×Ss= 0.24
SM1 = Fv×S1 = 0.18
SDs= 2/3(SMS)= 0.16
SD1= 2/3(SM1)= 0.12
SDs/2.5= 0.064

## Slide 25
Where:
Ss: The mapped spectral accelerations for short periods
S1: The mapped spectral accelerations for 1-second periods
Fa: Site coefficient for Ss
Fv: Site coefficient S1
SMS and SM1: Maximum spectral response acceleration
SDS and SD1: Design spectral response acceleration
R : Response modification factor
I : occupancy importance factor
CT and x: factors for calculating the fundamental period
Ta: Approximate the fundamental period
Cs: Seismic response coefficient

## Slide 27: Spectral Response acceleration curve.

## Slide 28
For X-direction:
  The scale factor for U1= = 1.78.
  The scale factor for U2= X 30%= 0.535.
  The result base shear in X direction=1419.973KN.
For Y-direction:
  The scale factor for U2= = 1.78.
  The scale factor for U1= X 30%= 0.535.

## Slide 29: Total Reactions for Response Spectral from SAP 2000

## Slide 34
Strip Section in MAT Foundation Y dir