## Slide 1: An-Najah National University Redesign of The Administrative Building of Hisham Hadid
Prepared by:
Tahani Al-Masri
Adan Abubaker
Alma Eid
Haneen Ahmad
Under Supervisor:
Monther Dwaikat

## Slide 2: Contents: 1. Introduction 2. Site Analysis 3. Architectural design 4. Structural Design 5. Environmental Design 6.Mechanical Design 7.Electrical Design 8.Safety Design 9. Cost Estimation

## Slide 3: Introduction *In this project, an integrated building design was created that keeps pace with the development of the times and meets basic needs.

## Slide 4: Site Analysis our building is located in Albalou near Police station in Ramallah. Areas Area of land which the building is built on equals to (1153) m². Figure(1):location of Hisham Hadid building.

## Slide 5: Site Analysis Temperature The average maximum temperature in the last year is 30 °C and minimum temperature is 12°C. Figure(2): Annual temperature for Ramallah city in 2021.

## Slide 6: Wind speed and its direction Wind speed at Ramallah in general is southwest with annual mean speed 18.6 Kmph in last year. Figure(3)Annual wind speed for Ramallah city in 2021.

## Slide 7: Rainfall The wettest month (with the highest rainfall) is February (63.2mm). Figure(4): Annual rainfall for Ramallah city in 2021.

## Slide 8: Architectural Aspect * General Information. * Floors , Elevations and Sections.

## Slide 9: General Information The Building includes eleven story. Total area equals to7007 m2.

## Slide 10: Basement The improvement is make the ramp works according to the standards. Figure 5: Basement floor plan

## Slide 11: Architectural Aspect First basement Figure 6: first Basement floor plan

## Slide 12: Ground floor Figure 7: ground floor plan

## Slide 13: First floor Figure 8: first floor plan

## Slide 14: Offices floor From the second to the fourth floor, the same division of floors. Figure 9: office floor plan

## Slide 15: Sections After Re-design Figure10 : sections

## Slide 16: Elevations After Re-design Figure : elevations

## Slide 17: 4. Structural Analysis

## Slide 18: Assumptions:
Codes Design:
1. Building Code Requirements for Structural Concrete ACI 318-14.
2. ASCE-16 for load computations.
3. Uniform Building Code (UBC 97)
Materials:
The materials that used in the design have the following properties:
1. Compressive strength for the concrete fʹc equals to 28 Mpa.
2. Yielding strength of the steel fy equals to 420 Mpa.
3. The concrete unit weight equals to 25 KN/𝑚3.

## Slide 19: Loads:

## Slide 20: Design:
* Slab System: U-Boot System Slab Weight of the voided slab = 6 KN/𝑚2
* Beams: vertical (400×600) and horizontal (400×500) * Columns: The dimensions of the columns = 1200mm & 500mm

## Slide 21: ETABS Structural Model:

## Slide 22: ETABS Checks
To ensure that the calculation is done correctly and to adopt the design results from ETABS; some checks are required::
compatibility check
Equilibrium check
Stress-strain check check
period check
Modal mass participate ratio check (MPMR)
Base shear Check:
drift check
All checks were done for the building and all were acceptable.

## Slide 23: Compatibility Check:

## Slide 24: * Equilibrium check:
Load Types | Manual (KN) | ETABS (KN) | Error (%)
Dead | 69209.07 | 68556.76 | 0.95
Live | 30433.66 | 30433.26 | 0.0013
SID | 22425.61 | 22190.30 | 1.06

## Slide 25: Period check
T = 0.0488× = 0.702 sec

## Slide 26: Mass participation check sum y = 93% sum x = 95% both are more than 90%
Sum UZ | Sum UY | Sum UX | UZ | UY | UX | Period | Mode | Case
 |  |  |  |  |  | sec |  | 
0 | 0.899 | 0.9049 | 0 | 0.0003 | 0.0005 | 0.054 | 30 | Modal
0 | 0.9038 | 0.9137 | 0 | 0.0049 | 0.0088 | 0.054 | 31 | Modal
0 | 0.906 | 0.9193 | 0 | 0.0022 | 0.0056 | 0.052 | 32 | Modal
0 | 0.9081 | 0.9196 | 0 | 0.0021 | 0.0003 | 0.051 | 33 | Modal
0 | 0.9167 | 0.9403 | 0 | 0.0086 | 0.0207 | 0.048 | 34 | Modal
0 | 0.9205 | 0.9411 | 0 | 0.0038 | 0.0009 | 0.048 | 35 | Modal
0 | 0.924 | 0.9447 | 0 | 0.0035 | 0.0035 | 0.046 | 36 | Modal
0 | 0.9265 | 0.9456 | 0 | 0.0025 | 0.001 | 0.044 | 37 | Modal
0 | 0.9267 | 0.9526 | 0 | 0.0002 | 0.007 | 0.043 | 38 | Modal
0 | 0.927 | 0.9546 | 0 | 0.0004 | 0.002 | 0.041 | 39 | Modal
0 | 0.9355 | 0.9546 | 0 | 0.0084 | 3.03E-05 | 0.041 | 40 | Modal

## Slide 27: Base reaction check
Output case | FX(KN) | FY(KN) | FZ(KN)
Dead | -0.0002 | -0.0001 | 64086.6537
Live | -0.0001 | -4.89E-05 | 30431.6593
SID | -0.0001 | 0.0003 | 22030.9859
EQX | 2460.0245 | 863.8805 | 0.0001
EQy | 888.2514 | 3708.6964 | 0.0002

## Slide 28: Drift check
Drift-limitation | Delta-y | Delta-X | Drift-y | Drift-X | Dis-Y | Dis-X | Height | Story
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
47 | 0.28105 | 0.16555 | 0.073 | 0.043 | 0.073 | 0.043 | 2350 | 1
47 | 0.64295 | 0.2926 | 0.167 | 0.076 | 0.24 | 0.119 | 2350 | 2
47 | 1.6324 | 0.6776 | 0.424 | 0.176 | 0.664 | 0.295 | 2350 | 3
66 | 3.25325 | 3.11465 | 0.845 | 0.809 | 1.509 | 1.104 | 3300 | 4
66 | 4.79325 | 13.22475 | 1.245 | 3.435 | 2.754 | 4.539 | 3300 | 5
66 | 7.58835 | 18.1258 | 1.971 | 4.708 | 4.725 | 9.247 | 3300 | 6
66 | 6.8838 | 21.7833 | 1.788 | 5.658 | 6.513 | 14.905 | 3300 | 7
66 | 7.86555 | 24.28965 | 2.043 | 6.309 | 8.556 | 21.214 | 3300 | 8
66 | 8.03495 | 26.86145 | 2.087 | 6.977 | 10.643 | 28.191 | 3300 | 9
66 | 8.05035 | 27.0809 | 2.091 | 7.034 | 12.734 | 35.225 | 3300 | 10
66 | 7.2149 | 26.4803 | 1.874 | 6.878 | 14.608 | 42.103 | 3300 | 11

## Slide 29: Column-beam-slab layout

## Slide 30: Column C1 detailing

## Slide 31: Beams design

## Slide 32: Shear wall design

## Slide 33: Footing Design

## Slide 34: Environmental analysis and Design.

## Slide 35: Environmental analysis and Design This section provides full details and analysis of Environmental Simulation and Design, including topics shown
Shading analysis
Sun path analysis
Daylight analysis
Energy Conservation measure(ECM)
Heating and cooling loads
Thermal comfort

## Slide 36
Summer shading analysis:
Sun shading simulation in summer at 8:00A.m.
Sun shading simulation in summer at 12:00 p.m.
The Shading Analysis was done for two periods, summer and winter, each case was evaluated in three different times for all building’s elevations to get accurate and detailed analysis.
Shading analysis

## Slide 37
Sun shading simulation in winter at 8:00A.m.
Sun shading simulation in summer at 2:00 p.m.
Winter shading analysis:
Sun shading simulation in winter at 8:00A.m.

## Slide 38
Sun shading simulation in winter at 12:00 p.m.
Sun shading simulation in winter at 2:00 p.m.

## Slide 39: Sun path analysis:
Sun path diagram illustrate how the sun impact our building through the day in both seasons, summer and winter.
sun path diagram at 8:00 a.m.in summer
sun path diagram at 12:00 p.m.in summer

## Slide 40
sun path diagram at 2:00 p.m.in summer
sun path diagram at 8:00a.m. in winter.

## Slide 41
sun path diagram at 12:00pm.in winter
sun path diagram at 2 :00 p.m.in winter.

## Slide 42: Daylight analysis:
recommended daylight factors.
This analysis calculates the Daylight Factor - the ratio between the interior and exterior illuminance levels of natural lighting. This factor is calculated under a CIE overcast sky model.
The daylight factor (DF%) values for each space in each floor was calculated, the results were compared with the standard range which is 2% - 5%.

## Slide 43: Passive design used to improve daylight factor inside the building Using of horizontal louvers On all facades:
a window blind or shutter with horizontal slats that are angled to admit light and air, but to keep out rain and direct sunshine. The angle of the slats may be adjustable, usually in blinds and windows, or fixed
louver balde geometry
Treatment and improve

## Slide 44: Daylight analysis after trewas done by using design builder, and the following results were obtained:
daylight analysis in roof floor.
daylight analysis fourth floor.

## Slide 45
daylight analysis third floor.
daylight analysis second floor

## Slide 46
daylight analysis first floor
daylight analysis ground floor

## Slide 47: Energy Conservation measure(ECM)
means a measure designed to reduce energy use, including alternative energy systems which replace conventional fuels with renewable resources.
Design builder simulation:

## Slide 48: Material used in office building constructions:
Wall layer :
external wall layers of the base model
material properites of external wall layers

## Slide 49
: roof layers of the base model
Roof layers:
material properites of roof layers.
roof layers of the base model

## Slide 50: Internal wall layers:
internal wall layers of the base model
material properites of internal wall.

## Slide 51
internal floor layers of the base model

## Slide 52
windows material
material properites of windows

## Slide 53
Artificial lighting:
-We use led with linear control lamp:
The most economical lighting template.
-We use infiltration of constant rate(ac/h)=0.3
-Fresh air(I/s-person)=6
-Change the size of windows
-In opening the revel of windows=0.3
-In HVAC we use VRF (Air-cooled).Heat Recovery,DOAS
We use horizontal louvers

## Slide 54
horizontal louvers in windows

## Slide 55
Site and source energy
Simulation heat gain.

## Slide 56
Heating and cooling loads :
Heating loss
This figure shows the temperature values and heat loos ,In addition
show the air ,radiant and operative temperatures in new design.
Total heating loads in buildings=90 kw

## Slide 57
Foor cooling load, this figure shows temperature ,heat gain ,sensible and latent cooling ,relative humidity ,ventilation and infiltration .As appear in the figure air temprrature and operative temperature have approximately the same value that is indicator a good insulation that used in external wall construction.
Cooling load
Total cooling loads=150kw

## Slide 58
The PMV SET value which expresses the expected average Vote for the amount of thermal comfort for building users, should be between (-0.5-0.5) and as shown in the graph above, the average Vote between this period, so we can conclude that the thermal design results are satisfactory during Months of the year
project comfort results
Thermal comfort

## Slide 59
 | Original building | New building
Total heating load (kw) | 277.89 | 90
Total cooling load (kw) | 304.2 | 150
Energy Consumption(KWh/m2) | 236.85 | 61.31
Comparing between thermal analysis for current office building and new design
thermal analysis for office building and new design

## Slide 60: Acoustical design
Room acoustics design:
Spaces taken for acoustics design:
1.office
OFFICE ROOM PLANE
MULTIPURPOSE HALL PLANE
2.MULTIPURPOSE HALL

## Slide 61: 4.Shops
3.meeting room
MEETING ROOM PLANE
Shops PLANE

## Slide 62: Literature review:
Articulation loss %
AL | Person satisfied with speech privacy(%) | Open-Office Speech Privacy Descriptor
0-0.5 | 95-92% | confidential
0.06-0.2 | 90-80% | Normal
0.21-0.3 | 79-65% | Minimal
>0.3 | <65% | Unacceptable
Recommended Noise Criteria(NC)is:NC35-NC40
Minimum STC required is40 dB.
The minimum impact insulation class required is 50 dB.

## Slide 63: Reverberation time
STI Range | case
0-0.3 | Bad
0.3-0.45 | poor
0.45-0.6 | Fair
0.6-0.75 | Good
0.75-1.0 | Excellent
Recommended reverbertation time
Sound transmission index cases
Sound transmission index(STI)

## Slide 64: Design
Normal partition layers and its stc
Normal partition

## Slide 65
glazed partition
Glazed partition layers and its stc

## Slide 66
STC and OTIC of the exterior wall
exterior wall

## Slide 67
STC of the ceiling
Internal floor
IIC of Internal floor

## Slide 68: Surface mount speaker design
:
wall speaker specifications
ATEO6
WALL SPEAKER WITH CLEVERMOUNT™ 6"

## Slide 69: reverbertation time design
Finishing materials used in rooms and its sound absorption coefficient.

## Slide 70: Meeting room
reverbertation time is within standard(0.60-1.20)sec

## Slide 71
office room
reverbertation time is within standard(0.40-0.70)sec.

## Slide 72
multipurpose hall.
reverbertation time is within standard(0.80-1.90)sec.

## Slide 73
SPL in multipurpose hall.
AL % value in multipurpose hall

## Slide 74
reverbertation time in shop.
shop.

## Slide 75
Direct sound pressure level in shop.
SPL in shop.
AL % value in shop

## Slide 76: HVAC System Design
VRF means VARABLE REFRIGERANT FLOW SYSTEM. This System consists of one Condenser Unit with multiple Indoor Units
Advantages:
1.no need to install ducts, cost reduction of installation
2.Power saving
3. mainly useful in public areas
Dis - Advantages
1.System is complicated when compare to Split units
2.this system required qualified / skilled man power

## Slide 77
Outdoor unit specification catalogue
Based on total cooling load we need two outdoor VRF unit with cooling capacity 106.5,61.5
Capacity cooling load required =61.5+106.5=218.5KW>150kw

## Slide 78: Indoor Unit
Fan coil unit was combined with a duct and a diffuser used in the internal spaces where the Toshiba fan coil units were used (AP0724H-E, AP0274H-E) with the capacity flow rate 1320 m3 /h and 3600m3/h
Fan Coil

## Slide 79: We use split unit in other floors

## Slide 80: Selecting Diffuser:
Diffuser calculation from the catalog MultiPurposeHall:
Vs= 1.88(m3/sec)
length room = 14.5m
width room = 14m
N(diffuser) = 1.88/(225/1000) ≈ 9.

## Slide 81
Basement floor
Return design:

## Slide 82: Main Return duct design
the (main return ducts) are designed for each room (use assume velocity =5 m/s):

## Slide 83
Duct & diffusers distribution in basement floor.

## Slide 84: Split unit in ground floor.

## Slide 85
Split unit in first floor.
Split unit in second floor

## Slide 86
Split unit in roof floor.

## Slide 87: FIREFIGHTING SYSTEM
Fire extinguishers system
Fire hose station:
the most common system used in the office building:
The chosen type is dry powder chemical they can be used for class A,class B &class c and electrical fire.

## Slide 88: DETECTION AND NOTIFICATION SYSTEAM
manual fire alarm
smock detector
Heat detector

## Slide 89: EMERGENCY STAIR
The following figure shows the emergency stair:

## Slide 90: Emergency sign and lighting design

## Slide 91: Emergency Lighting:
In the figure bellow show type of emergency lighting
VISOR LED
For use EM12 corridor 0B LED2S EL3 WH
Emergency rout sign

## Slide 92: Egress Route
Egress route for basement floor

## Slide 93
Egress route for ground floor

## Slide 94
Egress route for first floor

## Slide 95: Egress route for second floor

## Slide 96
Egress route for third floor
Egress route for fourth floor

## Slide 97: Egress route for roof floor

## Slide 98
Fire protection system for ground floor.
Fire protection system for basment floor.

## Slide 99
Fire protection system for first floor.
Fire protection system for second floor.

## Slide 100
Fire protection system for roof floor.

## Slide 101: Electrical Design DIALux program was used to design lighting system Some of spaces in the building Figure : Mayor room Figure : Meeting room

## Slide 102: Figure : Malty purpose hall Figure : clothing's shop

## Slide 104: Electrical Design
Outlets design
For Ground Floor
special load
I load= 7.6 Amp.
I cable = I Design *1.15*1.15 =7.6*1.15*1.15=11 A.
Copper wire is used with 2.5 mm²

## Slide 105: The allowable voltage drops in the wire= (3-5) % × 220V Table 1: Check for Drop voltage for each floor
Name | D.B.N | Drop voltage% | Cheek
B4 | D.B.1 | 1.2 % | Ok
B3 | D.B.2 | 1.2 % | Ok
B2 | D.B.3 | 1.2 % | Ok
B1 | D.B.4 | 0.4% | Ok
GF | D.B.8 | 0.6% | Ok
First Floor | D.B.12 | 0.46% | Ok
Second Floor | D.B.14 | 0.4% | Ok
Third Floor | D.B.16 | 0.4% | Ok
4TH Floor | D.B.18 | 0.4% | Ok
Roof Floor | D.B.20 | 0.066% | Ok

## Slide 106
.
Normal load:
The Table below has shown the calculation first Floor:
Table 2 : Current calculation for normal outlets
Normal load |  |  | 
Power Watt | V | Power Factor | I load (A)
Watt | Volt |  | Amp
600 | 220 | 0.9 | 3
I design =I load *1.15*1.15=3*1.15*1.15=3.96 Amp.

## Slide 107
Name | D.B.N | Drop voltage% | Cheek
B4 | E.D.B.1 | 0.13% | Ok
B3 | E.D.B.2 | 0.13% | Ok
B2 | E.D.B.3 | 0.13% | Ok
B1 | E.D.B.4 | 0.24% | Ok
GF | E.D.B.6 | 0.26% | Ok
1st | E.D.B.12 | 0.36% | Ok
2nd | E.D.B.14 | 0.36% | Ok
3rd | E.D.B.16 | 0.36% | OK
4th | E.D.B.18 | 0.36% | Ok
Roof | E.D.B.20 | 0.24% | Ok
Table 5: Wire Drop voltage calculation for normal outlets for each floor
We will use the wire between the circuit breaker and a normal loads with an area of cross section 2.5 mm and can be implemented 18 amps

## Slide 108
Lighting calculation:
D . B .12 the First floor, the critical room is offices 40 m, contains 8 lamps (35 watt).
Table 6: Current calculation for lighting
lighting load |  |  | 
Power Watt | V | Factor | I load (A)
Watt | Volt |  | Amp
280 | 220 | 0.9 | 1.41

## Slide 109
Name | D.B.N | Power | I | ρ | Max length | Area wire | resistance wire | Drop voltage % | check
B4 | E.D.B.1 | 280 | 1.41 | 1.68E-08 | 100 | 1.5 | 1.12 | 0.5% | ok
B3 | E.D.B.2 | 280 | 1.41 | 1.68E-08 | 100 | 1.5 | 1.12 | 0.5% | ok
B2 | E.D.B.3 | 280 | 1.41 | 1.68E-08 | 100 | 1.5 | 1.12 | 0.5% | ok
B1 | E.D.B.5 | 210 | 1.4 | 1.68E-08 | 30 | 1.5 | 0.34 | 0.22% | ok
G.F | E.D.B.9 | 475 | 3.17 | 1.68E-08 | 27 | 1.5 | 0.3 | 0.4% | ok
1ST Floor | E.D.B.12 | 280 | 1.86 | 1.68E-08 | 40 | 1.5 | 0.45 | 0.84% | ok
2nd Floor | E.D.B.14 | 210 | 1.4 | 1.68E-08 | 36 | 1.5 | 0.4 | 0.25% | ok
3rd Floor | E.D.B.16 | 210 | 1.4 | 1.68E-08 | 36 | 1.5 | 0.4 | 0.25% | ok
4th Floor | E.D.B.18 | 210 | 1.4 | 1.68E-08 | 36 | 1.5 | 0.4 | 0.25% | ok
Roof Floor | E.D.B.20 | 315 | 1.7 | 1.68E-08 | 12 | 1.5 | 0.13 | 0.1% | ok
Table 9 :Drop voltage wire calculation for lighting for each floor
We will use the wire to connect the lighting distribution panel in the cross-sectional area of 1.5 mm2

## Slide 110: Circuit breaker and distribution board
Power calculation:
Calculation for Single -phase equation:
Total current in EDB-20 (1Φ) = total power / (V × D.F)
= 4279.2 / (220 × 0.90)
= 22 Amp
The current load for the circuit breaker is = 1.15 × I
= 25Amp.
The current in the circuit breaker cable = 1.15 × I C.B
= 28 Amp.
Total current in the cable that connects the main E.D.B.20 panel distribution is 25, and will be used with the cable cross-section 6 mm2 area and can implement 31 amps.

## Slide 111
Name | Power Lighting | Normal | Special loads | total power load | Phase Type
E.D.B.1 | 1804 | 400 | 8000 | 9563 | one Phase
E.D.B.2 | 1804 | 400 | 8000 | 9563 | one Phase
E.D.B.3 | 1808 | 400 | 8000 | 9566 | one Phase
E.D.B.4 | 574 | 2400 | 1500 | 2679.2 | one Phase
E.D.B.5 | 1288 | 3200 | 1500 | 3490 | one Phase
E.D.B.6 | 670 | 2000 | 3000 | 4136 | one Phase
E.D.B.7 | 245 | 1200 | 0 | 556 | one Phase
E.D.B.8 | 975 | 2000 | 3000 | 4380 | one Phase
E.D.B.9 | 825 | 1800 | 3000 | 4200 | one Phase
E.D.B.10 | 565 | 2400 | 1500 | 2672 | one Phase
E.D.B.11 | 1008 | 3200 | 1500 | 3266.4 | one Phase
E.D.B.12 | 2058 | 17200 | 1500 | 8306.4 | one Phase
E.D.B.13 | 1295 | 4200 | 1500 | 3796 | one Phase
E.D.B.14 | 2520 | 12800 | 4000 | 9856 | one Phase
E.D.B.15 | 1295 | 4200 | 1500 | 3796 | one Phase
E.D.B.16 | 2520 | 12800 | 4000 | 9856 | one Phase
E.D.B.17 | 1295 | 4200 | 1500 | 3796 | one Phase
E.D.B.18 | 2520 | 12800 | 4000 | 9856 | one Phase
E.D.B.19 | 686 | 1800 | 1500 | 2588.8 | one Phase
E.D.B.20 | 924 | 6800 | 1500 | 4279.2 | one Phase
Table 12:Distribution board calculation for E.D.B

## Slide 112
D.B.N | total power load | Phase Type | I load | I C.B | I Cable | cross-sectional area
E.D.B.1 | 9563 | one Phase | 48.30 | 55.54 | 63.87 | 25 mm2
E.D.B.2 | 9563 | one Phase | 48.30 | 55.54 | 63.87 | 25 mm2
E.D.B.3 | 9566 | one Phase | 48.31 | 55.56 | 63.89 | 25 mm2
E.D.B.4 | 2679.2 | one Phase | 13.53 | 15.56 | 17.90 | 2.5 mm2
E.D.B.5 | 3490 | one Phase | 17.63 | 20.27 | 23.31 | 4 mm2
E.D.B.6 | 4136 | one Phase | 20.89 | 24.02 | 27.63 | 6 mm2
E.D.B.7 | 556 | one Phase | 2.81 | 3.23 | 3.71 | 2.5 mm2
E.D.B.8 | 4380 | one Phase | 22.12 | 25.44 | 29.26 | 6 mm2
E.D.B.9 | 4200 | one Phase | 21.21 | 24.39 | 28.05 | 6 mm2
E.D.B.10 | 2672 | one Phase | 13.49 | 15.52 | 17.85 | 2.5 mm2
E.D.B.11 | 3266.4 | one Phase | 16.50 | 18.97 | 21.82 | 4 mm2
E.D.B.12 | 8306.4 | one Phase | 41.95 | 48.24 | 55.48 | 16 mm2
E.D.B.13 | 3796 | one Phase | 19.17 | 22.05 | 25.35 | 6 mm2
E.D.B.14 | 9856 | one Phase | 49.78 | 57.24 | 65.83 | 25 mm2
E.D.B.15 | 3796 | one Phase | 19.17 | 22.05 | 25.35 | 6 mm2
E.D.B.16 | 9856 | one Phase | 49.78 | 57.24 | 65.83 | 25 mm2
E.D.B.17 | 3796 | one Phase | 19.17 | 22.05 | 25.35 | 6 mm2
E.D.B.18 | 9856 | one Phase | 49.78 | 57.24 | 65.83 | 25 mm2
E.D.B.19 | 2588.8 | one Phase | 13.07 | 15.04 | 17.29 | 2.5 mm2
E.D.B.20 | 4279.2 | one Phase | 21.61 | 24.85 | 28.58 | 6 mm2

## Slide 118: Mechanical design
Mechanical system is one of the most important systems that is required to be carefully designed for any building
According to table1, the average daily water consumption per person in offices is 57 liters (0.057 m³/day).
Volume of water needed for firefighting= (0.5 × 0.057 × 360 person) = 10.26 m³/day.
Total water demand/day= 20.52 + 10.26 = 30.78 m³/day.

## Slide 119
The amount of rainwater failing on the roof = 519 × 0.7 = 363.3 m3/year.= 1m3/day
The rainwater tank volume will be used = 364 m3
Volume of gray water tank
Volume = 360 person × 0.002 m 3 /day = 0.72 m 3 /day.
Municipality provides the water for the building every days.
10 tanks are used on roof with radius 0.75 m and 1.80m height.
The volume of one roof tank= (0.75 2 × 3.14 ) × 1.80 = 3.18 m 3 .

## Slide 123
Figure 10 Plan for water drainage
Figure 11 Plan for water drainage 2

## Slide 124: Total cost of building (NIS)=9599000 Total cost of building (NIS/m2)=1370 Table : Summary of cost estimation
activity | Cost (Nis)
Earth work | 626,500
structural work | 2913920
Architectural work | 4643340
mechanical work | 998340
Electrical work | 416900