## Slide 1: Development of a Facility Master Plan for Nablus City with Emphasis on Khalit Alamod Water Distribution Zone
Prepared By :
Amjad Abdullatef Abuzant.
Ahmad Ayman Jury.
Sajed Aladden Shakhsher.
Under Supervision of:
Dr. Anan F. Jayyousi

## Slide 2: Outline
Main characteristics of Nablus city.
Analysis of the city’s water situation.
Deep analysis of the critical zone (Khalit Alamod).
Expected future network for Khalit Alamod.
Generalizing the solution for the whole city of Nablus.
Conclusion.

## Slide 4: Main Characteristics About Nablus City
Location: 69 km. North of Jerusalem and 42 km. East of the Mediterranean sea.
Area: 29 Km2.
Pop.2014: 182,300 capita.
Elevation: 600m AMSL.
Climate: mild climate.

## Slide 5: Nablus Water Resources
Resource | Water Production2014 (m3/year)
Wells | 6,336,000
Springs | 1,031,400
Total | 7,367,400
Considering water loss in conveyance lines | 6,697,200

## Slide 6
Existing Reservoirs Distribution
Reservoirs Distribution

## Slide 7: Information About The Existing Main Network
Length: 68,600 m
Diameter: 2”-12”
Materials: HDPE, Steel And Ductile Iron.

## Slide 8
Existing Pressure Zones

## Slide 9: Main Results
Total Water Supply: 6,697,200m3/year.
Per Capita Supply: 100.65 L/C/Day.
UFW: 24.9%.
Per Capita Consumption: 75.6 L/C/Day.
Monthly Peak Factor: 1.27.

## Slide 10: Main Future Needs
Pop. 2034: 287,300 Capita.
Standard Per Capita Consumption: 120 L/C/Day (PWA).
Standard Water Loss: 15%.
Future Demand: 141.2 L/C/Day.
Total Future Demand: 14,803,500m3.
Additional Needed Quantities: 8.1MCM.

## Slide 12: General Characteristics
Location: Southern Part Of The City.
Area: 0.31 Km2.
No. Of Meters2014: 1,270 Meter.
Population2014: 6,340 Capita.
Elevation Difference: 105 M (Resource – Highest Point).

## Slide 13: Water Conditions
Water Source: Ein Dafna Reservoir.
Water Supplied: 312,800 M3/year.
Water Consumed: 170,500 M3/year.
UFW: 45.5%.
Per Capita Consumption: 74 L/C/Day.
Hourly Peak Factor: 1.36.

## Slide 14: Existing Network Condition
Age: (1952-2014).
Length: 10,650 m.
Diameter: 0.5”-8”.
Materials: HDPE, Polypropylene, Steel And Ductile Iron.

## Slide 15: Network Hydraulic Analysis
Water supply was 24 hrs. every 4 days.
Junctions demand was estimated using both Thiessen Polygons & Ortho map.

## Slide 16
Chart: Pipe labels
Chart: Junctions labels
Results

## Slide 17: Main Problems
Uncounted For Water (UFW).
Water Resources.
Reservoir Capacity.
Water Network.
Pumping.
House Connections.

## Slide 18: Future Water Demand for the Zone
Population2034: 10,000 c
Saturation Pop.: 12,400 c
Future Demand: 515,400 m3/year  1412 m3/day
Demand Pattern:

## Slide 19: Expected Future Network
Proposed alternatives:
Continuous Direct Pumping
Gravity Flowing Network
Multiple Criteria Decision Analysis.
Proposed Future Network: Gravity Flowing Network.
Attribute |  | Weight of attribute | 
Process operational complexity |  | 15% | 
Social aspects |  | 10% | 
Hydraulic aspects | Pressure | 50% | 15%
 | Velocity | 50% | 15%
Maintenance / Reliability of service |  | 20% | 
Water quality |  | 20% | 
Economic |  | 20% | 

## Slide 20: Proposed Actions
Proposed action | Expected date (year)
New network | 2017-2018-2019-2020
New reservoir | 2017-2018
Transmission line | 2019
Meters maintenance | 2020

## Slide 21: Cost Estimates for The Zone
Total Cost = 1,332,000
project period = 19 years
Avg. Pop. = 8,170 c
Per month house hold cost = 3.5 NIS/house/month.
Maintenance cost (Municipality) = 6.2 NIS/house/month.

## Slide 22: Generalizing the solution for the whole city of Nablus needs the following proposed actions:
Additional resources.
Gravity flowing network:
Trunk lines.
Additional Reservoirs.
Additional Pumps.
Replacement for the existing network.
Replacement for the existing meters.

## Slide 24: Investments Cash Flow
Chart: Time
| 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034
Network replacement | 272600 | 272600 | 272600 | 272600 | 272600 | 272600 | 272600 | 272600 | 272600 | 272600 | 272600 | 272600 | 272600 | 272600 | 272600 | 272600 | 272600 | 272600 | 272600
Meter Replacement | 247900 | 247900 | 247900 | 247900 | 247900 | 247900 | 247900 | 247900 | 247900 | 247900 | 247900 | 247900 | 247900 | 247900 | 247900 | 247900 | 247900 | 247900 | 247900
Reservoirs | 155000 | 155000 | 155000 | 155000 | 124000 | 124000 | 103350 | 103350 | 103350 | 186000 | 92000 | 124000 | 124000 | 124000 | 124000
Trunk Lines | 91000 | 100000 | 16500 | 16500 | 80500 | 80500 | 116000 | 75000 | 120000 | 15000 | 15000
Wells | 70700 | 70700 | 70700 | 70700
Pumps | 475000 | 237000 | 237000 | 132000 | 475000 | 237000 | 176000 | 237000

## Slide 26: Financial Considerations
Total Project Cost = 15,057,000 €.
Project execution period = 19 years.
Average Pop. of Nablus city = 188,680 c
Per year capita cost = 4.20 €
Per month capita cost = 0.35 €  1.47 NIS/c/month
Per house hold = 7.35 NIS/house/month.

## Slide 27: Conclusion
Studying the Whole city’s water problems.
Analyzing the critical zone and solving its water problems.
Generalizing the solutions from Khalit Alamod to The city of Nablus.
A facility Master Plan for the city was developed.
Future graduation projects could consider the analysis of other zones within the city of Nablus and more detailed design for each zone could be developed. In order to get more specific results.

## Slide 28
Questions & Comments
