## Slide 1: Building engineering department Graduation project 2 Integrated design for energy plus building municipal
Under the supervision of :Eng.Moayed salhab
Prepared By: Islam Adwan, Reem Jaber & Hadeel Alakhars
Al-Najah National University Faculty of Engineering

## Slide 2
Introduction:
This project represents an integrated design for a municipality in the West of Nablus. Its strategic location to serve all categories of the city's population and its accessibility and given the importance of the municipality to develop and improve the level was administrative, architectural, and urban planning of the country. The concept of this project is Energy plus Building.

## Slide 3: Architectural- Environmental aspect:

## Slide 4
Architectural plans
Site location
Architectural

## Slide 5
Architectural plans
After
Before

## Slide 6
Before
After

## Slide 7
Before
After

## Slide 8
Before
After

## Slide 9
Before
After

## Slide 10
Site location

## Slide 11
Proposals
Environmental Analysis
Thermal
Analysis
Energy conservation
Photovoltaics
Environmental

## Slide 12
Increase Glazing area.
Type glass(Double glass 12 mm)
Setback on the southern façade
Louvers on south wall
interior court
perforated Canopy
Vertical louvers in west and East
Mesh Cantilever
Proposals

## Slide 13
Wind movement around building:
Environmental analysis

## Slide 14
Time In Summer | Image | Time In Winter | Image
8:00 AM |  | 8:00 AM | 
12:00 PM |  | 12:00 PM | 
2:00 PM |  | 2:00 PM | 
Overshadowing and shading:

## Slide 15
Solar radiation in summer for elevation:
south elevation
East elevation
west elevation
North elevation
Solar radiation

## Slide 16
Solar radiation in winter for elevation:
south elevation
East elevation
west elevation
North elevation

## Slide 17
Solar radiation Inside (Summer) :
GF (before)
GF (after)
1st , 2nd and 3rd (after)
1st ,2nd and 3rd (before)

## Slide 18
Solar radiation Inside (Winter) :
GF (before)
GF (after)
1st , 2nd and 3rd (after)
1st ,2nd and 3rd (before)

## Slide 19
GF (before)
GF (after)
1st , 2nd (after)
1st ,2nd (before)
Daylight factor:
3rd (after)
3rd (before)

## Slide 20
Internal ventilation:
(before) | Image | (after) | Image
Gf floor |  | Gf floor | 
1st ,2nd floor |  | 1st ,2nd floor | 
3rd floor |  | 3rd floor | 

## Slide 21
Photovoltaics:
Package A (South wall)
Package B (East wall)
Package C (West wall)
Package D
Package E

## Slide 22
Summary
Name | Max power(Kwp) | # of module | Energy(Mwh/year)
package A | 22.8 | 48 | 25.1
package B | 57 | 120 | 49.4
package C | 59.9 | 126 | 65.4
package D | 148 | 312 | 245
package E | 68.4 | 144 | 115
Total |  |  | 487.7

## Slide 23
Economic analysis:
Present cash flow :
Payback period=7.45 Years
future saving for 50 years = 20675910.4 (ILS)
present saving for 50 years = 4106761.7 (ILS).

## Slide 24
Base model
Use Double glass (12)mm
We use 4cm polystyrene In wall
We use 5cm polystyrene in roof
Convert to (LED with step control
Energy conservation:
Proposals to convert the building to energy- plus building:
Converting the building to tight infiltration
Name | U (w/m^2.k)
Wall | 2.44
Partition | 2.44
Roof | 1.78
Floor | 2.32
Window | 5.89

## Slide 25
Use heat recovery in the HVAC
perforated Canopy
Setback on the southern façade
Vertical louvers in west
Vertical louvers in East
Energy conservation:
Proposals to convert the building to energy- plus building:
Mesh cantilever in east wall
Co2 sensor
Isolation of the floor between Gf and B1 (4cm polystyrene)

## Slide 26
Rustles:

## Slide 27
There is a surplus of electricity 280.9 Mwh/year.
Energy- plus:

## Slide 28
Thermal analysis:
u=0.36 (w/m^2.k).
External Wall
Window
u=0.45 (w/m^2.k)
Roof

## Slide 29
Heating load: (total load =279.8 Kw) (79.55 Ton)
Cooling load: (total load =349.2 Kw)(99.28 Ton)
Heating and cooling load

## Slide 30
Thermal comfort:
High PMV between (0.5 to-0.5)
Number the of hours of discomfort is equivalent to 479

## Slide 31
LUMION render: (Exterior render)

## Slide 32
LUMION render: (Internal render)

## Slide 33: Structure aspects

## Slide 34
Assumption
Structure blocks
Details
Martials Properties
ETABS check
Manual calculation
Seismic checks
Structure

## Slide 35
Assumption:
loads:
Live load =3.84 Kn/m2
Superimposed load =3.7 Kn/m2
Wall load =15 Kn/m2
Wind load =-1.01(Kn/m2)
Snow load =2.5(kn/m2).
Seismic load:
seismic zone 2B(Z=0.2),
Soil profile: SD
Ca=0.28
Cv=0.4
Important factor =1.25
Vv=(0.175*Dead load)
R=5.5

## Slide 36
Structure blocks:
Martials characteristics:
Manual calculation:
Fy=420 MPa
Fc=40 Mpa
u-boot thickness =450mm
Dead load =7.54 Kn/m2
concentrated load=2165.48 Ton.

## Slide 37
ETABS check
Compatibility check
As we can see in the analysis before us, there is nothing disconnected then Compatibility
Equilibrium check

## Slide 38
Stress-strain check:
Columns:

## Slide 39
Frame and beams :
First, we will check for one-way solid slab beams, which are beams 2 and 3, This analysis was done on the ultimate load 1.2dead and 1.6 Live load:
Two-way slab:(Beam1 and Frame):

## Slide 40
Use ultimate load 1.2dead and 1.6 Live load: shown in the
Mo (Wall and Beam Weight)=30*(13.75^2)/8=710 Kn/m2
Mo (beam)=(710+692.3)=1402.3 (Kn/m2).

## Slide 41
Deflection check
Slab deflection:
Beam deflection:
Shear check:
Max shear from ETABS=120Kn/m------> 120*0.78=93Kn/Rib.
ФVc=0.75*1.1*(1/6)*(40^0.5)*(260)*(450-30) =95Kn/rib. ----->Vu< ФVc(Ok).

## Slide 42
Seismic checks:
MPMR
Period check
Base shear check
Drift Check:

## Slide 43
Details
Columns:

## Slide 44
Beam:

## Slide 45
Shear wall:

## Slide 46
Slab:
Foundation
Raft footing

## Slide 47
Single footing

## Slide 48
Retiling wall

## Slide 49
Sheet pile
Sheet pile

## Slide 50
Beam :

## Slide 51
Propped :

## Slide 52
Stair

## Slide 53
Water tank :
Horizontal section in water tank
Vertical section in water tank display roof and wall
Vertical section in water tank display Footing and wall

## Slide 54: Electro-mechanical aspects:

## Slide 55
Water supply
Drainage Design
Vertical transportation
Firefighting system
Artificial lighting
HVAC design
Acoustic
Electrical design
Electro-mechanical aspects

## Slide 56
Acoustic
Architectural
Sound Insulation
RW (Sound Transmutation class)
1.Rw for project component:
RW for External wall
RW for Girtin wall

## Slide 57
RW for partition
RW for ceiling
2.Achieve Rooms for RW
Achieve canteen for RW
Achieve Mayor for RW
Achieve meeting room for RW
Achieve multi-purpose hall for RW
Achieve construction office for RW

## Slide 58
Lnw for floor (Impact insulation class):
1.Lnw for floor
2.Achieve Rooms for Lnw

## Slide 59
Reverberation Time:

## Slide 60
1. Distributed Sixto 63 SP in the ceiling
Distribution ceiling materials for Construction office
Distribution ceiling materials for canteen
Distribution ceiling materials for multi-purpose hall
In Meeting for All ceiling is SIXTO 63 SP.

## Slide 61
2. Achieve Rooms for RT60
Achieve RT60 for construction office
Achieve RT60 for canteen
Achieve RT60 for meeting room
Achieve RT60 for Multi-purpose hall

## Slide 62
Electro-Acoustic:
PRO 3031-A catalog
Catalog for ceiling LSP (CENA812) from AUDAC Company

## Slide 63
Distribution ceiling loud speaker
Loud speaker distribution In Multi-purpose hall
ceiling sound speaker distribution in fees collected
Ceiling sound speaker distribution in public services hall
Ceiling sound speaker distribution in corridor (GF)
Ceiling sound speaker distribution in corridor (1st ,2nd ,3rd )
Ceiling sound speaker distribution in canteen

## Slide 64
Water supply

## Slide 65
Main Branch Design
Main Horizontal Design
Main vertical Design
2.Calculation loss for each story
Cold water design
1.Dimeter design for pipes:

## Slide 66
Hot water design
Main Branch Design
Main Horizontal Design
Main vertical Design
1.Dimeter design for pipes:
2.Calculation loss for each story

## Slide 67
Water tank design
The amount of water consumption per person for offices (including canteen) =15 L/day
Total = 432 *15 =6.48 m3/day =25.92 m3/4days use 6 roof Tanks (each tank 5 m3)
Solar water heater design:
Then total Area = (28.42)/ (0.375*0.4*6.321) =30m2 we need to 30m2
Mirror of water heater we use 15 Mirror or 7 solar water heater
Water conservation
To create water savings, a water tank is designed to collect rainwater. This tank is designed to
collect 100% of rainwater, Area roof =1436 m2, Rain fill 660.1mm.
Total volume for water tank = (1436*0.6601)-((6.48*26*3)) =442 m3 then use rain water-----> tank (15*8*4 m)

## Slide 68
Vertical and horizontal transportation
Elevator design
Elevator calculation
Elevator calculation
The end we need to (4 Elevators (capacity=2500Ib, speed=350fpm))

## Slide 69
Artificial lighting design :
Indoor lighting design:
Limitation:
All lighting element luminaires is LED with step control elements.
The daylight factor should be in between this ringing (1-5) present
Light Levels (Illuminance) for indoor area as levels of offices area standard.
The reflection percentage it’s for floor its 0.2, ceiling its 0.8 and wall its 0.7.
Lighting transmission for Windows =0.69.
Ceiling void =0.85 m.

## Slide 70
Offices and public halls :
The parameter for design this room is 500 lux min as standard.

## Slide 71
Public service hall :

## Slide 72
Reception (entrance hall) and loopy :
The parameter for design this room is 300 lux min as standard, uniformity =0.6 and UGR<22.

## Slide 73
Multi-purpose Hall (Stage area).

## Slide 74
Wash and bath rooms

## Slide 75
Emergency stair:

## Slide 76
Outer lighting design:
Focus on directed lighting on the environmental ideas to highlight the beauty and view of architectural design of the building
Elevation lighting

## Slide 77
Open parking on the northern side and east Stair :

## Slide 78
Middle yard and canteen Yard

## Slide 79
Firefighting system:
Standard and codes
Jordanian code, 2004 Edition.
NFPA 13, 2019 Edition.
Articles 34 and 35 of the Palestinian Civil Defense Regulations for safety requirements.

## Slide 80: Automatic suppression systems Requirements:
All halls, lobbies and public kitchens are equipped with an automatic fire extinguishing system using automatic water sprinklers.
Automatic extinguishing systems must be linked to the automatic alarm system so that these systems work at the same time.

## Slide 81: Design fire protection systems for all public halls, lobbies, public kitchens, reception area and rest area.

## Slide 82: water agent- Pre-action Fire Sprinkler System
The concept of it is a dry pipe system in that water is not normally contained within the pipes. The difference it is that water is held from piping by an electrically operated valve, known as a pre-action valve. Valve operation is controlled by independent flame, heat, or smoke detection.”

## Slide 83: Fire sprinklers network
Ground floor fire sprinklers network
1st,2nd and 3rd floor fire sprinklers network-this is 1st floor plan

## Slide 84: Manual fire extinguishers
There are no less than two manual fire extinguishers on each floor.
Smoke and heat detector

## Slide 85: Audible and visual fire alarm :
Audible fire alarm
1.Sound level for audible fire alarm not less than 65 dB
2.There should be at least two warning sounds in one floor.
3.All alarm sounds distributed throughout the building work together at the same time.
Visual fire alarm
Visual signal devices must be hung on walls at a height of not less than 2 m and not more than 2.4 m.

## Slide 86: Fees Collecting hall
Kitchen west area-1st, 2nd and 3rd floor.

## Slide 87
HVAC design
Outdoor unit:
The system used for HVAC design is (VRF system)
The LG VRF Catalog was used.

## Slide 88: Indoor unit :
Fan coil:
The LG Fan Coil Catalog was used.
Diffuser:
OC waterloo catalog.

## Slide 89
Return Air:
Catalog selected from ADA

## Slide 90
Gf floor
1st ,2nd floor
3rd floor

## Slide 91
Drainage Design
Drainage network:

## Slide 92
Rain water drainage

## Slide 93
Drainage manholes network:

## Slide 94: Electrical design
Name | Area cross section (mm2)
Lighting | 1.5
Normal load | 2.5
Special load | 2.5
Fan coil | 1.5
After designing wire for the worst case each floor:

## Slide 97
Quantity surveying & Cost Estimate:
Initial cost 19858818.44 ILS-----> Unit cost =2142.27 ILS/m2.
Base Model:
1. Initial cost:
2. Life cycle cost(future ):

## Slide 98
Final Model:
1. Initial cost
Initial cost =21413936.72 ILS-----> Unit cost =2310 ILS/m2.
2. Life cycle cost (future):