## Slide 1: Assessment and Redesigning of HVAC system for Al-Rawda Complex
Graduation Project 2
Done by :
Abdullah Alshelleh
Mohammed Fauor
Dunia Lahham
Supervisor: Dr. Abdelrahim Abusafa

## Slide 2: TEAM MEMBERS
Mohamed Faour Energy Engineer
Dunia Lahham Energy Engineer
Abdullah Alshelleh Energy Engineer

## Slide 3: 1 3 2 4 TABLE OF CONTENTS
Main idea
Methodology
Proplem statement
Case study
5
Thermal load
6
Detailed design
7
Feasibility study
8
Results & conclusion

## Slide 4: Main idea of the project
The project involved suggesting the replacement of the existing heating and air conditioning system found in the medical complex and Al-Rawda Mosque. The proposal was to upgrade from the current split unit system to a more advanced and energy-efficient option like the VRF system. In the current project, a suitable VRF system was specifically designed for the location, and its effectiveness and economic feasibility were verified.

## Slide 5: Problem statement
The most common and used HVAC system in Palestine is the split unit systems, and this system is currently used in the mosque and the medical complex .
Some of the disadvantages of this system used in the complex:
Wrong installation .
Costly .

## Slide 6: METHODOLOGY
General Analysis by visits .
View existing system , bills and data.
Take dimensional measurements.
Calculate the heating and cooling load.
Economic feasibility calculation.
Suggestion for a new system.

## Slide 7: Case study
COMPLEX
Al-Rawda Mosque
Taddamun dispensary

## Slide 8: Construction of the complex

## Slide 9: Al-rawda mosque
Area = 565
7 air conditioners of 3 kilowatts ( Split unit system)
24 fans of 92 W
100 LED & 7 fluorescent lights
31 glass windows
3 wood doors

## Slide 10: Taddamun dispensary
The dispensary consists of two floors:
Basement floor
Ground floor

## Slide 11: COST
Al-Rawda Mosque
The estimated monthly electricity consumption from HVAC sys ranges from 700 to 1200 shekels.
Taddamun dispensary
The average account per month of the dispensary with the Electricity Company is about 7,298 shekels, including lighting, heating and air conditioning, in addition to the devices that are used in clinics.

## Slide 12: THERMAL LOAD CALCULATION
Heating load (Heat loss)
Cooling load (Heat gain)
Heat load refers to the amount of heating or cooling necessary to maintain the required temperature in a building or space within that building. This can be determined in relation either to the required heating or the required cooling.
Thermal load

## Slide 13
Heating load theory
Heat loss from walls , doors and windows
Heat loss from infiltration
Cooling load theory
Heat gain from walls, floors and ceiling
Heat gain from Windows

## Slide 14: load summary
Heating load
For the Mosque
Cooling load

## Slide 15
For the ground floor of Dispensary
Cooling load
Heating load

## Slide 16
Heating load
Cooling load

## Slide 17
Total | Dispensary (First floor) | Dispensary (Ground floor) | Mosque | Load
127 kW | 40.8 kW | 33.64 kW | 52.5 kW | Heating load
99.1 kW | 34.27 kW | 26.12 kW | 38.7 kW | Cooling load

## Slide 18: Ventilation rate
The aim of ventilation is to remove the product of respiration and space contaminants such as smells, water vapor, gases, fumes and vapors of industrial processes.

## Slide 19
The following table is for Ventilation rate for the basement floor (dispensary) :

## Slide 20: Detailed design
The variable refrigerant flow is used for cooling and heating in multi-floor buildings and multi-use rooms that have different heat loads, as some rooms need heating and others are cooled
In addition to providing superior comfort, VRF systems offer design flexibility, energy savings, and cost effective installation.
Variable refrigerant flow (VRF) system

## Slide 21
VRF Advantages
Energy saving
Cost effective installation
Design Flexibility
Control means comfort

## Slide 22
A heat recovery air handling unit is a mechanical ventilation system that uses a heat exchanger to recover heat from the outgoing air stream and transfer it to the incoming air stream. These units are typically used in larger commercial or industrial buildings to provide a constant supply of fresh air while also maintaining a comfortable indoor temperature.
Heat recovery Air handling units
Benefits of Heat Recovery AHU
Improved energy efficiency
Improved indoor air quality
Reduced carbon footprint

## Slide 23
Scenarios for the design
More than one scenario was proposed in the design process. There were scenarios that depended on outdoor units that were brought from the official Samsung website. For the last scenario, the necessary units were brought from the Palestinian market.

## Slide 24
Two outdoor units (Samsung AM220FXVAGH/EU)
Total cooling capacity = 61.6 kW X 2 = 123.2 kW
Total heating capacity = 69.3 kW X 2 = 138.6 kW
First Scenario
Dispensary
Winter
1284 NIS/month
Summer
1340 NIS/month
Winter
608 NIS/month
Summer
573 NIS/month
Mosque

## Slide 25
Four outdoor units (Samsung MV6-R335WV2GNI)
Total cooling capacity = 33.5 kW X 4 = 134 kW
Total heating capacity = 33.5 KW X 4 = 134 kW
Second Scenario
Dispensary
Winter
1045 NIS/month
Summer
1227 NIS/month
Winter
492 NIS/month
Summer
524 NIS/month
Mosque

## Slide 26
Three outdoor units (Samsung AM140HXVFGH/ID)
Total Cooling capacity = 40 KW X 3 = 120 kW
Total Heating capacity = 45 kW X 3 = 135 kW
Third Scenario (from the Palestinian market)
Dispensary
Winter
1522 NIS/month
Summer
1252 NIS/month
Winter
716 NIS/month
Summer
535 NIS/month
Mosque

## Slide 27: Feasibility study
The main objective of a feasibility study is to determine if the proposed project or business idea is viable and if it aligns with the organization's goals and objectives. The study helps decision-makers understand the potential risks and benefits of the proposed project and make an informed decision on whether to proceed with it or not.

## Slide 28: ECONOMIC Parametrs
2
4
3
1
Simple payback period
Saving to investment ratio
Present value
Rate of return

## Slide 29
The investment is divided into several sections , including:
Remote control
Piping and labor
Indoor units
Investment cost
Outdoor units

## Slide 30
The following tables represent the indoor capacity and cost of each zone
First floor
Ground floor

## Slide 31
The following tables represent the indoor capacity and cost for the mosque
Mosque
Total investment for the indoor units = 8000$+4300$+4800$ = 17100 $

## Slide 32
Investment and saving for each Scenario
First scenario
 | Outdoor units
 | Indoor units
 | Piping & labor
 | Remote control
 | Outdoor units
 | Indoor units
 | Piping & labor
 | Remote control
Total investment = 57940 = 208580 NIS
Investment
Total saving | Cooling | Heating | 
 |  |  | Dispensary
 |  |  | Mosque
Total saving | Cooling | Heating | 
 |  |  | Dispensary
 |  |  | Mosque
Total saving for the First Scenario per year =
Saving
55,209 NIS
208,580 NIS

## Slide 33
Investment and saving for each Scenario
Second scenario
 | Outdoor units
 | Indoor units
 | Piping & labor
 | Remote control
 | Outdoor units
 | Indoor units
 | Piping & labor
 | Remote control
Total investment = 56940 = 204980 NIS
Investment
Total saving | Cooling | Heating | 
 |  |  | Dispensary
 |  |  | Mosque
Total saving | Cooling | Heating | 
 |  |  | Dispensary
 |  |  | Mosque
Total saving for the Second Scenario per year =
Saving
57,458 NIS

## Slide 34
Investment and saving for each Scenario
Third scenario (from Palestinian market)
 | Outdoor units
 | Indoor units
 | Piping & labor
 | Remote control
 | Outdoor units
 | Indoor units
 | Piping & labor
 | Remote control
Total investment = 56940 = 204980 NIS
Investment
Total saving | Cooling | Heating | 
 |  |  | Dispensary
 |  |  | Mosque
Total saving | Cooling | Heating | 
 |  |  | Dispensary
 |  |  | Mosque
Total saving for the Third Scenario per year =
Saving

## Slide 35: results
Scenarios | SPP | PV | SIR | ROR
First | 4 years | 292552 NIS | 2,4 | 25%
Second | 3.56 years | 316566,2 NIS | 2.5 | 28%
Third | 3,8 years | 283389.8 NIS | 2.4 | 29%
The third scenario was chosen because it is the most realistic and reliable based on several factors, the most important of which was the coefficient of performance (COP), which is equal to 3.5, in addition to being taken from the Palestinian labor market.

## Slide 36: Conclusion
It turned out to us that the VRF system is one of the latest and most abundant systems that can be installed in buildings Existing without the need for the building to be in the construction.

## Slide 37: Thanks!