## Slide 1: An-Najah National University Faculty Of Engineering Civil Engineering Department
KAFA VILLAGE WATER SUPPLY NETWORK
Prepared By : Adham Jihad Dibbas
Supervision of Dr. Anan Jayyousi

## Slide 2: Outline:
Objectives of the project.
Study area.
Methodology.
Analysis of Existing Network.
Design of Future Network.

## Slide 3: Objective:
Analysis of Existing Water Supply Network for Kafa Village.
Design of Future Water Supply Network for Kafa village.

## Slide 4
Location :
Kafa village is located in Tulkarm at a distance about 5 km to the south of Tulkarm city.
It is surrounded by Faroun from the west, Shofa from the east, Ezbet Algrad from the north and Ezbet Shofa from the south.
Study area

## Slide 6
Area :
The area of the lands belonging to the Kafa is 634 donum Which include agriculture lands about 330 donum and building lands about 304 donum.
Population :
The present population is 1,000 persons.
Elevation :
Kafa is rising between (65-200) meters above mean sea level (A.M.S.L).

## Slide 7: The Questionnaire
I took sample of 30 families and tried to be representative

## Slide 8
Family Size:
The average number of the persons in Kafa Families is 6 persons.
The Income of Families:
Chart: The Monthly Income(NIS)
1500> 1500-3000 3000-4500 4500< | 3 | 16 | 7 | 4

## Slide 9
Education:
The education in Kafa town is moderate good, as shown in figure below.
Chart: 
إعدادي ثانوي بكالوريوس دكتوراة | 5 | 13 | 10 | 2

## Slide 10
Houses Gardens or Agricultural Land:
You can see in figure below that 93% of the families own gardens or agricultural land.
Chart: 
they have they don't have | 28 | 2

## Slide 11
Source of Water:
The main source of water in Kafa town is from the municipality, in addition about 33% of the families have cisterns as shown if figure below.
Chart: 
cisterns Municipality | 10 | 20

## Slide 12
Water Bills in Summer and Winter :
The average of water consumption in the summer season is about 31.5 CM/month, and it’s larger than the consumption in the winter season which about 21.5 CM/month.
Chart: Water consumption in summer and winter
summer | 30 | 35 | 10 | 30 | 15 | 18 | 12 | 30 | 18 | 30 | 15 | 35 | 70 | 15 | 30 | 70 | 45 | 30 | 20 | 20 | 15 | 30 | 12 | 40 | 60 | 30 | 50 | 80 | 30 | 20
winter | 20 | 25 | 8 | 15 | 10 | 10 | 8 | 20 | 12 | 25 | 10 | 25 | 50 | 10 | 20 | 50 | 35 | 20 | 20 | 15 | 10 | 20 | 7 | 30 | 40 | 20 | 30 | 50 | 20 | 10

## Slide 13
Problems with Water:
As shown in figure below, 60% of families complained from the water quality.
Chart: The existence of problems in the water
Yes | 18
NO | 12

## Slide 14
The problems:
Chart: Water problems
Dust Leaking water buoy chlorine water meters | 9 | 6 | 5 | 5 | 8

## Slide 15
The Relation between per capita consumption and the number of family members:
Chart: # of person
| 6 | 9 | 9 | 2 | 6 | 7 | 6 | 10 | 2 | 6 | 7 | 2 | 6 | 4 | 6 | 7 | 7 | 4 | 5 | 4 | 4 | 4 | 6 | 6 | 13 | 6 | 8 | 11 | 5 | 4
 | 166.6667 | 129.6296 | 37.037 | 500 | 83.3333 | 85.7143 | 66.6667 | 100 | 300 | 166.6667 | 71.4286 | 583.3333 | 388.8889 | 125 | 166.6667 | 333.3333 | 214.2857 | 250 | 133.3333 | 166.6667 | 125 | 250 | 66.6667 | 222.2222 | 153.8462 | 166.6667 | 208.3333 | 242.4242 | 200 | 166.6667
The figure shows that the L/C/day decrease with the in increase # of person.
The average L/C/day = 180 (consumption)
L/C/day (demand) = consumption/(1-UFW) = 285
UFW form municipality = 37%

## Slide 16: Rainfall
The only available rainfall data are being recorded at Tulkarm meteorological stations located in the city are shown in the following Table.
Year | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016
Rainfall (mm) | 660.5 | 467 | 565 | 680 | 412.5 | 695.5 | 410

## Slide 17: Methodology
Hydraulic Equations:
Head loss due to friction in the pipes calculated by Hazen-William’s equation.
Analysis and Design Constraints:
Pressure at junction between (20-100) m.H2O.
Velocity in pipe (0.1-3.0) m/s.

## Slide 18
Node :
In Kafa’s network, there are 36 nodes that connect the pipes together.
Now, I find the demand of the nodes by assume density of each area.
Analysis of Existing Network

## Slide 20
Analysis of Existing Network
The Equation:
D(A6+A5)+0.5(A1+A3)+0.25D(A2+A4) = # of Pop =1000
D=3.93*10^-3
For Example the population of A3 = 0.5D*Area=172 capita
As you can see in the table below

## Slide 21
Table of Areas:
Analysis of Existing Network
The demand of each area(CM/day) = # of Pop * L/C/day(demand) * 10^-3
L/C/day (demand) = 285
Demand(CM/day) | Population | Type | Area(m^2) | # Area
5.13 | 18 | 0.5D | 9285.415 | 1
14.25 | 50 | 0.25D | 51377.245 | 2
49.02 | 172 | 0.5D | 87121.415 | 3
24.225 | 85 | 0.25D | 86211.595 | 4
136.8 | 480 | D | 122316.495 | 5
55.575 | 195 | D | 49510.226 | 6
285 | 1000 |  | 405822.4 | Sum

## Slide 22
Now find the density of each node using GIS program:
A1
A2
Analysis of Existing Network
Demand(CM/day) | Population | Density | Nodes
3.42 | 12 | 0.6666 | 2
1.71 | 6 | 0.3334 | 3
5.13 | 18 | 1 | Sum
Demand(CM/day) | Population | Density | Nodes
9.69 | 34 | 0.68 | 4
4.56 | 16 | 0.32 | 5
14.25 | 50 | 1 | Sum

## Slide 23
A3
A4
Analysis of Existing Network
Demand(CM/day) | Population | Density | Nodes
2.85 | 10 | 0.0581 | 6
3.705 | 13 | 0.0755 | 7
4.56 | 16 | 0.0930 | 8
7.695 | 27 | 0.1569 | 9
2.28 | 8 | 0.0465 | 10
5.13 | 18 | 0.1046 | 11
7.695 | 27 | 0.1569 | 12
8.835 | 31 | 0.1802 | 13
1.71 | 6 | 0.0348 | 14
4.56 | 16 | 0.0930 | 15
49.02 | 172 | 1 | Sum
Demand(CM/day) | Population | Density | Nodes
3.135 | 11 | 0.1294 | 16
4.845 | 17 | 0.2 | 17
1.995 | 7 | 0.0825 | 18
6.27 | 22 | 0.2588 | 19
3.42 | 12 | 0.1411 | 20
4.56 | 16 | 0.1882 | 21
24.225 | 85 | 1 | Sum

## Slide 24
A5
A6
Analysis of Existing Network
Demand(CM/day) | Population | Density | Nodes
3.135 | 11 | 0.0229 | 22
13.395 | 47 | 0.0979 | 23
4.275 | 15 | 0.0312 | 24
4.845 | 17 | 0.0354 | 25
15.675 | 55 | 0.1145 | 26
7.41 | 26 | 0.0541 | 27
15.96 | 56 | 0.1166 | 28
9.405 | 33 | 0.0687 | 29
18.525 | 65 | 0.1354 | 30
12.255 | 43 | 0.0895 | 31
23.94 | 84 | 0.1750 | 32
7.98 | 28 | 0.0583 | 33
136.8 | 480 | 1 | Sum
Demand(CM/day) | Population | Density | Nodes
26.505 | 93 | 0.4769 | 34
10.83 | 38 | 0.1948 | 35
18.24 | 64 | 0.3282 | 36
55.575 | 195 | 1 | Sum

## Slide 25
Pipelines :
The Network has 37 pipes of different diameter(1,2,3)inches, the roughness coefficient is 100 for steel, as reported by Hazen Williams roughness coefficient.
Analysis of Existing Network

## Slide 26
Table of Pipes:
Analysis of Existing Network
C | D (inch) | L | TO | From | Pipes ID
100 | 3 | 161 | N-1 | Pumps | Main-Pipe
100 | 3 | 161 | N-2 | N-1 | P-1
100 | 1 | 76 | N-3 | N-2 | P-2
100 | 3 | 160 | N-4 | N-2 | P-3
100 | 2 | 35 | N-5 | N-4 | P-4
100 | 3 | 237 | N-6 | N-4 | P-5
100 | 2 | 49 | N-7 | N-6 | P-6
100 | 2 | 69 | N-8 | N-7 | P-7

## Slide 28
Analysis of Existing Network
Diameters of pipes

## Slide 29
Pump:
There is two pumps connected in parallel in Kafa’s town, which has a head of each pump between (98.6 to 179) meters, flow between (8 to 24 ) Cm/day.
Analysis of Existing Network

## Slide 30
EPS Analysis and Demand Pattern
After running the model using Water-Cad program, I have this results.
Chart: 
1 2 3 4 5 6 7 8 9 10 11 12 13 14 15 16 17 18 19 20 21 22 23 24 | 0.45 | 0.45 | 0.27 | 0.27 | 0.45 | 0.45 | 1.8 | 1.8 | 1.35 | 1.35 | 0.99 | 0.99 | 0.9 | 0.9 | 0.99 | 0.99 | 1.08 | 1.08 | 1.8 | 1.8 | 1.17 | 1.17 | 0.72 | 0.72

## Slide 31
Junctions Table (Peak Hour)

## Slide 32
Pressure of Nodes

## Slide 33
Pipes Table (Peak Hour)

## Slide 34
Velocity in Pipes

## Slide 35
Pump Table

## Slide 36
Conclusions of Analysis
From the results obtained from previously model, noticed that most of junction has pressure head between (60-200) m H2O,which is grater than the Constraints and all velocity is between (0.05-1.3) m/s.

## Slide 37
Population Projection:
The current population of Kafa town is 1000 inhabitant. In order to develop the current water network to serve for the 25 years. One needed to calculate the future population.
According to Palestinian Central Bureau of statistics (PCBS), Kafa’s population growth rate is about 3.5%.
Based on this, the future population of Kafa town till 2042 is estimated according on the following equation:
P2042=P2017*(1+i)^n
If i (growth rate) = 3.5%
n= 25 years
P2017= 1000 person
P2042= 2364 person
Design of Future Network

## Slide 38
Future Water Demand:
In order to supply people with enough of water in the future, the minimum domestic consumption rate is taken as 120 L/C/d according to WHO standards for small communities, so the municipal consumption will be:
Municipal consumption = Domestic consumption/0.9 = 120/0.9 = 133.34 L/C/day
Demand = consumption / (1-UFW) = 133.34/(1-0.37) = 212 L/C/day
The present Demand per capita equals 285 L/C/day
This less than the present per capita demand rate, so take the present per capita demand.
Design of Future Network

## Slide 39
Estimation of Future Water Demand:
To estimation the future water demand for each node, the existing water demand will be multiplied by the future demand factor that equals to:
Factor = (P2042/P2017) * (new demand / old demand)
Factor = 2.364
Future Demand = Existing Demand * Factor = 285 CM/day * 2.364
= 674 CM/day
Design of Future Network

## Slide 40
By using “ load builder ” on WaterCAD software

## Slide 42
EPS Analysis and Demand Pattern
Chart: 
1 2 3 4 5 6 7 8 9 10 11 12 13 14 15 16 17 18 19 20 21 22 23 24 | 0.45 | 0.45 | 0.27 | 0.27 | 0.45 | 0.45 | 1.8 | 1.8 | 1.35 | 1.35 | 0.99 | 0.99 | 0.9 | 0.9 | 0.99 | 0.99 | 1.08 | 1.08 | 1.8 | 1.8 | 1.17 | 1.17 | 0.72 | 0.72

## Slide 43
Future Analysis Based on Existing Network
Node ID | Pressure(mH2O ) | Node ID | Pressure(mH2O )
N-1 | 106 | N-19 | -20
N-2 | 80 | N-20 | -10
N-3 | 43 | N-21 | -12
N-4 | 53 | N-22 | -27
N-5 | 50 | N-23 | -28
N-6 | 21 | N-24 | -35
N-7 | 16 | N-25 | -39
N-8 | 16 | N-26 | -40
N-9 | 14 | N-27 | -35
N-10 | 16 | N-28 | -36
N-11 | 16 | N-29 | -36
N-12 | 16 | N-30 | -39
N-13 | 6 | N-31 | -45
N-14 | -13 | N-32 | -46
N-15 | 17 | N-33 | -36
N-16 | 3 | N-34 | -39
N-17 | -17 | N-35 | -42
N-18 | -9 | N-36 | -53

## Slide 44
To solve the problem of the negative pressure in the future network, I have two options. The first one to add another booster pump in parallel, the second one to conversion the system from pump system to gravity system.
The design criteria that I used according to PWA:
Pressure: (20-100) mH20
Velocity: (0.1-3) m/sec
Design of Future Network

## Slide 45
Option One:
The new pump has a head of (170m) and flow of (730 CM/day), the three pumps connected in parallel to increase the flow of water in system, because the existing two pumps their capacity of flow is 1152 CM/day and head 100 mH2O at maximum operation, but the demand at the peak hour of day is 1213 CM/day, so I use another pump (in parallel) to increase the flow of water.
To maintain high pressure in the low elevation areas with the standards and the increase of pressure at the minimum consumption of water of the day, a pressure reducing valve (PRV) was used.
Design of Future Network

## Slide 46
Option One:
Design of Future Network

## Slide 47
Result of this Option (Peak Hour)
1- Velocity

## Slide 49
Result of this Option
2- Pressure

## Slide 51
Option Two:
This option considered to conversion the system from pump system to gravity system by elevate the water to new reservoir (200 MSL) using the existing pumps, the height of the new reservoir is equal 20 meters.
The total length added to transfer the water from the old reservoir to new one is equal 1759 meters.
Design of Future Network

## Slide 52
Option Two:
Design of Future Network

## Slide 53
Result of this Option (Peak Hour)
1- Velocity

## Slide 55
Result of this Option
2- Pressure

## Slide 57
Conclusions of Design
After calculation the cost of each option, option two was found to be better than option one with its high efficiency according to the design criteria such as velocity and pressure, but option one was found to be better than option two with its low cost.

## Slide 58
Thank You
For Your Attention…