## Slide 1
Structural Design of Commercial Building under Gravity and Seismic Loads
Prepared By:
Razan Zaidan Rawya Amarneh
Under Supervision of:
Dr. Mohammed Samaaneh.

## Slide 2
Presentation Contents:
1- Project Description.
2- Site and Geological Information.
3- General Notes.
4- Preliminary Design of the Project.
5- 3D Modeling and Design of the Project.

## Slide 3
Project Description:
Use of floor | Height (m) | Area () | Floor
Parking | 3 | 969.8 | Third Basement
Parking | 3 | 969.8 | Second Basement
Stores | 3 | 969.8 | First Basement
Gallery | 3 | 878.0 | Ground
Gallery | 3 | 954.3 | First floor
Gallery | 3 | 954.3 | Second floor
Gallery and apartments | 3 | 954.3 | Third floor
Gallery and apartments | 3 | 954.3 | Fourth floor
Gallery and apartments | 3 | 954.3 | Fifth floor
Gallery and apartments | 3 | 954.3 | Sixth floor
Gallery and apartments | 3 | 954.3 | Seventh floor
- | 2.85 | 78.9 | Staircase
- | 35.85 | 10546.5 | Total
Use of floor | Height (m) |  | Floor
Parking | 3 | 969.8 | Third Basement
Parking | 3 | 969.8 | Second Basement
Stores | 3 | 969.8 | First Basement
Gallery | 3 | 878.0 | Ground
Gallery | 3 | 954.3 | First floor
Gallery | 3 | 954.3 | Second floor
Gallery and apartments | 3 | 954.3 | Third floor
Gallery and apartments | 3 | 954.3 | Fourth floor
Gallery and apartments | 3 | 954.3 | Fifth floor
Gallery and apartments | 3 | 954.3 | Sixth floor
Gallery and apartments | 3 | 954.3 | Seventh floor
- | 2.85 | 78.9 | Staircase
- | 35.85 | 10546.5 | Total

## Slide 4: Basment Floors Plan.

## Slide 5: Ground Floor Plan

## Slide 6: Upper Floors Plan.

## Slide 7
Site Geological and Information:
Al-Affori Building has a prime location as it resides on Rafedia Street, Which considered as a vital street that witnesses a rapid development plan in the residential and commercial areas.
The soil in the site is mainly rocky and has a bearing capacity of 300 kN/

## Slide 8: General notes:
1- Concrete compressive strength = 24 Mpa.
2- Steel yield strength of 420 Mpa.
3- The soil bearing capacity is 250 kn/m^2.
4- Design Codes:
ACI 318-11.
ASCE 7-10.
UBC 97.
5- Design Programs:
SAP2000 program.
SAFE Program.
AutoCAD.

## Slide 9
5- Design loadings:
All floors expect the roof floor:
- Roof Floor:
Used Value | Load
4.4 kN/ | SD Load
5 kN/ | Live Load
21 kN/m | Wall Weight
2.2 kN/m | Glass Weight
Used Value | Load
 | SD Load
 | Live Load
21 kN/m | Wall Weight
2.2 kN/m | Glass Weight
Used Value | Load
4.4 kN/ | SD Load
10 kN/ | Live Load
14 kN/m | Wall Weight
Used Value | Load
 | SD Load
 | Live Load
14 kN/m | Wall Weight

## Slide 10
Preliminary Design of the Structure

## Slide 11
Structural system

## Slide 12: Analysis and Design using SAP program

## Slide 13: 3D model of structure

## Slide 14: Check of model
Compatibility check

## Slide 15
Equilibrium check
Total hand calculation Dead load = 55406.62 kN.
SAP result = 55749.483 kN.
Percent of error = *100% = 0.62% < 5% → OK.

## Slide 16
Live load:
Hand calculation:
{(427.8896*3+342.5+457.1*6)*5} +{ (457.1)*10}=26415 kN.
SAP result = 26511.4 kN.
Percent of error = * 100% = .36%.

## Slide 17
Super Imposed load
Hand Calculation
- Super Imposed load = slabs areas * 4.4 = 4825.8*4.4 = 21233.5 kN.
SAP result = 21308.5 kN.
Percent of error = * 100% = .35%.< 5% Ok.

## Slide 18
Wall weight:
Hand Calculation:
Wall weight =(78.5*3+39.4+55*6) * 21+75.2*14 = 13755 kN.
SAP result = 13787.2 kN.
Percent of error = * 100% = .23% < 5% Ok.

## Slide 19
Glass weight:
Hand Calculation:
- Glass weight = (16.23+18.44*6)*2.2 = 279.114 kN.
SAP result = 279.2 kN.
Percent of error = * 100% = .03% < 5% Ok.

## Slide 20
Stress Strain relationship
Slab:
= + 19.3 = 53.924 kN.m
= + 24.3 = 55.55 kN.m
% of error = * 100% = 2.9% < 5% → ok.

## Slide 21
Stress Strain relationship
Beam:
= + 16 = 32.5 kN.m
= + 16.45 = 30.4 kN.m
% of error = * 100% = 6.5% < 10 % → ok.

## Slide 22: Check deflection
Slab deflection from service load:
- Max deflection ( as shown in figure) = 24.4 mm.
- Allowable deflection = = 45.8 mm > 28.4 mm. → ok.

## Slide 23
2. Slab Long term deflection :
From SAP
= 4.2 mm
= 10.3 mm
=
=
== 26.9 mm < 45.8 mm. → ok.
3. Beam deflection :
= ( ACI 318-11, 9.5(b), Floor slab with partitions not likely to be damaged by large deflection ).
= = 45.8 mm.
= 40.8 mm < 45.8 mm.→ ok.

## Slide 24
From Section 1630.2.2 in UBC 97:
T = (Ct) (hn) ^ (3/4)
T= (0.03) (108.27) ^0.75 = 1 sec.
SAP Result:
T = 1.85 sec.

## Slide 25: Seismic Analysis of the Structure

## Slide 26: Period Calculations
Method A:
From Section 1630.2.2 in UBC 97:
T = (Ct) () ^ (3/4)……….. (4.1)
Where:
Ct =0.035 for steel moment-resisting frames.
Ct =0.03 for reinforced concrete moment-resisting frames and eccentrically braced frames.
Ct =0.02 for all other buildings.
T= (0.03) (108.27) ^0.75 = 1.01 sec.

## Slide 27
SAP2000 Program:
The Value from SAP must be smaller than (1.4* T Method-A)
X-direction:-
T = 1.4 Sec.
(1.4) ( Tmethod A) = (1.4*1.01) = 1.414 Sec. > 1.4 Sec →OK
B. Y- direction:-
T = 1.28 Sec.
(1.4) ( Tmethod A) = (1.4*1.01) = 1.414 Sec. > 1.28 Sec →OK

## Slide 28
Seismic Analysis of the Structure:
Determine seismic zone factor (Z):

## Slide 29
Determine site soil classification:
- The Soil profile is found to be (SC).
Determine (Ca) and (Cv) based on site soil classification:
- Seismic coefficients: Ca = 0.24, Cv = 0.32

## Slide 30
Determine occupancy type:
I = Importance Factor: From table 16-K—occupancy category in UBC-97.
I = 1.00 (Standard Occupancy Structures).

## Slide 31
Determine modification factor(R):

## Slide 32
In this project Equivalent Static and response spectrum methods will be used for calculating the seismic load.
Calculate Base shear Manually:
the least of V= or V= 2.5
In X-direction:
Cs = = = 0.058
Cs max = = = 0.109.
Cs min = 0.11 Ca I = 0.11 * 0.24 * 1= 0.0264.
Cs min< Cs < Cs max OK.
Base shear (V) = Cs * W = 0.058 *(55749.48 + 21308.5 + .25*26511.4 + 13787.155 + 279.2) = 5669.6 kN.
In Y-direction:
Cs = = = 0.058
Cs min < Cs < Cs max OK.
Base shear (V) = Cs * W = 0.058 *97752.2 = 5669.6 kN.

## Slide 33
Seismic Analysis Basic Definitions :
- Define modal acceleration in X and Y according to (Ritz vectors).

## Slide 34
Modal Mass Participation Ratio in X-DIR

## Slide 35
Modal Mass Participation Ratio in Y-DIR

## Slide 36
Define Mass Source:
Mass includes = mass of (Dead load + Superimposed dead load + 0.25 Live load + Wall and Glass load).

## Slide 37
Equivalent static method:
Define function of Equivalent static:
1- In X-Dir:

## Slide 38
2- In Y-Dir:

## Slide 39
Base Reactions SAP Results:
Percent of error = *100%1.4 =.% < 5% → ok.

## Slide 40
Response Spectrum method:
Define function of Response Spectrum:
1- In X-Dir:

## Slide 41
2- In Y-Dir:

## Slide 42
Base Reactions SAP Results:
Percent of error (in X-Dir) = *100% = 46.4 > 25% →Not ok.
Percent of error (in Y-Dir) = *100% = 38.4 > 25% →Not ok.

## Slide 43
Modification of Response Spectrum scale factor:
For Force from Response Spectrum in X-Direction :
New Scale factor in (U’1) = X scale factor
= X 1.78 *.9= 2.95
New Scale factor in (U’2) = .
For Force from Response Spectrum in Y-Direction :-
New Scale factor in y-direction (U’1) = X scale factor
= X 1.78*.9 = 2.57
New Scale factor in y-direction (U’2) = 0.3*2.57 = 0.771

## Slide 44
So, after make analysis we get the expected results:
Percent of error (in X-Dir) = *100% = 9.9% < 25% → ok.
Percent of error (in Y-Dir) = *100% = 10% < 25% → ok.

## Slide 45: Structural Design of Concrete Members
The code used for design and detailing is ACI 318-11 regarding seismic and gravity loads.
Provisions were applied to all structural members including:
  Beams
  Columns
  Shear Walls
  slabs
  Foundations

## Slide 46: Structural Design of Concrete Members
Beams layout for the roof

## Slide 47: Structural Design of Concrete Members
for B20
key for reinforcement

## Slide 48: Structural Design of Concrete Members
Longitudinal steel

## Slide 49: Structural Design of Concrete Members
Stirrups

## Slide 50: Structural Design of Concrete Members
Beams detailing

## Slide 51: Structural Design of Concrete Members
Column layout

## Slide 52: Structural Design of Concrete Members
Check slenderness :
For C10

## Slide 53: Structural Design of Concrete Members
M2 =13.2 kN.m
M1 =33 kN.m

## Slide 54: Structural Design of Concrete Members
Design load

## Slide 55: Structural Design of Concrete Members

## Slide 56: Structural Design of Concrete Members
Columns detailing:

## Slide 57: Structural Design of Concrete Members
Columns detailing:

## Slide 58: Structural Design of Concrete Members
Shear wall:

## Slide 59: Structural Design of Concrete Members
Shear Wall detailing:

## Slide 60: Structural Design of Concrete Members
Slab detailing for basement

## Slide 61: Structural Design of Concrete Members
Footing
SAFE model:
Mat thickness = 1.3 m

## Slide 62: Structural Design of Concrete Members
Deflection check:
Max deflection =0.7172 mm < 10 mm → ok.

## Slide 63: Structural Design of Concrete Members
Mat deleting (Y-direction)

## Slide 64: Structural Design of Concrete Members
Mat deleting (X-direction)

## Slide 65
The End