## Slide 1: Evaluation of The Structural Design of Nursing and Optical Faculty- An Najah National University
Prepared by:
Ahmad F. Amad
Ahmad A. Zeineddin
Fawzi S. Abu-Aladas
Mahhmoud A. Sukkar
Supervisor:
Mr. Ibrahim M. Arman

## Slide 2: Out Lines
Project description.
Three dimensional modeling.
Structural design and evaluation

## Slide 3: Project Objectives
Evaluation
                Comparison

## Slide 4: Location

## Slide 5: Project Description
This structure is used for educational purposes.
The faculty consists of seven floors.
Six main floors and roof floor.
This structure includes mechanical rooms and three water tanks.
The project has two axes of symmetry.

## Slide 6: Plan of Ground Floor

## Slide 7: Loads
Gravity loads:
  Dead load.
  Live load.
  Snow load:1.5 KN/m2.
CASE | LOAD (KN/m2)
Offices, class rooms | 3.0
MECHANICAL ROOMS | 7.5
Staircase | 4.0
Roofs: | 
With access | 1.5
Without access | 1.0
Mechanical equipment | 7.5

## Slide 8: Loads
Lateral loads:
  Wind loads.
  Seismic loads (UBC-97 is used).
    I= 1
    Seismic zone 2B.
    Z=0.2
    Cv=0.2
    Cs=0.2
    R=5.5
    Soil profile type =Sp

## Slide 10: Load Cases and Load Patterns

## Slide 11: Design Codes
ACI 318 – 02 American concrete institute
UBC – 97 Uniform building code
ASCE7 – 02 American society of civil engineering
JCLF – 06 Jordan code for loads and forces
JSC – 05 Jordan seismic code.

## Slide 12: Structural System
Shear walls.
Frames, which consist of:
  Beams.
  Columns.

## Slide 13: Three dimensional modeling

## Slide 14: Material Property for concrete

## Slide 15: Shell Data
Ribbed slab definition

## Slide 16: Modifiers equations
where:
Modifiers for ribbed slab

## Slide 17: Modifiers
Two way solid slab
Shear wall

## Slide 18: Modifiers
For beams
For columns

## Slide 19: Response Spectrum

## Slide 20: EQULIPRIUM this result from sap

## Slide 21: Dead load
This include own weight for all structural elements Slabs, Beams, columns and walls.
floor | weights (KN)
B3 | 7184.74
B2 | 15775.82
B1 | 13096
GF | 13964.56
F1 | 10331.02
F2 | 10103.91
RF | 9396.28
TR | 1215.66
total | 81068.08

## Slide 22: Live load
Live load in this project has different values depending on the function, which are mechanical room, offices, class rooms and stairs.
floor NO | TOTAL LIVE LOAD(KN)
B2 | 3765.75
B1 | 3200.4
GF | 3652.5
F1 | 2553.9
F2 | 2553.9
RF | 1721.955
TF | 198
total | 17646.405

## Slide 23: Snow load
Roof floor and top roof are exposed to snow load
Error =
* 100% =0.7%.
floor | snow LOAD
TF | 296.97
RF | 1044.765
total | 1341.735
Floor number | Super imposed dead load (KN)
B2 | 4507.2
B1 | 4208.8
GF | 4146.68
F1 | 3346.8
F2 | 3346.8
RF | 0
TF | 0
Total | 19556.28
Super imposed dead load
This project has two SID; first one on the slab (include partition load tiles and fill) and the other outer shear wall (include masonry, mortar and plaster)
Total SID= 14232.2 + 19556.28 = 33778.5
Error =
*100% =3.4%

## Slide 24: Soil load :
Soil is covering the three basements floor in the north approach, and this affect on retaining wall.
K 0 = 1- sin α (α= 30 0), k =0.5
Unit weight equal 20 KN/m3
Live load = 15 KN/m3
Long of wall=31.25m
Total load = (845*31.25)+(97.5*31.25) =29453.1 KN/m
Error =0%

## Slide 25: Check moment in beams
The live load is chosen as an example of load carried by beams to make the comparison:
Beam Name | Moment by T.A.M (KN.m) | Moment by SAP (KN.m) | % of error
GB5 | 11.34 | 10.5 | 7.98
1B1 | 46.25 | 44.17 | 4.7
2B11 | 69.77 | 71.75 | 2.76

## Slide 26: Check moment in slabs

## Slide 27: Period calculation
Period from SAP2000=0.327 S
Error = 2.75 %

## Slide 28: Seismic load

## Slide 29: Structural design and evaluation

## Slide 30: Columns
Number of columns at the building 216 columns.
The columns uniformed into 9 sets in the basement floors and 8 sets in the upper floors.
Floor | Columns sets |  |  |  |  |  |  |  | 
B3 | 3BC1 | 3BC2 | 3BC3 | 3BC4 | 3BC5 | 3BC6 | 3BC7 | 3BC8 | 3BC9
B2 | 2BC1 | 2BC2 | 2BC3 | 2BC4 | 2BC5 | 2BC6 | 2BC7 | 2BC8 | 2BC9
B1 | 1BC1 | 1BC2 | 1BC3 | 1BC4 | 1BC5 | 1BC6 | 1BC7 | 1BC8 | 1BC9
Gr | GC1 | GC2 | GC3 | GC4 | GC5 | GC6 | GC7 | GC8 | -
1 | 1C1 | 1C2 | 1C3 | 1C4 | 1C5 | 1C6 | 1C7 | 1C8 | -
2 | 2C1 | 2C2 | 2C3 | 2C4 | 2C5 | 2C6 | 2C7 | 2C8 | -
Rf | RC1 | RC2 | RPC1 | RPC2 | - | - | - | - | -

## Slide 31: Columns
Dimensions

## Slide 32: Columns
Plan shows columns distribution at the floor

## Slide 33: Columns
The design of the columns.
SAP2000
Longitudinal
Lateral

## Slide 34: Columns
Floor No. |  |  |  | Reinforcement from structural drawings |  |  |  |  |  |  |  | Reinforcement from SAP2000 |  |  |  |  |  |  |  |  | 
Gr | (mm) | (mm) | (mm)2 | Longitudinal reinforcement |  |  |  | Lateral reinforcement |  |  |  | Longitudinal |  |  | Lateral reinforcement |  |  |  |  | Longitudinal | Lateral
Column No. | Width | Depth | area | # bars | ɸ | Ab | As | # legs | ɸ | Av | S | As | ɸ | # bars | As | ɸ | # legs | Max. S | Practical S | Comments | Comments
GC1 | 300 | 300 | 90000 | 8 | 14 | 153.86 | 1230.88 | 4 | 10 | 314 | 200 | 900 | 14 | 6 | 157 | 10 | 4 | 224 | 200 | Safe | Safe
GC2 | 400 | 400 | 160000 | 8 | 16 | 200.96 | 1607.68 | 4 | 10 | 314 | 200 | 1600 | 16 | 8 | 157 | 10 | 4 | 256 | 250 | Safe | Safe
GC3 | 400 | 400 | 160000 | 8 | 16 | 200.96 | 1607.68 | 4 | 10 | 314 | 200 | 1600 | 16 | 8 | 157 | 10 | 4 | 256 | 250 | Safe | Safe
GC4 | 400 | 400 | 160000 | 8 | 20 | 314 | 2512 | 4 | 10 | 314 | 200 | 1600 | 20 | 6 | 157 | 10 | 4 | 320 | 300 | Safe | Safe
GC5 | 400 | 400 | 160000 | 8 | 18 | 254.34 | 2034.72 | 4 | 10 | 314 | 200 | 1600 | 18 | 8 | 157 | 10 | 4 | 288 | 250 | Safe | Safe
GC6 | 400 | 400 | 160000 | 8 | 18 | 254.34 | 2034.72 | 4 | 10 | 314 | 200 | 1600 | 18 | 8 | 157 | 10 | 4 | 288 | 250 | Safe | Safe
GC7 | 400 | 400 | 160000 | 8 | 16 | 200.96 | 1607.68 | 4 | 10 | 314 | 200 | 1600 | 16 | 8 | 157 | 10 | 4 | 256 | 250 | Safe | Safe
GC8 | 400 | 400 | 160000 | 8 | 16 | 200.96 | 1607.68 | 4 | 10 | 314 | 200 | 1600 | 16 | 8 | 157 | 10 | 4 | 256 | 250 | Safe | Safe
Comparison between SAP2000 and office’s designs for the ground floor

## Slide 35: Columns
The differences between the two designs:
  3BC2 & 2BC2
  3BC8
  1C1
  1C2

## Slide 36: Columns
The column 1C1
Moments in 1C1
Moments in GC1

## Slide 37: Columns
The column 2C1
Axial loads in 2C1
Axial loads in GC1

## Slide 38: Columns
Axial forces diagram from SAP2000

## Slide 39: Shear walls
All the exterior walls and the elevators’ wells are shear walls.
Shear walls were treated as columns.

## Slide 40: Shear walls
Shear wall | Width (m) | Depth (m) | P (KN) | M (KN/m)
A | 9.3 | 0.2 | 4477.6 | 5203.375
B | 3.625 | 0.2 | 2231.61 | 332.54
C | 2.5 | 0.25 | 1296.6 | 171
D | 6.625 | 0.25 | 3901.54 | 3208
E | 6 | 0.2 | 4191.49 | 3699
F | 2.5 | 0.25 | 963.66 | 152.75
The shear walls were taken.

## Slide 41: Shear walls
Chart: Interaction diagram for shear wall A
| 0 | 14402.919 | 24208.505000000001 | 31435.861000000001 | 36126.729999999996 | 38395.850000000013 | 44056.53 | 46392.89 | 35802.44 | 20408.333999999992 | 0
 | 25207.75 | 25207.75 | 24607.24 | 21424.84 | 18138.71 | 14680.29 | 13058.76 | 10609.3 | 5748.84 | 889.332 | -4015.1162
 | 4477.6

## Slide 42: Beams
Number of beams sets varies from 12 to 16 depending on the floor.
Number of spans and the dimension of the beams different from one set to another.

## Slide 43: Beams
list of selected beams
Beam Name | Floor | Width | Depth
2BB9 | B2 | 400 | 800
2BB10 | B2 | 300 | 1500
1BB1 | B1 | 300 | 600
1BB2 | B1 | 300 | 600
1BB4 | B1 | 300 | 800
Gb1 | Gb | 300 | 600
Gb7 | Gb | 250 | 800
Gb10 | Gb | 300 | 1500
1B2 | B1 | 300 | 1005
1B12 | B1 | 250 | 800
1B16 | B1 | 400 | 800
2B2 | B2 | 300 | 1005
2B12 | B2 | 250 | 800
2B15 | B2 | 800 | 300
Rb2 | Rb | 300 | 900
Rb8 | Rb | 400 | 800
Rb17 | Rb | 400 | 800

## Slide 44: Beams
Design of beams:
  Longitudinal reinforcing.
  Lateral reinforcing.
  Structural drawings.

## Slide 45: Beams
TOP |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 
 |  |  |  |  |  | Structural Drawings |  |  |  |  |  | SAP2000 |  |  |  |  |  | 
 |  |  |  |  |  | Left |  | Middle |  | Right |  | Left |  | Middle |  | Right |  | 
Beam No. | Floor | width | depth | para. | Span | # Bars | ɸ | # Bars | ɸ | # Bars | ɸ | # Bars | ɸ | # Bars | ɸ | # Bars | ɸ | Comments
2BB9 | B2 | 400 | 800 | 2400 | 1 | 3 | 25 | 3 | 16 | 3 | 16 | 2 | 25 | 2 | 16 | 4 | 16 | The left and middle are safe, the right is not safe
 |  | 400 | 800 | 2400 | 2 | 3 | 25 | 3 | 16 | 3 | 25 | 2 | 25 | 2 | 16 | 2 | 25 | All are safe
 |  | 400 | 800 | 2400 | 3 | 3 | 25 | 3 | 16 | 3 | 25 | 2 | 25 | 2 | 16 | 2 | 25 | All are safe
 |  | 400 | 800 | 2400 | 4 | 3 | 16 | 3 | 16 | 3 | 25 | 7 | 16 | 3 | 16 | 2 | 25 | The left is not safe, the middle and right safe

## Slide 46: Beams
Top reinforcing differences.
Moment from gravity combination
Moment from earthquake combination

## Slide 47: Beams
Comments on beams:
  Longitudinal reinforcing steel.
  Lateral reinforcing.
  Deflection.

## Slide 48: Slabs
There is two types of slabs; one way ribbed slab and two way solid slab.
All slabs have a thickness of 30 cm.
A representative strip were taken in solid slabs and a representative sample slab were taken in ribbed slab.

## Slide 49: Slabs
Design of slabs:
  Two way solid slabs.
  One way ribbed slab.

## Slide 50: Slabs
M11 diagram for the second basement slab

## Slide 51: Slabs

## Slide 52: Slabs
Sample strip
TOP |  |  |  |  |  |  |  |  |  |  |  |  | 
 |  |  |  |  | Left |  |  | Middle |  |  | Right |  | 
 | Center |  |  |  | SAP2000 |  | office | SAP2000 |  | office | SAP2000 |  | office
Floor | Line | Span | Span length | Span width | p | As(mm2/m) | As (mm2/m) | p | As(mm2/m) | As (mm2/m) | p | As(mm2/m) | As (mm2/m)
B2 | 5 | 1 | 6825 | 3000 | 0.001074 | 279.16 | 565.2 | 0.000000 | 0.00 | 565.2 | 0.000583 | 151.59 | 3018.325
 |  | 2 | 2550 | 3000 | 0.000587 | 152.65 | 3018.325 | 0.000666 | 173.22 | 3018.325 | 0.002143 | 557.24 | 3018.325
 |  | 3 | 12650 | 3000 | 0.001918 | 498.70 | 3018.325 | 0.000000 | 0.00 | 565.2 | 0.003156 | 820.45 | 3018.325
 |  | 4 | 2550 | 3000 | 0.002309 | 600.40 | 3018.325 | 0.000862 | 224.08 | 3018.325 | 0.000482 | 125.19 | 3018.325
 |  | 5 | 6825 | 3000 | 0.000810 | 210.68 | 3018.325 | 0.000000 | 0.00 | 565.2 | 0.001506 | 391.59 | 565.2

## Slide 53: Slabs
Top moments on the strip ((K, P), (4, 9)) from moments M22
 | Gridlines |  |  | Top |  |  |  |  |  |  |  |  |  |  |  |  |  | 
 |  |  |  | sap |  |  | office |  | sap |  |  | office |  | sap |  |  | office | 
Floor | X | Y | Span | L | ƿ | As (SAP) | As | Different | M | ƿ | As | As | Different | R | ƿ | As | As | Different
1 | K,P | 4,9 | 1 | 19 | 0.0093 | 364.61 | 804.6 | -440.01 | 10 | 0.0047 | 183.7 | 804.6 | -620.92 | 20 | 0.0099 | 385.82 | 804.6 | -418.8
 |  |  | 2 | 25 | 0.0127 | 495.79 | 804.6 | -308.83 | 0 | 0.0000 | 0.00 | 157.0 | -157.00 | 30 | 0.0157 | 613.32 | 157.0 | 456.3

## Slide 54: Slabs
Comments on slabs
  Flexural steel.
  Punching shear.
  Deflection.

## Slide 55: Footing

## Slide 56: Single footing :

## Slide 57: Single footing :

## Slide 58: Single footing :

## Slide 59: Single footing :

## Slide 60: Wall footing

## Slide 61: Wall footing
Footing thicknesses:
from wide beam shear
qu = 616.5 KN /m2
ɸVc = Vu  d=266 mm & H =350mm
Office design : H = 500 mm
Reinforcement:
MU = 93.2 KN .m
𝛲 = 0.00359 ,𝐴𝑆 = 954 𝑚𝑚2/𝑚,𝐴𝑠 𝑚𝑖𝑛 == 630 𝑚𝑚2/𝑚
Longitudinal reinforcement = 630*1.3 =819 𝑚𝑚2
Structural drawing : long direction= 1230 𝑚𝑚2
short direction = 1004.8 𝑚𝑚2/𝑚

## Slide 62: Water tank footing

## Slide 63: Water tank footing

## Slide 64: Water tank footing
Sd = 1.26
Mu design = sd * Mu -* µ = 1.26 * 46.7 * 1.025 = 60.3 KN. m/m
Ρ = 0.000955 AS==391mm2/m
Use Asmin=0.0018*1000*500=900mm2/m.
Structural drawing :As = 2453.1 mm2/m

## Slide 65: Elevator footing

## Slide 66: Elevator footing
Stress=415.4 KPa<450KPa .
Dimension

## Slide 67: Elevator footing
Thickness
structural drawing noted the thickness of footing (H) equal to 500 mm and d =410 mm.
Vu = 222.7 KN /m
ɸVc = 0.75 *1/6 *√(f’c) *b*d = 271KN/ m
ɸVc > Vu (OK)
Reinforcement
M- = 139.6 KN.m/m , Ρ = 0.002237 ,
AS = 917 mm2 /m
Asmin = 900 mm2 /m .
Structural drawing : As = 2453.1 mm2 /m

## Slide 68: Combined footing design
A combined footing contains two columns lie at the intersection of grids E6 and F6 will be evaluated.

## Slide 69: Check on dimensions
Area Of Footing | 
Designed | 19.25 m²
Required | 9.256 m²
Footing Thickness |  |  | 
 | Can be resisted (KN) | Applied (KN) | Met or not
Wide beam shear | 1666.82 | 1790 | met
Punching shear | 6135.4 | 3199.6 | doesn’t meet

## Slide 70: Reinforcement check:
Bottom Steel |  |  |  |  | 
In long direction |  |  | In short direction |  | 
Reinforcement from AutoCAD drawings | As (mm²) | As calculated (mm) | Reinforcement from AutoCAD drawings | As (mm²/m) | As calculated (mm²/m)
ɸ25@150 | 3437 | 8391.6 | ɸ20@150 | 2198 | 1440
Top Steel |  |  |  |  | 
In long direction |  |  | In short direction |  | 
Reinforcement from AutoCAD drawings | As (mm²) | As calculated (mm) | Reinforcement from AutoCAD drawings | As (mm²/m) | As calculated (mm²/m)
ɸ18@150 | 1782 | 8391.6 | ɸ16@150 | 1407 | 1440

## Slide 71: Retaining wall design
Retaining wall lies in southern side of the building, has a thickness of 40 cm and a height of 13 m, supported by slabs in B3, B2 and B1.
Structural Model

## Slide 72: Reinforcement of wall
Floor | from soil side |  |  | From building side |  | 
 | Reinforcement from AutoCAD drawings | As (mm2) | As(mm2)(from SAP) | Reinforcement from AutoCAD drawings | As (mm) | As (from SAP)
B3 | Ø20/200 | 1570 | 1122 | Ø16/200 | 1005 | 1360
B2 | Ø20/200 | 1570 | 1122 | Ø16/200 | 1005 | 1122
B1 | Ø16/200 | 1005 | 1122 | Ø12/200 | 565 | 1122
GF | Ø12/200 | 565 | 1122 | Ø12/200 | 565 | 1122
Floor | Reinforcement from AutoCAD drawings | As (mm²) | As (shrinkage)
B3 | Ø12/200 | 565 | 360
B2 | Ø12/200 | 565 | 360
B1 | Ø10/200 | 392.5 | 360
GF | Ø10/200 | 392.5 | 360
Vertical reinforcement
Horizontal reinforcement

## Slide 73: Check on dimensions
1- Check footing dimensions depending on bearing capacity (didn't met).
2- Check on footing thickness from wide beam shear (met).
Footing reinforcement |  |  |  |  |  | 
 | Short Direction |  |  | Long Direction |  | 
 | from AutoCAD drawings | As(mm²/m) | As(mm²/m) (calculated) | from AutoCAD drawings | As(mm²/m) | As(mm²/m) (calculated)
Top steel | Ø14/200 | 770 | 450 | Ø14/200 | 770 | 450
Bottom steel | Ø20/200 | 1570 | 6660 | Ø16/200 | 1005 | 1419
Reinforcement of wall footing

## Slide 74: Thank you for your attention