## Slide 1: Graduation Project Indoor Cell Planning For An-Najah Educational National Hospital
In Corporation With Jawwal
Superviser
Dr.Allam Mousa
Prepared by
Mohammed Donbok
Haitham Fahed

## Slide 3: Problems’ Description
This project discussed the problems existing in An Najah Educational National Hospital which are poor quality calls, drop calls and call setup failure. These problems are because of weak signal strength.

## Slide 4: Project’s Goal
Solve the problems inside the building of An Najah Educational National Hospital which is considered to serve the areas north of the West Bank, with an acceptable range of coverage, capacity, quality.

## Slide 5: Problem Solution
Design a system that will distribute a uniform strong signal inside the building, from the indoor cell, using indoor system in order to provide sufficient coverage, quality, capacity and dominance.
RX-Level | 
Deep Indoor | -45 dBm to -64 dBm
Indoor | -65 dBm to -74 dBm
InCar | -75 dBm to -84 dBm
Outdoor | -85 dBm to -94 dBm
Bad Service | -95 dBm to -110 dBm

## Slide 6: System Components
1- Radio Base Station (RBS) : Ericsson 2308, 4 TRUs, 34 dBm output power.

## Slide 7: Cont’d (System Components)
2- Antennas : Omni and Directional Antennas.
3- Splitters : 2,3 and 4 ports.
4- Cables: ½in with 7dB/100m loss.

## Slide 8: The Design
1- Passive or Active Distributed Antenna Systems?
Two system types can be used for indoor solution, Active DAS or Passive DAS.
In this project Passive DAS has been used for these reasons:
Components from different manufacturers are compatible.
It can be installed in harsh environment.
No high data rate needed.
No DC power supply is needed for the equipments.

## Slide 9: Cont’d ( The Design )
2- Capacity Dimensioning.
These conditions should be determined to calculate the number of channels that are needed to solve the capacity problem.
Number of subscriber = 900 subscribers.
Types of subscriber : Normal = 25 mE.
Grade of service (Call Blocking Rate ) = 2%.

## Slide 10
Total Load = number of Subscribers X Load Per User
Total Load = 900 X 0.025
≈ 23 E
According to Erlang B-Table with 2% GOS,
32 channels are needed.
Cont’d (Capacity Dimensioning)

## Slide 11
Every TRUs can carry 8 channels so
32/8 = 4 TRUs are needed.
The system uses 3 channels for control so
32 – 3 = 29 traffic channels.
Cont’d (Capacity Dimensioning)

## Slide 12: Indoor Link Calculations ( By Hand )
1-Link Budget: The power that just comes out antenna can be calculated according to this equation:

## Slide 13
First Try
Antenna Locations in B1
Cont’d (Indoor Link Budget)

## Slide 14
Power Splitting
Cont’d (First Try)

## Slide 15
Basement one |  |  |  | 
Antenna | Loss in Cable | Loss in splitter | Total Loss | Tx (antenna
Tx 1-0 | 1.2 | 9.3 | 10.5 | 5
Tx 1-1 | 1.2 | 9.3 | 10.5 | 5
Tx 1-2 | 2.5 | 9.3 | 11.8 | 3.7
Tx 1-3 | 3.2 | 9.3 | 12.5 | 3
Tx 1-4 | 2.5 | 12.71 | 15.21 | 0.29
Tx 1-5 | 3.1 | 12.71 | 15.81 | -0.31
Tx 1-6 | 3.2 | 12.71 | 15.91 | -0.41
Tx 1-7 | 3.8 | 11 | 14.8 | 0.7
Tx 1-8 | 4.1 | 11 | 15.1 | 0.4
Tx 1-9 | 4.9 | 11 | 15.9 | -0.4
Tx 1-10 | 5.1 | 11 | 16.1 | -0.6
Floor | Antenna # | RBS output power (dBm) | Cable Length (m) |  |  | 2 Port Splitter | 3 Port Splitter | 4 Port Splitter | TX Power (dBm)
B1 | TX-10 | 34 | 25 | 11 | 0 | 6 | 1 | 0 | 7.95
B1 | TX-11 | 34 | 25 | 11 | 0 | 6 | 1 | 0 | 7.32
B1 | TX-12 | 34 | 25 | 11 | 0 | 6 | 1 | 0 | 5.50
B1 | TX-13 | 34 | 25 | 11 | 0 | 6 | 1 | 0 | 5.64
B1 | TX-14 | 34 | 25 | 11 | 0 | 4 | 3 | 0 | 3.03
B1 | TX-15 | 34 | 25 | 11 | 0 | 4 | 3 | 0 | 2.40
B1 | TX-16 | 34 | 25 | 11 | 0 | 4 | 3 | 0 | 0.27
B1 | TX-17 | 34 | 25 | 11 | 0 | 6 | 2 | 0 | -1.19
B1 | TX-18 | 34 | 25 | 11 | 0 | 6 | 2 | 0 | -0.98
B1 | TX-19 | 34 | 25 | 11 | 0 | 6 | 2 | 0 | -2.10
B1 | TX-110 | 34 | 25 | 11 | 0 | 6 | 2 | 0 | -3.15
link Budget Calculations for B1 Floor

## Slide 16
Antenna Location in B1
Final Design
Cont’d (Indoor Link Budget)

## Slide 17
Power Splitting

## Slide 18
Floor | Antenna # | RBS output power (dBm) | Cable Length (m) |  |  | 2 Port Splitter | 3 Port Splitter | 4 Port Splitter | TX Power (dBm)
B1 | 11 | 34 | 63 | 10 | 35 | 1 | 2 | 1 | 7.47
B1 | 12 | 34 | 63 | 10 | 18 | 1 | 2 | 1 | 8.66
B1 | 13 | 34 | 63 | 10 | 9 | 0 | 3 | 1 | 7.53
B1 | 14 | 34 | 63 | 10 | 9 | 0 | 3 | 1 | 7.53
B1 | 15 | 34 | 63 | 10 | 20 | 0 | 3 | 1 | 6.76
B1 | 16 | 34 | 0 | 5 | 48 | 1 | 1 | 2 | 10.07
B1 | 17 | 34 | 0 | 5 | 22 | 1 | 1 | 2 | 11.89
B1 | 18 | 34 | 0 | 5 | 20 | 1 | 1 | 2 | 12.03
B1 | 19 | 34 | 0 | 5 | 3 | 1 | 1 | 2 | 13.22
B1 | 112 | 34 | 0 | 5 | 20 | 1 | 1 | 2 | 12.03
B1 | 113 | 34 | 0 | 5 | 34 | 1 | 1 | 2 | 11.05
B1 | 110 | 34 | 40 | 5 | 28 | 2 | 2 | 1 | 6.81
B1 | 111 | 34 | 40 | 5 | 14 | 2 | 2 | 1 | 7.79
B1 | 114 | 34 | 40 | 5 | 21 | 2 | 2 | 1 | 7.30
B1 | 115 | 34 | 40 | 5 | 7 | 2 | 2 | 1 | 8.28
B1 | 116 | 34 | 40 | 5 | 28 | 2 | 2 | 1 | 6.81
B1 | 117 | 34 | 40 | 5 | 34 | 2 | 2 | 1 | 6.39
link Budget for B1

## Slide 19
Lifts link Budget
Antenna # | RBS output power (dBm) | Cable Length (m) |  |  | 2 Port Splitter | 3 Port Splitter | 4 Port Splitter | TX Power (dBm)
LA1 | 34 | 34 |  | 1 | 1 | 2 | 1 | 19.43
LA2 | 34 | 34 |  | 1 | 1 | 2 | 1 | 19.43
LC1 | 34 | 40 |  | 1 | 0 | 3 | 1 | 17.25
LC2 | 34 | 40 |  | 1 | 0 | 3 | 1 | 17.25
LC3 | 34 | 41 |  | 1 | 0 | 3 | 1 | 17.18
LC4 | 34 | 42 |  | 1 | 1 | 2 | 1 | 18.87
LC5 | 34 | 43 |  | 1 | 1 | 2 | 1 | 18.80
LB1 | 34 | 63 | 25 | 1 | 2 | 1 | 1 | 17.41
LB4 | 34 | 63 | 24 | 1 | 2 | 1 | 1 | 17.48

## Slide 20
2- Path loss Calculations
FSPL : Free Space Path Loss ( dB )
d: Distance in (Km)
f: frequency ( MHz)
Cont’d (Indoor Link Calculations)

## Slide 21
Path Loss Samples Of Basement Two
Floor | Point # | TX Power (dBm) | EIRP (dBm) | Distance (m) | Freq. (MHz) | FSPL (dB) | # of walls | Loss In Walls (dB) | RX Power (dBm)
B2 | P212 | 10.47 | 12.47 | 09.60 | 950 | -51.7 | 4 | -12.80 | -52.07
B2 | P210 | 11.66 | 13.66 | 11.30 | 950 | -53.1 | 1 | -3.20 | -42.69

## Slide 22: Software Results
1- Link budget.
Antenna # | Hand Calculations | iBwave Calculations | Difference
115 | 8.82 dBm | 7.76 dBm | 1.06 dB
Notes: Why

## Slide 23
2- Path Loss
Sample | Hand calculation | iBwave calculation | Results
p212 | -52 dBm | -51 to -54 dBm | Deep indoor

## Slide 30: Conclusion
Indoor systems can be a solution if the coverage, quality and capacity from outdoor cells are weak.
The indoor system will radiate a dominant signal inside a building.
The way of splitting affects on RX-signal.
The design process includes: capacity dimensioning, choosing the components, deciding the target coverage level and distributing the antennas inside the building.

## Slide 31
This design solve the existing problems completely which means that the goal of this project has been achieved.
The most important areas inside the hospital have a deep indoor signal level ( >-64 dBm ).
The design can serve 900 subscribers.
Cont’d (Conclustion)

## Slide 32: Questions

## Slide 33: BIG THANKS AN-Najah National University JAWWAL COMPANY