An-Najah National University

Faculty of Engineering

Electrical Engineering department

Design and analysis of an electric power system, with the design of a load flow program using MATLAB

Prepared by : 1- Saleem Shalabi 2- Rami Hamed 3- Salama Salama

Supervisor : Dr. Maher Khammash

2010-2011

إهداء

نهدي هذا العمل المتواضع إلى نور الحياة ونبع الحنان أمهاتنا الفاضلات

وإلى ذلك الرجل الذي أفنى حياته من أجل تحقيق طموحاتنا في الحياة آبائنا الفاضلين

ونهدي أيضا هذا العمل إلى أساتذتنا الفاضلين في قسم الهندسة الكهربائية  وعلى رأسهم الدكتور ماهر خماش الذي أعطانا من وقته وإرشاداته التي كان لها الفضل الكبير في إنجاح هذا المشروع .

والله ولي التوفيق

Courtesy

We dedicate this humble work to the light of life and compassion spring our virtuous mothers.
And to the men who dedicated there life to achieve our ambitions in life our virtuous fathers.
And also dedicate this work to the virtuous our professors in the Department of Electrical Engineering, headed by Dr. Maher Khammash which has given us of his time and guidance, which had a great credit to the success of this project.

Contents

Introduction	5

A figure of AC generators	5

Chapter One Intoduction to the project	8

The transmission line	9

The network	9

The distances table…………………………………	10

The load table………………………………….	10

Chapter Tow Balance of Real and Reactive Power 	11

Balance of real power  ………………………………………………………………………………………………….12

Balance of reactive power………………..	12

Chapter Three  network design 	14

The network designs……………………….	15

Chapter Four Technico- Econmical Comparison 	28

3.1-Selection of transformers :…………	29

3.2- selection of transmission lines:-	36

3.3. Selection of Switch gear:……..	41

3.4. The economical study:………..	44

3.4.1: Capital cost	45

3.4.2: Running cost	49

Chapter Five  Load Flow Study 	65

4.1 Data for load flow:………………	66

4.2. The Maximum Load State Analysis:	67

4.2.1. Original Condition of the network:	67

4.2.1. Improvement of the maximum load state:	68

4.3. Minimum load state:………….	71

4.3.1. Original minimum load state:	71

4.3.2 Improvement of minimum load state:	73

4.4 After fault condition:…………..	76

4.4.1 Fault at line (A-1)	76

4.4.2 Improvement of after fault condition:	77

4.5 The economical benefit of using the capacitors:	78

Appendix A………………………………………………………………………………………………………………………

Appendix B………………………………………………………………………………………………………………………

Appendix C……………………………………………………………………………………………………………………….

Appendix D……………………………………………………………………………………………………………………….

Appendix E ……………………………………………………………………………………………………………………….

References ………………………………………………………………………………………………………………………..

# Introduction

Electric power systems:

It's a complex assemblage of equipment and circuits for generating, transmitting, transforming, and distributing electrical energy, and the electrical energy required to supply electric power systems is produced in generating stations, commonly called power plants. Such generating stations, however, should be considered as conversion facilities in which the heat energy of fuel (coal, oil, gas, or uranium) or the hydraulic energy of falling water is converted to electricity and here a presentation of this equipment:

- Generators :

A generator forces electrons in the windings to flow through the external electrical circuit. It is somewhat analogous to a water pump, which creates a flow of water but does not create the water inside. The source of mechanical energy may be a reciprocating or turbine steam engine, water falling through a turbine or waterwheel, an internal combustion engine, a wind turbine, a hand crank, compressed air or any other source of mechanical energy.

# A figure of AC generators

- Transmission line :

It will be link between buses and carry the high voltages with long distance and fewer losses,(and it will be studied well in this search).

3) Transformers:

Transformers provide an additional means of control of the flow of both real and reactive power. Our usual concept of the function of transformers in a power system is that of changing from one voltage level to another, as when a transformer converts the voltage of a generator to the transmission-line voltage. However, transformers which provide a small adjustment of voltage magnitude, usually in the range of ±10% and others which shift the phase angle of the line voltages are important components of a power system. Some transformers regulate both the magnitude and phase angle.

4) The load:

The load study's principle is to determine the current, the voltage, real power and reactive power at the generation buses in the network under exiting or contemplated conditions of normal operation. Load flow is essential in design the future development.  Every power system have a special operation of the system depend on knowing the effects of this power system with other power systems and we will have new loads ,new generating stations and new transmission lines before they are installed.

Chapter One

The network

The transmission line:

The transmission system carries electric power efficiently and in large amounts from generating stations to consumption areas. Such transmission is also used to interconnect adjacent power systems for mutual assistance in case of emergency and to gain for the interconnected power systems the economies possible in regional operation, and our project talks about this transmission line and how to choose the most reliable system to deliver electrical energy with the minimum loss of it, this reliability achieved by chose the suitable materials that used in the line that carry the electric energy depending on the length if the T.L and the resistance, capacitance and reactance of the wire ,and we also going to make our own program to analysis the system.

The network:

Our network is a Russian network it's that we are going to design and analysis our design to get the most reliable design.

The first part of our project is to define a network and get the optimum design of this network depending on the data we have.

And the data is:

The following graph shows the pleases of the substation according to the main station:

All the distances between the main station and different substation (buses) and between themselves in KM shown the following table:

## The distances table

|  | 1 | 2 | 3 | 4 | 5 | 6 |
| --- | --- | --- | --- | --- | --- | --- |
| A | 75 | 65 | 80 | 95 | 95 | 105 |
| 1 | - | 40 | 20 | 25 | 50 | 60 |
| 2 | 40 | - | 30 | 60 | 30 | 65 |
| 3 | 20 | 30 | - | 30 | 30 | 40 |
| 4 | 25 | 60 | 30 | - | 45 | 35 |
| 5 | 50 | 30 | 30 | 45 | - | 20 |
| 6 | 60 | 65 | 40 | 35 | 20 | - |

And we have the power at each substation that includes the real, reactive power, power factor.

## The load table

| Load | S(MVA) | 1st class | 2nd class | 3rd class | Power factor | P(MW) | Q(MVAR) |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | 30 | + | + | + | 0.8 | 24 | 18 |
| 2 | 35 | + | + | + | 0.76 | 26.6 | 22.75 |
| 3 | 20 | + | + | + | 0.83 | 16.6 | 11.15 |
| 4 | 12 | - | + | + | 0.85 | 10.2 | 6.32 |
| 5 | 15 | + | + | + | 0.9 | 13.5 | 6.52 |
| 6 | 8 | + | + | + | 0.78 | 6.24 | 5.076 |
|  |  |  |  |  |  | 97.14 | 69.816 |

# Chapter Tow

# Balance of real and reactive power

- Balance of real power :

In this section we calculate the power needed to be generated for this network and we take into a count the power loss in the transmission lines and T.R, and also the future expansion on the network:

PG=P load+ P loss

PG=0.9 PL+ (0.05-0.075) PL

P L=97.14(MW).

PG=(0.9*97.14)+(0.075*97.14)

=87.426+7.2855

P G total =94.7115 (MW)

PG'=1.2 PG=113.654 (MW)

- Balance of reactive power:

This part is important because we want to reach an economical power factor, the power factor in our network is 0.8 and we studied the load to calculate the capacitor banks needed to correct the power factor:

QA + QT.L + Qc= QL +∆ QT.L+∆QT.R

QT.L=∆ QT.L

∆QT.R=10%*S*M *#of T.R

S=P2+Q2= 97.142+69.8162=119.62

M=2

∆QT.R=0.1*119.62*22= 47.848

PG'=113.654 (MW)

QA=113.654*tancos-10.8=85.2405 MAVR

P.F economical = costan-1(QL-Qc)PL∑

QC∑=QL∑ + ∆QT.R – QA

=69.816+47.85-85.2405=37.393 MVAR

P.F economical =0.933

Now to calculate the Qc for each bus using this equation

Q C n=P n tan(cos-1P.Fold-cos-1P.Feco. )

QC1=24 * tan(cos-10.8 -cos-10.933)=6.7 ≅9 MVAR

QC2=26.6 * tan(cos-10.76 -cos-10.933)=9.4 ≅12 MVAR

QC3=16.6 * tan(cos-10.83 -cos-10.933)=3.77 ≅6 MVAR

QC4=10.2 * tan(cos-10.85 -cos-10.933)=1.93 ≅3 MVAR

QC5=13.5 * tan(cos-10.9 -cos-10.933)=1.125 ≅3 MVAR

QC6=6.24 * tan(cos-10.78 -cos-10.933)=1.987 ≅3 MVAR

Now we have new reactive power on each load:

QL new 1=18 – 9 =9 MVAR

QL new 2=22.75 – 12 = 10.75 MVAR

QL new 3=11.15 – 6 = 5.15 MVAR

QL new 4 = 6.32 – 3 = 3.32 MVAR

QL new 5 = 6.52 – 3 = 3.52 MVAR

QL new 6 = 5.076 – 3 = 2.076 MVAR

The new Qc total = 33.816 MVAR

# Chapter Three

Network Design

The network designs:

In this chapter we calculate the voltage in each branch using this function:

V=1000√((2500\P)+(500\L))  ;where V:KV , P: MW  ,  L: KM

Put in the ring network we use this method to calculate the power to be used in the voltage law:

Like this we make the connection like that:

And use this low:

P1-3=P3*L2-3+L3-1+P2L2-1(L1-3+L3-2+L2-1)

P1-2=P2*L2-3+L3-1+P3L3-1(L1-3+L3-2+L2-1)

P3-2=P1-3 – P3

For the design of the network we have 9 schematics that contain two groups and for this schematics we going to calculate the voltage that would be transmitted in the lines:

- Radial schematics which is 6 designs:

- First network

| # of Branch | Length (KM) | Distance (KM) | P (MW) | Q (MVAR) | V cal (KV) | V st (KV) | # of T.R |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | 150 | 75 | 70.54 | 23.66 | 154.1 | 220 | 0 |
| 2 | 130 | 65 | 26.6 | 10.75 | 99.17 | 110 | 1 |
| 3 | 40 | 20 | 46.54 | 14.066 | 112.7 | 220 | 0 |
| 4 | 60 | 30 | 10.2 | 3.32 | 61.8 | 110 | 1 |
| 5 | 60 | 30 | 19.74 | 5.596 | 83.5 | 110 | 1 |
| 6 | 40 | 20 | 6.24 | 2.076 | 48.47 | 110 | 1 |
| Total | 480 | 240 | 179.86 | 59.468 |  |  | 4 |

2- Second network

| # of Branch | Length (KM) | Distance (KM) | P (MW) | Q (MVAR) | V cal (KV) | V st (KV) | # of T.R |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | 150 | 75 | 57.04 | 19.546 | 140 | 220 | 0 |
| 2 | 130 | 65 | 40.1 | 14.27 | 119.49 | 220 | 0 |
| 3 | 40 | 20 | 33.04 | 10.546 | 99.668 | 110 | 1 |
| 4 | 60 | 30 | 16.44 | 5.396 | 76.98 | 110 | 1 |
| 5 | 60 | 30 | 13.5 | 3.52 | 70.38 | 110 | 1 |
| 6 | 70 | 35 | 6.24 | 2.076 | 49.09 | 110 | 1 |
| Total | 510 | 255 | 245.7 | 55.354 |  |  | 4 |

3- Third network

| # of Branch | Length (KM) | Distance (KM) | P (MW) | Q (MVAR) | V cal (KV) | V st (KV) | # of T.R |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | 150 | 75 | 40.6 | 14.15 | 121.05 | 220 | 0 |
| 2 | 130 | 65 | 56.54 | 19.666 | 137.08 | 220 | 0 |
| 3 | 40 | 20 | 16.6 | 5.15 | 75.46 | 110 | 1 |
| 4 | 90 | 45 | 16.44 | 5.396 | 78.28 | 110 | 1 |
| 5 | 60 | 30 | 29.94 | 8.916 | 99.916 | 110 | 1 |
| 6 | 70 | 35 | 6.24 | 2.076 | 49.09 | 110 | 1 |
| Total | 540 | 270 | 166.36 | 53.354 |  |  | 4 |

4- Fourth network

| # of Branch | Length (KM) | Distance (KM) | P (MW) | Q (MVAR) | V cal (KV) | V st (KV) | # of T.R |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | 80 | 40 | 50.8 | 17.47 | 127.295 | 220 | 0 |
| 2 | 130 | 65 | 97.1 | 33.816 | 172.95 | 220 | 0 |
| 3 | 40 | 20 | 26.8 | 8.47 | 91.947 | 110 | 1 |
| 4 | 60 | 30 | 10.2 | 3.32 | 61.807 | 110 | 1 |
| 5 | 60 | 30 | 19.74 | 5.596 | 83.5 | 110 | 1 |
| 6 | 40 | 20 | 6.24 | 2.076 | 48.47 | 110 | 1 |
| Total | 410 | 205 | 210.12 | 70.748 |  |  | 4 |

5- Fifth network

| # of Branch | Length (KM) | Distance (KM) | P (MW) | Q (MVAR) | V cal (KV) | V st (KV) | # of T.R |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | 150 | 75 | 40.6 | 14.15 | 121.05 | 220 | 0 |
| 2 | 130 | 65 | 56.54 | 19.66 | 137.08 | 220 | 0 |
| 3 | 40 | 20 | 16.6 | 5.15 | 75.46 | 110 | 1 |
| 4 | 90 | 45 | 10.2 | 3.32 | 62.47 | 110 | 1 |
| 5 | 60 | 30 | 29.94 | 5.596 | 99.916 | 110 | 1 |
| 6 | 60 | 30 | 6.24 | 2.076 | 48.47 | 110 | 1 |
| Total | 510 | 225 | 210.12 | 49.952 |  |  | 4 |

6- Sixth network

| # of Branch | Length (KM) | Distance (KM) | P (MW) | Q (MVAR) | V cal (KV) | V st (KV) | # of T.R |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | 150 | 40 | 70.54 | 23.066 | 144.4 | 220 | 0 |
| 2 | 130 | 65 | 97.14 | 33.816 | 172.928 | 220 | 0 |
| 3 | 40 | 20 | 46.54 | 14.066 | 112.7 | 220 | 0 |
| 4 | 60 | 30 | 16.44 | 5.396 | 78.28 | 110 | 1 |
| 5 | 60 | 30 | 29.94 | 8.916 | 99.416 | 110 | 1 |
| 6 | 40 | 20 | 6.24 | 2.076 | 49.09 | 110 | 1 |
| Total | 470 | 235 | 266.84 | 87.336 |  |  | 3 |

- Radial schematics which is 3 designs:

7- The seventh network

| # of Branch | Length (KM) | Distance (KM) | P (MW) | Q (MVAR) | V cal (KV) | V st (KV) | # of T.R |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | 150 | 75 | 34.2 | 12.52 | 111.98 | 220 | 0 |
| 2 | 130 | 65 | 26.6 | 10.75 | 99.17 | 110 | 1 |
| 3 | 160 | 80 | 40.139 | 15.15 | 120.8 | 220 | 0 |
| 4 | 50 | 25 | 10.2 | 3.32 | 61.4 | 110 | 1 |
| V3-5 | 50 | 50 | 11.773 | 5 | 66 | 110 | 1 |
| V3-6 | 40 | 40 | 7.966 | 3.553 | 55.5 | 110 | 1 |
| V5-6 | 20 | 20 | 3.8 | 1.446 | 38.266 | 110 | 1 |
| Total | 600 | 355 | 266.84 | 51.739 |  |  | 5 |

8- The eighth network

| # of Branch | Length (KM) | Distance (KM) | P (MW) | Q (MVAR) | V cal (KV) | V st (KV) | # of T.R |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | 150 | 75 | 55.145 | 19.834 | 138.673 | 220 | 0 |
| 2 | 130 | 65 | 46.34 | 16.346 | 127.34 | 220 | 0 |
| V1-3 | 20 | 20 | 15.573 | 7.34 | 73.4 | 110 | 1 |
| V1-4 | 25 | 25 | 11.226 | 6.08 | 64.2 | 110 | 1 |
| V3-4 | 30 | 30 | 4.346 | 1.25 | 41.1 | 110 | 1 |
| 5 | 60 | 30 | 19.74 | 5.596 | 83.5 | 110 | 1 |
| 6 | 40 | 20 | 6.24 | 2.076 | 48.47 | 110 | 1 |
| Total | 455 | 256 | 266.84 | 57.406 |  |  | 5 |

9- The ninth network

| # of Branch | Length (KM) | Distance (KM) | P (MW) | Q (MVAR) | V cal (KV) | V st (KV) | # of T.R |
| --- | --- | --- | --- | --- | --- | --- | --- |
| V3-1 | 20 | 20 | 21.62 | 7.38 | 84.42 | 110 | 1 |
| 2 | 130 | 65 | 112.48 | 38.332 | 182.57 | 220 | 0 |
| 3 | 60 | 30 | 59.9 | 19.19 | 130.85 | 220 | 0 |
| V3-4 | 30 | 30 | 12.52 | 3.98 | 68 | 110 | 1 |
| V1-4 | 25 | 25 | 9.16 | 3.4 | 58.42 | 110 | 1 |
| 5 | 60 | 30 | 19.74 | 5.596 | 83.53 | 110 | 1 |
| 6 | 40 | 20 | 6.24 | 2.076 | 48.47 | 110 | 1 |
| Total | 365 | 220 | 241.66 | 79.95 |  |  | 5 |

Now for the table of all systems:

| # of network | Length (KM) | Distance (KM) | P (MW) | Q (MVAR) | # of T.R |
| --- | --- | --- | --- | --- | --- |
| 1 | 480 | 240 | 179.86 | 59.468 | 4 |
| 2 | 510 | 255 | 245.7 | 55.354 | 4 |
| 3 | 540 | 270 | 166.36 | 53.354 | 4 |
| 4 | 410 | 205 | 210.12 | 70.748 | 4 |
| 5 | 510 | 225 | 210.12 | 49.952 | 4 |
| 6 | 470 | 235 | 266.84 | 87.336 | 3 |
| 7 | 600 | 355 | 266.84 | 51.739 | 5 |
| 8 | 455 | 256 | 266.84 | 57.406 | 5 |
| 9 | 365 | 220 | 241.66 | 79.95 | 5 |

From this table we will choose 4 networks to be studied in the first semester and these networks are:

- Network #1 because it has the smallest length.

- Network #4 because it has the smallest length.

- Network #8 which is ring and it has the smallest length.

- Network #9 which is ring and it has the smallest length.

# Chapter Four

Technical & Economical study

In this chapter we will study the four network that we chose in the previous chapter to select the economical design for this distribution points, so we going to calculate the cost for all  networks that’s includes the component and running cost :

- Cost of transformers.

- Cost of transmission lines.

- Cost of switchgears, C.B and bus-bar isolation.

- Cost of maintenance.

- Cost of the power lost in the component.

Form the pervious points we will achieve the most economical network , and to do so we should select the transformers, T.L ,and switchgears.

## 3.1-Selection of transformers:-

The selection of transformers depends on the rated apparent power that flows in the transformers (S).

To insure reliability of the transformation, two transformers are used so we can select less capacity for each transformer. and we select the transformer to bear a 40% over its normal lead, so when a fault accurse in one of the transformers we can do the maintenance without affecting the power flow in the network or the bus.

In the selection we will take in consideration that 70% of the power flows in one transformer . so

Snom(transformer)= 0.7 of Snom(lead)   Snom(transformer)= Snom(lead)\ 1.4.

From sertin tables we will select the transformer depending in Snom(transformer) and get the operating voltage of that transformer and resistance, reactance , excitation branch in(VAR) and the power loss in Rc , Xm (W).

** Selection of transformers in network #1

The following calculations represent the selection of transformers used in network #1.

- Transformer at bus 1:

this transformer will convert the 220 (kv) – 6.6(kv).

So

Snom(transformer)= Snom(lead)1.4

Snom(bus1) =25.6 MVA

Snom(transformer)= 25.61.4

Snom(transformer)= 18.29 MVA

At 220 (KV) transformer from the tables will be rated at 40 (MVA) .

VH\ VL= 230\6.6 (KV).

RT=5.6 Ω  ,  XT=158.7 Ω .

∆PO.C=0.005 MW  , ∆QO.C=0.36 MVAR.

- Transformer at bus A:

this transformer will convert the 220 (kv) – 110(kv).

So

Snom(transformer)= Snom(lead)1.4

Snom(bus1) =28.69 MVA

Snom(transformer)= 28.691.4

Snom(transformer)= 20.64 MVA

At 220 (KV) transformer from the tables will be rated at 25 (MVA) .

VH\ VL= 230\110 (KV).

RT=2.54 Ω  ,  XT=55.9 Ω .

∆PO.C=0 MW  , ∆QO.C=0.36 MVAR.

- Transformer at bus 2:

This transformer will convert the 110 (kv) – 6.6(kv).

So

Snom(transformer)= Snom(lead)1.4

Snom(bus2) =28.69 MVA

Snom(transformer)= 28.691.4

Snom(transformer)= 20.642 MVA

At 110 (KV) transformer from the tables will be rated at 25 (MVA) .

VH\ VL= 115\6.5 (KV).

RT=2.54 Ω, XT=55.9 Ω .

∆PO.C=0.027 MW, ∆QO.C=0.175 MVAR.

- Transformer at bus 3:

This transformer will convert the 220 (kv) – 6.6(kv).

So

Snom(transformer)= Snom(lead)1.4

Snom(bus3) =(36P )2+(36Q )2

Snom(bus3)=48.616 MVA

Snom(transformer)= 48.6161.4

Snom(transformer)= 34.727 MVA

At 220 (KV) transformer from the tables will be rated at 40 (MVA) .

VH\ VL= 230\121\6.6 (KV).

RTH=1.4 Ω,RTM=1.4Ω, RTL=2.8Ω

XTH=104 Ω, XTM=0,XTL=195.6 Ω .

∆PO.C=0.045 MW, ∆QO.C=0.315 MVAR.

- Transformer at bus 4:

This transformer will convert the 110 (kv) – 6.6(kv).

So

Snom(transformer)= Snom(lead)1.4

Snom(bus3) =10.73 MVA

Snom(transformer)= 10.731.4

Snom(transformer)= 7.664 MVA

At 110 (KV) transformer from the tables will be rated at 10 (MVA) .

VH\ VL= 115\6.6 (KV).

RT=7.95 Ω, XT=139 Ω .

∆PO.C=0.014 MW, ∆QO.C=0.070 MVAR.

- Transformer at bus 5:

This transformer will convert the 110 (kv) – 6.6(kv).

So

Snom(transformer)= Snom(lead)1.4

Snom(bus5) =13.95 MVA

Snom(transformer)= 13.951.4

Snom(transformer)= 9.964 MVA

At 110 (KV) transformer from the tables will be rated at 10 (MVA) .

VH\ VL= 115\6.6 (KV).

RT=7.95 Ω, XT=139 Ω .

∆PO.C=0.014 MW, ∆QO.C=0.070 MVAR.

- Transformer at bus 6:

This transformer will convert the 110 (kv) – 6.6(kv).

So

Snom(transformer)= Snom(lead)1.4

Snom(bus2) =6.58 MVA

Snom(transformer)= 6.581.4

Snom(transformer)= 4.664 MVA

At 110 (KV) transformer from the tables will be rated at 6.3 (MVA) .

VH\ VL= 115\6.6 (KV).

RT=14.7 Ω  ,  XT=220.4 Ω .

∆PO.C=0.0115 MW  , ∆QO.C=0.0504 MVAR.

In table (3.1) all the information needed to select the transformers of network #1

| Transformer | Sload (MVA) | S nom (MVA) | Standard S (MVA) | Type of transformer | VH\VL (KV) | RT(Ω) | XT(Ω) | PO.C (MW) | QO.C (MVAR) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| A | 28.69 | 20.64 | 63 | 3-winding | VH=230 | RTH=1.4 | XTH=104 | 0.045 | 0.315 |
|  |  |  |  |  | VM=121 | RTM=1.4 | XTM=0 |  |  |
|  |  |  |  |  | VL=O.C | RTL=2.8 | XTL=195.6 |  |  |
| 1 | 25.6 | 18.29 | 40 | 2-winding | 230\6.6 | 5.6 | 158.7 | 0.005 | 0.36 |
| 2 | 28.69 | 20.642 | 25 | 2-winding | 115\6.5 | 2.54 | 55.9 | 0.027 | 0.175 |
| 3 | 48.619 | 34.727 | 63 | 3-winding | VH=230 | RTH=1.4 | XTH=104 | 0.045 | 0.315 |
|  |  |  |  |  | VM=121 | RTM=1.4 | XTM=0 |  |  |
|  |  |  |  |  | VL=6.6 | RTL=2.8 | XTL=195.6 |  |  |
| 4 | 10.73 | 7.664 | 10 | 2-winding | 115\6.6 | 7.95 | 139 | 0.014 | 0.07 |
| 5 | 13.95 | 9.964 | 10 | 2-winding | 115\6.6 | 7.95 | 139 | 0.014 | 0.07 |
| 6 | 6.58 | 4.664 | 6.3 | 2-winding | 115\6.6 | 14.7 | 220.4 | 0.0115 | 0.0504 |

Table (3.1)

In table (3.2) all the information needed to select the transformers of network #4

| Transformer | Sload (MVA) | S nom (MVA) | Standard S (MVA) | Type of transformer | VH\VL (KV) | RT(Ω) | XT(Ω) | PO.C (MW) | QO.C (MVAR) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | 53.72 | 38.37 | 63 | 3-winding | VH=230 | RTH=1.4 | XTH=104 | 0.005 | 0.36 |
|  |  |  |  |  | VM=121 | RTM=1.4 | XTM=0 |  |  |
|  |  |  |  |  | VL=6.6 | RTL=2.8 | XTL=195.6 |  |  |
| 2 | 115.19 | 82.28 | 125 | 3-winding | VH=230 | RTH=0.5 | XTH=48.6 | 0.085 | 0.625 |
|  |  |  |  |  | VM=121 | RTM=0,5 | XTM=0 |  |  |
|  |  |  |  |  | VL=6.6 | RTL=1.0 | XTL=82.8 |  |  |
| 3 | 17.38 | 12.41 | 16 | 2-winding | 115\6.6 | 4.38 | 86.7 | 0.019 | 0.112 |
| 4 | 10.73 | 7.664 | 10 | 2-winding | 115\6.6 | 7.95 | 139 | 0.014 | 0.07 |
| 5 | 13.95 | 9.964 | 10 | 2-winding | 115\6.6 | 7.95 | 139 | 0.014 | 0.07 |
| 6 | 6.58 | 4.664 | 6.3 | 2-winding | 115\6.6 | 14.7 | 220.4 | 0.0115 | 0.0504 |

Table (3.2)

In table (3.3) all the information needed to select the transformers of network #8

| Transformer | Sload (MVA) | S nom (MVA) | Standard S (MVA) | Type of transformer | VH\VL (KV) | RT(Ω) | XT(Ω) | PO.C (MW) | QO.C (MVAR) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | 58.6 | 41.85 | 63 | 3-winding | VH=230 | RTH=1.4 | XTH=104 | 0.005 | 0.36 |
|  |  |  |  |  | VM=121 | RTM=1.4 | XTM=0 |  |  |
|  |  |  |  |  | VL=6.6 | RTL=2.8 | XTL=195.6 |  |  |
| 2 | 49.13 | 35.098 | 63 | 3-winding | VH=230 | RTH=0.5 | XTH=48.6 | 0.085 | 0.625 |
|  |  |  |  |  | VM=121 | RTM=0,5 | XTM=0 |  |  |
|  |  |  |  |  | VL=6.6 | RTL=1.0 | XTL=82.8 |  |  |
| 3 | 17.38 | 24.82 | 25 | 2-winding | 115\6.5 | 2.54 | 55.9 | 0.027 | 0.175 |
| 4 | 10.73 | 15.328 | 16 | 2-winding | 115\6.5 | 4.38 | 86.7 | 0.019 | 0.112 |
| 5 | 13.95 | 9.964 | 10 | 2-winding | 115\6.6 | 7.95 | 139 | 0.014 | 0.07 |
| 6 | 6.58 | 4.664 | 6.3 | 2-winding | 115\6.6 | 14.7 | 220.4 | 0.0115 | 0.0504 |

Table (3.3)

In table (3.4) all the information needed to select the transformers of network #9

| Transformer | Sload (MVA) | S nom (MVA) | Standard S (MVA) | Type of transformer | VH\VL (KV) | RT(Ω) | XT(Ω) | PO.C (MW) | QO.C (MVAR) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | 25.6 | 36.57 | 40 | 2-winding | 115\6.3 | 1.40 | 34.7 | 0.036 | 0.26 |
| 2 | 118.83 | 84.88 | 125 | 3-winding | VH=230 | RTH=0.5 | XTH=48.6 | 0.085 | 0.625 |
|  |  |  |  |  | VM=121 | RTM=0.5 | XTM=0 |  |  |
|  |  |  |  |  | VL=6.6 | RTL=1.0 | XTL=82.8 |  |  |
| 3 | 63.2 | 45.08 | 63 | 3-winding | VH=230 | RTH=1.4 | XTH=195.6 | 0.045 | 0.315 |
|  |  |  |  |  | VM=121 | RTM=1.4 | XTM=0 |  |  |
|  |  |  |  |  | VL=6.6 | RTL=2.8 | XTL=104 |  |  |
| 4 | 10.73 | 15.328 | 16 | 2-winding | 115\6.6 | 4.38 | 86.7 | 0.019 | 0.112 |
| 5 | 13.95 | 9.964 | 10 | 2-winding | 115\6.6 | 7.95 | 139 | 0.014 | 0.07 |
| 6 | 6.58 | 4.664 | 6.3 | 2-winding | 115\6.6 | 14.7 | 220.4 | 0.0115 | 0.0504 |

Table (3.4)

The following table shows the rated apparent power of transformers in each network and the total apparent in each network.

| Network bus | 1 | 4 | 8 | 9 |
| --- | --- | --- | --- | --- |
| 1 | 40 | 63 | 63 | 40 |
| 2 | 25 | 125 | 63 | 125 |
| 3 | 63 | 16 | 25 | 16 |
| 4 | 10 | 10 | 16 | 16 |
| 5 | 10 | 10 | 10 | 10 |
| 6 | 6.3 | 6.3 | 6.3 | 6.3 |
| total | 154.3 | 230.3 | 183.3 | 213.3 |

## 3.2- selection of transmission lines:-

In this section we will calculate the cross section of the conductors that will carry the power from the power sours to the substation, and the conductors that we will use is an Aluminum conductors because of its advantage on the other conductors. The type of the Aluminum being used is ACSR(Aluminum conductor steel reinforced), and all the conductors are overhead T.L.

Selection of transmission lines depends on the current flows in it, and we select the cross sectional area of the T.L. and we will use tables to determine the T.L, and we will find the current flow using this equation:

Inom= appearnt power calculated 3 V

But we should take in consideration the current that flows after the fault. Because when the fault occurs one of the lines will be off so the current will flow in the other line so

Imax T.L= Inom

I worst case= Imax T.L= Inom  * 2

And to insure that the corona losses will be minimum, we will take the minimum cross sectional for the T.L with 110 KV is 70 mm2 , and for 220 KV is 240 mm2.

And from the tables we will get the total resistances, total inductive reactance and total capacitive reactance.

And we will take in consideration the double line that will make the resistance and the inductance half and the capacitance the double.

Now we will start with network #1 .

**Branch A-1

Inom= 74.4 3 220 = 195.2 A

I worst case = Imax T.L= Inom  * 2=195.5*2=390.5

From the table the cross section area will be 240 mm2.

From tables R0=6.05 Ω , X0=21.75 , Y0=5.2 *10-4 (S).

**Branch A-2

Inom= 28.693 110 = 150.58 A

I worst case = Imax T.L= Inom  * 2=150.58*2=301A

From the table the cross section area will be 95 mm2.

From tables R0=15.3 Ω , X0=21.75 , Y0=5.22 *10-4 (S).

**Branch 1-3

Inom= 48.6193 220 = 127.59 A

I worst case = Imax T.L= Inom  * 2=127.59*2=255.1 A

From the table the cross section area will be 240 mm2.

From tables R0=6.05 Ω , X0=21.75 , Y0=5.2 *10-4 (S).

**Branch 3-4

Inom= 10.72 3 110 = 56.3 A

I worst case = Imax T.L= Inom  * 2=56.3*2=112.6

From the table the cross section area will be 70 mm2.

From tables R0=21.4 Ω , X0=22.2 , Y0=5.1 *10-4 (S).

**Branch 3-5

Inom= 20.5 3 110 = 107.69 A

I worst case = Imax T.L= Inom  * 2=107.69*2=215 A

From the table the cross section area will be 70 mm2.

From tables R0=21.4 Ω , X0=22.2 , Y0=5.1 *10-4 (S).

**Branch 5-6

Inom= 6.583 110 = 34.5 A

I worst case = Imax T.L= Inom  * 2=34.5*2=69.07

From the table the cross section area will be 70 mm2.

From tables R0=21.4 Ω , X0=22.2 , Y0=5.1 *10-4 (S).

In table (3.5a) illustration of the pervious results

| Branch | Distance(KM) | Vnom (kV) | Inom(A) | I worst case (A) | Cross section (mm2) |
| --- | --- | --- | --- | --- | --- |
| A-1 | 75 | 220 | 195.2 | 390.5 | 240 |
| A-2 | 65 | 110 | 150.58 | 301 | 95 |
| 1-3 | 20 | 220 | 127.59 | 255.1 | 240 |
| 3-4 | 30 | 110 | 56.3 | 112.6 | 70 |
| 3-5 | 30 | 110 | 107.69 | 215 | 70 |
| 5-6 | 20 | 110 | 34.5 | 69.07 | 70 |

Table (3.5a)

In table (3.5b) shows the resistance, inductance and capacitance

| Branch | Cross section (mm2) | R0(Ω) | X0(Ω) | Y0(S) |
| --- | --- | --- | --- | --- |
| A-1 | 240 | 6.05 | 21.75 | 5.2 *10-4 |
| A-2 | 95 | 15.3 | 21.7 | 5.22 *10-4 |
| 1-3 | 240 | 6.05 | 21.75 | 5.2 *10-4 |
| 3-4 | 70 | 21.4 | 22.2 | 5.1*10-4 |
| 3-5 | 70 | 21.4 | 22.2 | 5.1 *10-4 |
| 5-6 | 70 | 21.4 | 22.2 | 5.1 *10-4 |

Table (3.5b)

The following tables for network #4 (table 3.6a)

| Branch | Distance(KM) | Vnom (kV) | Inom(A) | I worst case (A) | Cross section (mm2) |
| --- | --- | --- | --- | --- | --- |
| A-2 | 65 | 220 | 269.83 | 539.66 | 300 |
| 2-1 | 40 | 220 | 140.9 | 281.95 | 240 |
| 1-3 | 20 | 110 | 147.5 | 295.04 | 95 |
| 3-4 | 30 | 110 | 56.3 | 112.6 | 70 |
| 2-5 | 30 | 110 | 107.69 | 215.38 | 70 |
| 5-6 | 20 | 110 | 34.5 | 69.07 | 70 |

Table (3.6a)

In table (3.6b) shows the resistance, inductance and capacitance

| Branch | Cross section (mm2) | R0(Ω) | X0(Ω) | Y0(S) |
| --- | --- | --- | --- | --- |
| A-2 | 300 | 4.9 | 21.45 | 5.28 *10-4 |
| 2-1 | 240 | 6.05 | 21.75 | 5.2 *10-4 |
| 1-3 | 95 | 15.3 | 21.7 | 5.22 *10-4 |
| 3-4 | 70 | 21.4 | 22.2 | 5.1*10-4 |
| 2-5 | 70 | 21.4 | 22.2 | 5.1 *10-4 |
| 5-6 | 70 | 21.4 | 22.2 | 5.1 *10-4 |

Table (3.6b)

The following tables for network #8 (table 3.7a)

| Branch | Distance(KM) | Vnom (kV) | Inom(A) | I worst case (A) | Cross section (mm2) |
| --- | --- | --- | --- | --- | --- |
| A-1 | 75 | 220 | 244.1 | 288.32 | 240 |
| A-2 | 65 | 220 | 199.97 | 400 | 240 |
| 1-4 | 25 | 110 | Imax fault=113.85 | 113.85 | 70 |
| 1-3 | 20 |  |  |  |  |
| 3-4 | 30 |  |  |  |  |
| 2-5 | 30 | 110 | 145.2 | 284 | 95 |
| 5-6 | 20 | 110 | 34.5 | 69.07 | 70 |

Table (3.7a)

In table (3.7b) shows the resistance, inductance and capacitance

| Branch | Cross section (mm2) | R0(Ω) | X0(Ω) | Y0(S) |
| --- | --- | --- | --- | --- |
| A-1 | 240 | 6.05 | 21.75 | 5.2 *10-4 |
| A-2 | 240 | 6.05 | 21.75 | 5.2 *10-4 |
| 1-4 | 70 | 21.4 | 22.2 | 5.1*10-4 |
| 1-3 |  |  |  |  |
| 3-4 |  |  |  |  |
| 2-5 | 95 | 15.3 | 21.7 | 5.22 *10-4 |
| 5-6 | 70 | 21.4 | 22.2 | 5.1*10-4 |

Table (3.7b)

The following tables for network #9 (table 3.8a)

| Branch | Distance(KM) | Vnom (kV) | Inom(A) | I worst case (A) | Cross section (mm2) |
| --- | --- | --- | --- | --- | --- |
| A-2 | 65 | 220 | 311.85 | 623.7 | 300 |
| 2-3 | 30 | 220 | 63.122 | 165.65 | 240 |
| 4-1 | 25 | 110 | Imax fault=171.17 | 171.17 | 70 |
| 3-1 | 20 |  |  |  |  |
| 3-4 | 30 |  |  |  |  |
| 2-5 | 30 | 110 | 145.2 | 284 | 95 |
| 5-6 | 20 | 110 | 34.5 | 69.07 | 70 |

Table (3.8a)

In table (3.8b) shows the resistance, inductance and capacitance

| Branch | Cross section (mm2) | R0(Ω) | X0(Ω) | Y0(S) |
| --- | --- | --- | --- | --- |
| A-2 | 300 | 4.9 | 21.45 | 5.28 *10-4 |
| 2-3 | 240 | 6.05 | 21.75 | 5.2 *10-4 |
| 4-1 | 70 | 21.4 | 22.2 | 5.1*10-4 |
| 3-1 |  |  |  |  |
| 3-4 |  |  |  |  |
| 2-5 | 95 | 15.3 | 21.7 | 5.22 *10-4 |
| 5-6 | 70 | 21.4 | 22.2 | 5.1*10-4 |

Table (3.8b)

## 3.3. Selection of Switch gear:-

The switch gears are located at the load buses and contain:

- Circuit breakers and isolators.

- Bus bars.

- Transformers.

Choosing the switch gear depend on several factors such as operating voltage, number of lines that can be connected through the S.G and the possibility to link other lines in the future, and in the location of the S.G in the network.

Selection of S.G. for network #1.

** Switch gear at bus #1:

This bus operates at 220 kv and it's transformers convert to 6.6 kv, and the number of lines connected to the bus is 4 lines, depending in the previous conditions the suitable S.G is #11 it operates at 220\110 and the number of lines can be connected is >4.

**Switch gear at bus#2:

This bus operates at 110 kv and it's in the end of the line, and the S.G that used in the end of the network is # 4.

**Switch gear at bus#3:

This bus contain a 3-winding transformer, in the high tension side we need a 2 line switch gear to change from (220-6.6)kv, so we chose S.G #5

And for the medium tension we need a 4 lines S.G so we chose S.G # 11

**Switch gear at bus#4:

This bus operates at 110 kv and it's in the end of the line, and the S.G that used in the end of the network is # 4.

**Switch gear at bus#5:

This bus operates at 110 kv and we have a 4 lines connected to it so we chose S.G #11.

**Switch gear at bus#4:

This bus operates at 110 kv and it's in the end of the line, and the S.G that used in the end of the network is # 4.

In the same way we chose the switch gears for the other networks and this tables shows the S.G that used in the other networks.

Table (3.9) Network #1

| The bus | Operating voltage | # of S.G |
| --- | --- | --- |
| 1 | 220 | 11 |
| 2 | 110 | 4 |
| 3 | H.T 220 M.T 110 | 5 |
|  |  | 11 |
| 4 | 110 | 4 |
| 5 | 110 | 11 |
| 6 | 110 | 4 |

Table (3.9)

Table (3.10) Network #4

| The bus | Operating voltage | # of S.G |
| --- | --- | --- |
| 1 | H.T 220 | 5 |
|  | M.T 110 | 5 |
| 2 | H.T 220 | 11 |
|  | M.T 110 | 5 |
| 3 | 110 | 11 |
| 4 | 110 | 4 |
| 5 | 110 | 11 |
| 6 | 110 | 4 |

Table (3.10)

Table (3.11) Network #8

| The bus | Operating voltage | # of S.G |
| --- | --- | --- |
| 1 | H.T 220 | 5 |
|  | M.T 110 | 5 |
| 2 | H.T 220 | 5 |
|  | M.T 110 | 5 |
| 3 | 110 | 5 |
| 4 | 110 | 5 |
| 5 | 110 | 11 |
| 6 | 110 | 4 |

Table (3.11)

Table (3.12) Network #9

| The bus | Operating voltage | # of S.G |
| --- | --- | --- |
| 1 | 110 | 5 |
| 2 | H.T 220 | 11 |
|  | M.T 110 | 5 |
| 3 | H.T 220 | 5 |
|  | M.T 110 | 5 |
| 4 | 110 | 5 |
| 5 | 110 | 11 |
| 6 | 110 | 4 |

Table (3.12)

## 3.4. The economical study:

After we select the component of the network we are going to study these networks from economic point of view, in this situation the study will take to parts:

- The capital cost: This paid when creating the network, including the cost of transformers, T.L, switch gear and measuring equipment.

- The running cost: which paid continuously, that includes the maintenance and the losses in the network.

And to calculate the capital and running cost we will use this equation:

Z= EN*K + I

Where:

Z: expenses per year in Ruble \year

K: the capital cost in Ruble

En: Depreciation factor = 0.2

I: operational and maintenance cost per year .

In this project we will use the Ruble because we use a Russian reference.

For the first network we will discuss in detail.

### 3.4.1: Capital cost

Calculation of network # 1

- Cost of the transmission lines :

The cost of transmission lines per KM depends on :

- The voltage at which the line operates.

- The cross sectional area of the conductors.

- Number of lines being connected.

Table (3.13) showing the calculation of transmission lines in network #1.

| Branch | Length (KM) | Voltage (KV) | Cross-sectional area (mm2) | Cost \KM (103*Ruble) | Total cost (103*Ruble) |
| --- | --- | --- | --- | --- | --- |
| A-1 | 150 | 220 | 240 | 27.8 | 4170 |
| A-2 | 130 | 110 | 95 | 16.9 | 2197 |
| 1-3 | 40 | 220 | 240 | 27.8 | 1112 |
| 3-4 | 60 | 110 | 70 | 15.8 | 948 |
| 3-5 | 60 | 110 | 70 | 15.8 | 948 |
| 5-6 | 40 | 110 | 70 | 15.8 | 632 |
| TOTAL |  |  |  |  | 10,007 |

Table (3.13)

From the table we can see that the total cost of the T.L at network #1 equal to:

KT.L=10,007 *103 Ruble

- Cost of the transformers:

The cost of transformers depends on :

- The rated power of the transformer.

- The voltage of the transformer should operate.

Table (3.14) shows the calculation of the transmission lines at network #1.

| Load Bus | Number of T.Rs | S nom (MVA) | voltage | Cost \T.R (103*Ruble) | Total cost (103*Ruble) |
| --- | --- | --- | --- | --- | --- |
| 1 | 2 | 40 | 220 | 169 | 338 |
| 2 | 2 | 25 | 110 | 66 | 132 |
| 3 | 2 | 63 | 220 | 159 | 318 |
| 4 | 2 | 10 | 110 | 54 | 108 |
| 5 | 2 | 10 | 110 | 54 | 108 |
| 6 | 2 | 6.3 | 110 | 49 | 98 |
| A | 2 | 63 | 220 | 159 | 318 |
| Total |  |  |  |  | 1420 |

Table (3.14)

Later, for the calculation we need to separate the cost of the T.R in two parts, one in 220 KV and the other on 110 KV.

The cost of T.R that operate at 220 KV:

KT.R(220KV)=338+318+318 =974* 103  Ruble

The cost of the T.R that operate at 110KV:

KT.R(110KV)=132+108+108+98 =446* 103  Ruble.

The total cost will be KT.R=1420 * 103  Ruble.

- The cost of the switch gear and the auxiliary requirements :

Both of S.G and the auxiliary requirement depends on the S.G being used on the bus and on the voltage at which the S.G operates.

The cost of the auxiliary requirements includes the cost of lighting, control, measuring instruments, land and building, communication devices and others.

Table (3.15) shows the cost of S.G and the auxiliary requirements.

| Bus # | Switchgear # | Voltage (KV) | Cost of S.G(103*Ruble) | K constant |
| --- | --- | --- | --- | --- |
| 1 | #11 | 220 | 595 | - |
| 2 | #4 | 110 | 36.3 | 130 |
| 3 | #5 at H.T | 220 | 180 | 520 |
|  | # 11 at M.T | 110 | 294 | 290 |
| 4 | #4 | 110 | 36.3 | 130 |
| 5 | #11 | 110 | 294 | 290 |
| 6 | #4 | 110 | 36.3 | 130 |
| Total |  |  | 1471.9 | 1490 |

Table (3.15)

Now for the purpose of calculation we separate the cost of the H.T from the M.T

The cost of S.G that operate at 220 KV:

KS.G(220KV)=595+180 =775* 103  Ruble.

The cost of the S.G that operate at 110KV:

KS.G(110KV)=36.3+294+36.3+294+36.3 =696.9* 103  Ruble.

The cost of auxiliary requirements that operate at 220 KV:

K K.Constant(220KV)= 520* 103  Ruble.

The cost of auxiliary requirements that operate at 110 KV:

K K.Constant(110KV)=970 * 103  Ruble.

Now the total cost of the substation will be the sum of the transformers, S.G and the K constant in the H.T and in M.T

K Sub(220KV)=KS.G+KT.R+KK CONSTANT

K Sub(220KV)= 775+520 +974 =2269* 103  Ruble.

K Sub(110KV)=KS.G+KT.R+KK CONSTANT

K Sub(110KV)= 446+696.9+970 =2112.9* 103  Ruble.

Now the total substation cost will equal the sum of K Sub(220KV) and

K Sub(110KV).

- Ksub  = K Sub(220KV) +K Sub(110KV)

Ksub= 2269+2112.9 =4381.9 * 103  Ruble.

The capital cost will be:

K = KSUB + KT.L

K=4381.9 +10007 =14388.9 * 103  Ruble.

### 3.4.2: Running cost

This cost contains the prices which must be paid continuously for the operation and maintenance on the different parts of the network; this will be calculated as a fraction of the capital cost, also this cost contains the losses in the T.L and T.R.

So the cost will be calculated as in the following equation:

I = IT.L + I SUB + I ∆w .

Where:

I : Operational and maintenance cost .

IT.L : cost of the maintenance of T.L.

I SUB: cost of maintenance of substation.

I ∆w : cost of losses per year.

It's found that running cost of the T.L that include maintenance and operation is 2.8% from the capital cost of the T.L. and for the substation it's found that  running cost of the H.T (220 KV) side  is 7.8% and for the M.T (110 KV) side is 8.8 % . So the previous relation can be written as :

I = (n* KT.L) + (m*K sub)+ Z losses.

Where:

n:maintenance factor for the T.L.

m: maintenance factor for the substation.

K T.L: capital cost of T.L.

K sub: capital cost of substation.

Z losses: the total losses per year.

Z losses stands for the cost of energy losses in transmission and transformers, which is the energy lost multiplied by the cost of 1 MWH.

- Z losses= z L * (∆W1 +∆W2)

z L = 160 Ruble \ MWH .

Where:

∆W1: variable losses dependent on the load in MWH.

∆W2: constant losses independent on the load in MWH.

∆W2 occur in the excitation branch of the transformers so:

∆W2= T *∆P O.C

Where:

T:  total time for operating which is equal to 8760 hours.

∆ P O.C : losses in excitation branch of the transformer in MW.

∆W1: the variable losses dependant in losses in the T.L and the T.R that we can get it from this equation:

∆W1= Ʈ ( ∆PT.L + ∆P T.R)

Where:

Ʈ: is the time factor which depends on Tmax that we can get from this equation. Ʈ=(0.124 + Tmax*10-4 ) *8760 ,where Tmax her equal 4000 H.

∆PT.L: power losses in the transmission lines which we can get from this equation.

∆PT.L=P2+ Q2V2* R where:

P: real power to be transmitted through the T.L.

Q: reactive power to be transmitted through the T.L.

V: voltage at the end of the line where P and Q

R: resistance of line in Ω.

∆PT.R: power losses occur in the transformer which we can get from this equation.

∆PT.R=P2+Q2V2 RH   where:

P: real power flowing through the transformer.

Q: reactive power flowing through the transformer.

V: the voltage at the high tension of the T.R.

RH: equivalent resistance of the T.R refers to H.T.

From the previous equation for the power losses in the T.L. we obtain table (3.16):

| Branches | Voltage (KV) | P+jQ (MVA) | R (Ω) | ∆PT.L(MW) |
| --- | --- | --- | --- | --- |
| A-1 | 220 | 70.54+j23.66 | 6.05 | 0.6916 |
| A-2 | 110 | 26.6+j10.75 | 15.3 | 0.898 |
| 1-3 | 220 | 46.54+j14.066 | 6.05 | 0.297 |
| 3-4 | 110 | 10.2+j3.32 | 21.4 | 0.203 |
| 3-5 | 110 | 19.74+j5.596 | 21.4 | 0.7445 |
| 5-6 | 110 | 6.24+j2.076 | 21.4 | 0.076 |
| Total |  |  |  | 2.9101 |

Table (3.16)

And from previous equations for the power loss in the T.R. we obtain table (3.17):

| Transformer # | Voltage (KV) | P+jQ (MVA) | R(Ω) | ∆PT.R(MW) | P O.C(MW) |
| --- | --- | --- | --- | --- | --- |
| A | 220 | 26.6+j10,75 | 2.54 | 0.0431 | 0.027 |
| 1 | 220 | 70.54+j23.66 | 5.6 | 0.64 | 0.05 |
| 2 | 110 | 26.6+j10.75 | 2.54 | 0.172 | 0.027 |
| 3 | 220 | 46.54+j14.066 | 1.4 | 0.068 | 0.045 |
|  | 220 | 29.94+j2.916 | 1.4 | 0.026 | - |
|  | 220 | 16.6+j5.15 | 2.8 | 0.175 | - |
| 4 | 110 | 10.2+j3.32 | 7.95 | 0.0755 | 0.014 |
| 5 | 110 | 19.74+j5.596 | 7.95 | 0.276 | 0.014 |
| 6 | 110 | 6.24+j2.076 | 14.7 | 0.052 | 0.0115 |
| Total |  |  |  | 1.5276 | 0.1885 |

Table (3.17)

After we found these tables we are going to use the equation we show previously starting with Ʈ.

Ʈ=(0.124 + Tmax*10-4) *8760 ,taking Tmax = 4000 hours

Ʈ = 2405 hours

After we found Ʈ we can find ∆W1 which is equal to:

∆W1= Ʈ ( ∆PT.L + ∆P T.R)

= 2405 (2.9101 + 1.5276) = 10,668.23 MW

After that we find ∆W2 which is equal to:

∆W2 = T *∆P O.C

= 8760 *0.1885 = 1651.26 MW.

After we found ∆W1 and ∆W2 we can found the cost of the energy loss which is equal to Z losses= z L * (∆W1 +∆W2)

Z losses= 160 *(10,668.23 + 1651.26) = 1,971.12 * 103  Ruble

Now we will find the running cost which is equal to:

I = (n* KT.L) + (m*K sub) + Z losses.

I = (2.8% * 10007) + (7.8% *2269) + (8.8% * 2112.9) + 1971

I = 280.196 + 176.982 +185.9352 + 3262.9 = 2614.2 * 103   Ruble.

After founding the running cost now we will find the total cost which is equal to:

Z= EN*K + I

Z= (0.2 *14388.9) + 2614.2 = 5492*103   Ruble.

Calculation of the cost for network # 4

- The capital cost

- Costs of transmission lines:

Table (3.18) shows the cost of the T.L

| Branch | Length (KM) | Voltage (KV) | Cross-sectional area (mm2) | Cost \KM (103*Ruble) | Total cost (103*Ruble) |
| --- | --- | --- | --- | --- | --- |
| A-2 | 130 | 220 | 300 | 30 | 3900 |
| 1-2 | 80 | 220 | 240 | 27.8 | 2224 |
| 2-5 | 60 | 110 | 95 | 16.9 | 1014 |
| 1-3 | 40 | 110 | 70 | 15.8 | 632 |
| 3-4 | 60 | 110 | 70 | 15.8 | 948 |
| 5-6 | 40 | 110 | 70 | 15.8 | 632 |
| TOTAL |  |  |  |  | 9350 |

Table (3.18)

- The cost of the transformers:

Table (3.19) shows the cost of the transformers

| Load Bus | Number of T.Rs | Snom (MVA) | voltage | Cost \T.R (103*Ruble) | Total cost (103*Ruble) |
| --- | --- | --- | --- | --- | --- |
| 1 | 2 | 63 | 220 | 201 | 402 |
| 2 | 2 | 125 | 220 | 253 | 506 |
| 3 | 2 | 16 | 110 | 63 | 126 |
| 4 | 2 | 10 | 110 | 54 | 108 |
| 5 | 2 | 10 | 110 | 54 | 108 |
| 6 | 2 | 6.3 | 110 | 49 | 98 |
| Total | 14 |  |  |  | 1348 |

Table (3.19)

The cost of T.R that operate at 220 KV:

KT.R(220KV)= 908* 103  Ruble

The cost of the T.R that operate at 110KV:

KT.R(110KV)=440* 103  Ruble.

The total cost will be KT.R=1348 * 103  Ruble.

- The cost of the switch gear and the auxiliary requirements :

Table (3.20) shows the cost of S.G and the auxiliary requirements.

| Bus # | Switchgear # | Voltage (KV) | Cost of S.G(103*Ruble) | K constant |
| --- | --- | --- | --- | --- |
| 1 | # 5 at H.T | 220 | 180 | 520 |
|  | #5 at M.T | 110 | 75 | 210 |
| 2 | # 11 at H.T | 220 | 595 | 750 |
|  | #5 at M.T | 110 | 75 | 210 |
| 3 | # 11 | 110 | 294 | 290 |
| 4 | #4 | 110 | 36.3 | 130 |
| 5 | #11 | 110 | 294 | 290 |
| 6 | #4 | 110 | 36.3 | 130 |
| Total |  |  | 1585.6 | 2400 |

Table (3.20)

The cost of S.G that operate at 220 KV:

KS.G(220KV)= 775* 103  Ruble.

The cost of the S.G that operate at 110KV:

KS.G(110KV)=774.3* 103  Ruble.

The cost of auxiliary requirements that operate at 220 KV:

K K.Constant(220KV)=1270* 103  Ruble.

The cost of auxiliary requirements that operate at 110 KV:

K K.Constant(110KV)=1130 * 103  Ruble.

Now the total cost of the substation will be the sum of the transformers, S.G and the K constant in the H.T and in M.T

K Sub(220KV)=KS.G+KT.R+KK CONSTANT

K Sub(220KV)= 775+908+1270 =2953* 103  Ruble.

K Sub(110KV)=KS.G+KT.R+KK CONSTANT

K Sub(110KV)= 774.3+440+1130 =2344.3* 103  Ruble.

Now the total substation cost will equal the sum of K Sub(220KV) and

K Sub(110KV).

- Ksub  = K Sub(220KV) +K Sub(110KV)

Ksub= 2953+2344.3 =5297.3 * 103   Ruble.

The capital cost will be:

K = KSUB + KT.L

K=5297.3 +9350 =14647.3 * 103    Ruble.

- The running cost

- Losses in the transmission lines:

Table (3.21)shows the losses in the T.L

| Branches | Voltage (KV) | P+jQ (MVA) | R (Ω) | ∆PT.L(MW) |
| --- | --- | --- | --- | --- |
| A-2 | 220 | 97.1+j33.816 | 4.9 | 1.07 |
| 2-1 | 220 | 50.8+j17.47 | 6.05 | 0.36 |
| 2-5 | 110 | 19.74+j5.596 | 21.4 | 0.744 |
| 1-3 | 110 | 26.8+j8.47 | 15.3 | 0.998 |
| 3-4 | 110 | 10.2+j3.32 | 21.4 | 0.203 |
| 5-6 | 110 | 6.24+j2.076 | 21.4 | 0.082 |
| Total |  |  |  | 3.457 |

Table (3.21)

- Losses in the transformers  shown in table (3.22):

| Transformer # | Voltage (KV) | P+jQ (MVA) | R(Ω) | ∆PT.R(MW) | P O.C(MW) |
| --- | --- | --- | --- | --- | --- |
| 1 | 220 | 50.8+j17.47 | 1.4 | 0.083 | 0.045 |
|  | 220 | 26.8+j8.47 | 1.4 | 0.0228 | - |
|  | 220 | 24+j9 | 2.8 | 0.038 | - |
| 2 | 220 | 97.1+j55.816 | 0.5 | 0.109 | 0.085 |
|  | 220 | 70.5+j23.066 | 0.5 | 0.056 | - |
|  | 220 | 26.6+j10.75 | 1 | 0.17 | - |
| 3 | 110 | 26.8+j8.47 | 4.38 | 0.279 | 0.019 |
| 4 | 110 | 10.2+j3.32 | 7.95 | 0.0755 | 0.014 |
| 5 | 110 | 19.74+j5.596 | 7.95 | 0.276 | 0.014 |
| 6 | 110 | 6.24+j2.076 | 14.7 | 0.052 | 0.0115 |
| Total |  |  |  | 1.1613 | 0.1885 |

Table (3.22)

From previous Ʈ equal to 2405   then  we can find ∆W1 which is equal to:

∆W1= Ʈ ( ∆PT.L + ∆P T.R)

= 2405(3.457 + 1.1613) = 11,107 MW

After that we find ∆W2 which is equal to:

∆W2 = T *∆P O.C

= 8760 *0.1885 = 1651.26 MW.

After we found ∆W1 and ∆W2 we can found the cost of the energy loss which is equal to  Z losses= z L * (∆W1 +∆W2)

Z losses= 160 *(11,107 + 1651.26) = 2,041.3 * 103  Ruble

Now we will find the running cost which is equal to:

I = (n* KT.L) + (m*K sub)+ Z losses.

I = (2.8% * 9350) +(7.8% *2953 )+(8.8% * 2344.3)+ 2,041.3

I = 261.8+ 230.334 +206.298 + 2,041.3 = 2739.7 * 103   Ruble.

After founding the running cost now we will find the total cost which is equal to:

Z= EN*K + I

Z= (0.2 * 14647.3) + 2739.7 = 5669.2 *103   Ruble

Calculation of the cost for network # 8

- The capital cost

- Costs of transmission lines:

Table (3.23) shows the cost of the T.L

| Branch | Length (KM) | Voltage (KV) | Cross-sectional area (mm2) | Cost \KM (103*Ruble) | Total cost (103*Ruble) |
| --- | --- | --- | --- | --- | --- |
| A-1 | 150 | 220 | 240 | 27.8 | 4170 |
| A-2 | 130 | 220 | 240 | 27.8 | 3614 |
| 1-3 | 20 | 110 | 70 | 10.5 | 210 |
| 1-4 | 25 | 110 | 70 | 10.5 | 262.5 |
| 3-4 | 30 | 110 | 70 | 10.5 | 315 |
| 2-5 | 60 | 110 | 95 | 16.9 | 1014 |
| 5-6 | 40 | 110 | 70 | 15.8 | 632 |
| TOTAL |  |  |  |  | 10217.5 |

Table (3.23)

- The cost of the transformers:

Table (3.24) shows the cost of the transformers

| Load Bus | Number of T.Rs | Snom (MVA) | voltage | Cost \T.R (103*Ruble) | Total cost (103*Ruble) |
| --- | --- | --- | --- | --- | --- |
| 1 | 2 | 63 | 220 | 201 | 402 |
| 2 | 2 | 63 | 220 | 201 | 402 |
| 3 | 1 | 25 | 110 | 66 | 66 |
| 4 | 1 | 16 | 110 | 63 | 63 |
| 5 | 2 | 10 | 110 | 54 | 108 |
| 6 | 2 | 6.3 | 110 | 49 | 98 |
| Total |  |  |  |  | 1139 |

Table (3.24)

The cost of T.R that operate at 220 KV:

KT.R(220KV)= 804* 103  Ruble

The cost of the T.R that operate at 110KV:

KT.R(110KV)=335* 103  Ruble.

The total cost will be KT.R=1139 * 103  Ruble.

- The cost of the switch gear and the auxiliary requirements :

Table (3.25) shows the cost of S.G and the auxiliary requirements.

| Bus # | Switchgear # | Voltage (KV) | Cost of S.G(103*Ruble) | K constant |
| --- | --- | --- | --- | --- |
| 1 | # 5 at H.T | 220 | 180 | 520 |
|  | #5 at M.T | 110 | 75 | 210 |
| 2 | # 5 at H.T | 220 | 180 | 520 |
|  | #5 at M.T | 110 | 75 | 210 |
| 3 | # 5 | 110 | 75 | 210 |
| 4 | #5 | 110 | 75 | 210 |
| 5 | #11 | 110 | 294 | 290 |
| 6 | #4 | 110 | 36.3 | 130 |
| Total |  |  | 990.3 | 2300 |

Table (3.25)

The cost of S.G that operate at 220 KV:

KS.G(220KV)= 360* 103  Ruble.

The cost of the S.G that operate at 110KV:

KS.G(110KV)=630.3* 103  Ruble.

The cost of auxiliary requirements that operate at 220 KV:

K K.Constant(220KV)=1040* 103  Ruble.

The cost of auxiliary requirements that operate at 110 KV:

K K.Constant(110KV)=1260 * 103  Ruble.

Now the total cost of the substation will be the sum of the transformers, S.G and the K constant in the H.T and in M.T

K Sub(220KV)=KS.G+KT.R+KK CONSTANT

K Sub(220KV)= 360+804+1040 =2204* 103  Ruble.

K Sub(110KV)=KS.G+KT.R+KK CONSTANT

K Sub(110KV)= 630.3+335+1260 =2225.3* 103  Ruble.

Now the total substation cost will equal the sum of K Sub(220KV) and

K Sub(110KV).

- Ksub  = K Sub(220KV) +K Sub(110KV)

Ksub= 4429.3 * 103   Ruble.

The capital cost will be:

K = KSUB + KT.L

K=4429.3+10217.5 =14646.8 * 103    Ruble

- The running cost

- Losses in the transmission lines:

Table (3.26)shows the losses in the T.L

| Branches | Voltage (KV) | P+jQ (MVA) | R (Ω) | ∆PT.L(MW) |
| --- | --- | --- | --- | --- |
| A-1 | 220 | 55.145+j19.834 | 6.05 | 0.43 |
| A-2 | 220 | 46.34+j16.346 | 6.05 | 0.3 |
| 1-3 | 110 | 15.573+j7.34 | 42.8 | 1.04 |
| 1-4 | 110 | 11.226+j6.08 | 42.8 | 0.57 |
| 3-4 | 110 | 4.346+j1.25 | 42.8 | 0.07 |
| 2-5 | 110 | 19.74+j5.596 | 15.3 | 0.532 |
| 5-6 | 110 | 6.24+j2.076 | 21.4 | 0.076 |
| Total |  |  |  | 3.018 |

Table (3.26)

- Losses in the transformers shown in table (3.27) :

| Transformer # | Voltage (KV) | P+jQ (MVA) | R(Ω) | ∆PT.R(MW) | P O.C(MW) |
| --- | --- | --- | --- | --- | --- |
| 1 | 220 | 55.145+j19.83 | 1.4 | 0.0993 | 0.045 |
|  | 220 | 31.145+j10.83 | 1.4 | 0.0314 | - |
|  | 220 | 24+j9 | 2.8 | 0.038 | - |
| 2 | 220 | 46.34+j16.346 | 1.4 | 0.0698 | 0.045 |
|  | 220 | 20.26+j5.595 | 1.4 | 0.0128 | - |
|  | 220 | 26.6+j10.75 | 2.8 | 0.0476 | - |
| 3 | 110 | 19.919+j8.59 | 2.54 | 0.098 | 0.027 |
| 4 | 110 | 15.572+j7.33 | 4.38 | 0.107 | 0.019 |
| 5 | 110 | 19.74+j5.596 | 7.95 | 0.277 | 0.014 |
| 6 | 110 | 6.24+j2.076 | 14.7 | 0.0535 | 0.0115 |
| Total |  |  |  | 0.834 | 0.1615 |

Table (3.27)

From previous Ʈ equal to   then  we can find ∆W1 which is equal to:

∆W1= Ʈ ( ∆PT.L + ∆P T.R)

= 2405 (3.018 + 0.834) = 9264.1 MW

After that we find ∆W2 which is equal to:

∆W2 = T *∆P O.C

= 8760 *0.1615 = 1414.74 MW.

After we found ∆W1 and ∆W2 we can found the cost of the energy loss which is equal to  Z losses= z L * (∆W1 +∆W2)

Z losses= 160 *(9264.1 + 1414.72) =1708.6* 103  Ruble

Now we will find the running cost which is equal to:

I = (n* KT.L) + (m*K sub)+ Z losses.

I = (2.8% * 10217.5) +(7.8% *2204 )+(8.8% * 2225.3)+ 1708.6

I = 286.09+ 171.9 +195.8 + 1708.6= 2362.4 * 103   Ruble.

After founding the running cost now we will find the total cost which is equal to:

Z= EN*K + I

Z= (0.2 *14646.8) + 2362.4 = 5291.6 *103   Ruble.

Calculation of the cost for network # 9

- The capital cost

- Costs of transmission lines:

Table (3.28) shows the cost of the T.L

| Branch | Length (KM) | Voltage (KV) | Cross-sectional area (mm2) | Cost \KM (103*Ruble) | Total cost (103*Ruble) |
| --- | --- | --- | --- | --- | --- |
| A-2 | 130 | 220 | 300 | 30 | 3900 |
| 2-3 | 60 | 220 | 240 | 27.8 | 1668 |
| 2-5 | 60 | 110 | 95 | 16.9 | 1014 |
| 5-6 | 40 | 110 | 70 | 15.8 | 632 |
| 3-1 | 20 | 110 | 70 | 10.5 | 210 |
| 3-4 | 30 | 110 | 70 | 10.5 | 315 |
| 1-4 | 25 | 110 | 70 | 10.5 | 262.5 |
| TOTAL |  |  |  |  | 8001.5 |

Table (3.28)

- The cost of the transformers:

Table (3.29) shows the cost of the transformers

| Load Bus | Number of T.Rs | Snom (MVA) | voltage | Cost \T.R (103*Ruble) | Total cost (103*Ruble) |
| --- | --- | --- | --- | --- | --- |
| 1 | 1 | 40 | 110 | 88 | 88 |
| 2 | 2 | 125 | 220 | 200 | 400 |
| 3 | 2 | 63 | 220 | 193 | 386 |
| 4 | 1 | 16 | 110 | 63 | 63 |
| 5 | 2 | 10 | 110 | 54 | 108 |
| 6 | 2 | 6.3 | 110 | 49 | 98 |
| Total |  |  |  |  | 1143 |

Table (3.29)

The cost of T.R that operate at 220 KV:

KT.R(220KV)= 786* 103  Ruble

The cost of the T.R that operate at 110KV:

KT.R(110KV)=357* 103  Ruble.

The total cost will be KT.R=1143 * 103   Ruble.

- The cost of the switch gear and the auxiliary requirements :

Table (3.30) shows the cost of S.G and the auxiliary requirements.

| Bus # | Switchgear # | Voltage (KV) | Cost of S.G(103*Ruble) | K constant |
| --- | --- | --- | --- | --- |
| 1 | # 5 | 110 | 75 | 210 |
| 2 | #11 at H.T | 220 | 595 | 750 |
|  | # 5 at M.T | 110 | 75 | 210 |
| 3 | #5 at H.T | 220 | 180 | 520 |
|  | # 5 at M.T | 110 | 75 | 210 |
| 4 | #5 | 110 | 75 | 210 |
| 5 | #11 | 110 | 294 | 290 |
| 6 | #4 | 110 | 36.3 | 130 |
| Total |  |  | 1405.3 | 2530 |

Table (3.30)

The cost of S.G that operate at 220 KV:

KS.G(220KV)= 775* 103  Ruble.

The cost of the S.G that operate at 110KV:

KS.G(110KV)=630.3* 103  Ruble.

The cost of auxiliary requirements that operate at 220 KV:

K K.Constant(220KV)=1270* 103  Ruble.

The cost of auxiliary requirements that operate at 110 KV:

K K.Constant(110KV)=1260 * 103  Ruble.

Now the total cost of the substation will be the sum of the transformers, S.G and the K constant in the H.T and in M.T

K Sub(220KV)=KS.G+KT.R+KK CONSTANT

K Sub(220KV)= 2247.3* 103  Ruble.

K Sub(110KV)=KS.G+KT.R+KK CONSTANT

K Sub(110KV)= 2831* 103  Ruble.

Now the total substation cost will equal the sum of K Sub(220KV) and

K Sub(110KV).

- Ksub  = K Sub(220KV) +K Sub(110KV)

Ksub= 5078.3* 103   Ruble.

The capital cost will be:

K = KSUB + KT.L

K=5078.3+8001.5 =13079.8 * 103    Ruble

- The running cost

- Losses in the transmission lines:

Table (3.31)shows the losses in the T.L

| Branches | Voltage (KV) | P+jQ (MVA) | R (Ω) | ∆PT.L(MW) |
| --- | --- | --- | --- | --- |
| A-2 | 220 | 112.48+j38.332 | 4.9 | 1.42 |
| 2-3 | 220 | 59.9+j19.91 | 6.05 | 0.498 |
| 2-5 | 110 | 19.74+j5.596 | 15.3 | 0.533 |
| 5-6 | 110 | 6.24+j2.076 | 21.4 | 0.076 |
| 3-1 | 110 | 21.62+j7.38 | 42.8 | 1.84 |
| 3-4 | 110 | 12.52+j3.98 | 42.8 | 0.610 |
| 1-4 | 110 | 9.16+j3.4 | 42.8 | 0.337 |
| Total |  |  |  | 5.32 |

Table (3.31)

- Losses in the transformers shown in table (3.32) :

| Transformer # | Voltage (KV) | P+jQ (MVA) | R(Ω) | ∆PT.R(MW) | P O.C(MW) |
| --- | --- | --- | --- | --- | --- |
| 1 | 110 | 30.78+j10.78 | 1.4 | 0.123 | 0.036 |
| 2 | 220 | 112.48+j38.332 | 0.5 | 0.145 | 0.085 |
|  | 220 | 85.88+j27.588 | 0.5 | 0.084 | - |
|  | 220 | 26.6+j10.75 | 1 | 0.017 | - |
| 3 | 220 | 59.9+j19.91 | 1.4 | 0.115 | 0.045 |
|  | 220 | 43.3+j14.76 | 1.4 | 0.06 | - |
|  | 220 | 16.6+j5.15 | 2.8 | 0.017 | - |
| 4 | 110 | 21.68+j7.38 | 4.38 | 0.189 | 0.019 |
| 5 | 110 | 19.74+j5.596 | 7.95 | 0.277 | 0.014 |
| 6 | 110 | 6.24+j2.076 | 14.7 | 0.0535 | 0.0115 |
| Total |  |  |  | 1.081 | 0.2105 |

Table (3.32)

From previous Ʈ equal to   then  we can find ∆W1 which is equal to:

∆W1= Ʈ ( ∆PT.L + ∆P T.R)

= 2405 (5.32 + 1.081) = 15394.4 MW

After that we find ∆W2 which is equal to:

∆W2 = T *∆P O.C

= 8760 *0.2105 = 1843.98 MW.

After we found ∆W1 and ∆W2 we can found the cost of the energy loss which is equal to  Z losses= z L * (∆W1 +∆W2)

Z losses= 160 *(15394.4 + 1843.98) =2758.1* 103  Ruble

Now we will find the running cost which is equal to:

I = (n* KT.L) + (m*K sub)+ Z losses.

I = (2.8% * 8001.5) + (7.8% *2831) + (8.8% * 2247.3) + 2758.1

I = 224+ 220.82 +197.76 +2758.1 = 3400.7* 103   Ruble.

After founding the running cost now we will find the total cost which is equal to:

Z= EN*K + I

Z= (0.2 *13079.8) +3400.7 = 6016.66 *103   Ruble.

From the previous calculation we obtain than network # 8 is the most economical network. So it will be selected to analysis it for load flow study.

# Chapter Five

Load-flow Study

Introduction:

The load flow study is very important in evaluating the operation of power systems.  Controlling them and planning for the future expansion, the relating to a real power system can be carried out only with a digital computer.

Because of the complexity of the calculation we use a computer program in our case we use the ETAP power station v4.0, this program uses a number of methods of calculation such as Newton-Raphson and Gauss-Seidal methods and others in or case we are going to use Newton-Raphson method.

## 4.1 Data for load flow:

The main source of data for the system is the One-Line diagram; this data includes the series impedance and shunt admittance's of the transmission line, other essential information includes transformer tap setting, data about the nominal voltages and the load power and the generated power, all of this information is in the previous chapter that we are going to use for network # 8.

In the load flow study we are going to study three cases:

- The maximum load state.

- The minimum load state.

- The after fault state.

## 4.2. The Maximum Load State Analysis:

In this section maximum load state will be studied and we will see the optimization problems and will search solution for this optimization problem; and obtain results and make recommendations.

### 4.2.1. Original Condition of the network:

The data will be supplied to the program with the rating that we get from calculation and it's in table (4.1)

| Bus ID | Type | Initial Voltage |  |  | Motor Load |  | Static Load |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | kV | % Mag. | Ang. | MW | Mvar | MW | Mvar |
| Bus 1 | Load | 110.000 | 100.0 | 0.0 |  |  |  |  |
| Bus2 | Load | 220.000 | 100.0 | 0.0 |  |  |  |  |
| Bus3 | Load | 220.000 | 100.0 | 0.0 |  |  |  |  |
| Bus4 | Load | 110.000 | 100.0 | 0.0 |  |  |  |  |
| Bus5 | Load | 110.000 | 100.0 | 0.0 |  |  |  |  |
| Bus6 | Load | 110.000 | 100.0 | 0.0 |  |  |  |  |
| Bus7 | Load | 110.000 | 100.0 | 0.0 |  |  |  |  |
| Bus8 | Load | 110.000 | 100.0 | 0.0 |  |  |  |  |
| Bus9 | Swing | 220.000 | 100.0 | 0.0 |  |  |  |  |
| Bus10 | Load | 110.000 | 100.0 | 0.0 |  |  |  |  |
| Bus LOAD 1 | Load | 6.600 | 100.0 | 0.0 | 21.427 | 8.469 | 2.381 | 0.941 |
| Bus LOAD 2 | Load | 6.600 | 100.0 | 0.0 | 24.189 | 9.560 | 2.688 | 1.062 |
| Bus LOAD 3 | Load | 6.600 | 100.0 | 0.0 | 13.266 | 5.243 | 1.474 | 0.583 |
| Bus LOAD 4 | Load | 6.600 | 100.0 | 0.0 | 8.789 | 3.473 | 0.977 | 0.386 |
| Bus LOAD 5 | Load | 6.600 | 100.0 | 0.0 | 11.676 | 4.615 | 1.297 | 0.513 |
| Bus LOAD 6 | Load | 6.600 | 100.0 | 0.0 | 5.499 | 2.173 | 0.611 | 0.241 |
| Total Number of Buses: 16 |  |  |  |  | 84.847 | 33.534 | 9.427 | 3.726 |

Table (4.1)

After we run the program we get the results that is in Appendix A, and from table (4.2) we can see that some voltages is less then nominal  voltages (220 ,110 ,6.6 ).

| CKT / Branch | From-To Bus Flow |  | To-From Bus Flow |  | Losses |  | % Bus Voltage |  | Vd % Drop in Vmag |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| ID | MW | Mvar | MW | Mvar | kW | Kvar | From | To |  |
| Line 1-3 | -12.720 | -6.080 | 13.770 | 6.935 | 1049.1 | 854.4 | 89.5 | 98.0 | 8.53 |
| Line1-4 | -1.702 | -0.794 | 1.720 | 0.760 | 18.4 | -34.1 | 89.5 | 90.6 | 1.12 |
| T5 | 14.422 | 6.874 | -14.372 | -5.680 | 50.4 | 1194.0 | 89.5 | 86.6 | 2.93 |
| Line15 | -46.495 | -20.325 | 46.826 | 21.269 | 331.3 | 943.2 | 98.5 | 100.0 | 1.53 |
| Line A-1 | -49.689 | -22.350 | 50.073 | 23.706 | 383.7 | 1355.7 | 98.3 | 100.0 | 1.67 |
| Line 3-4 | -11.236 | -5.373 | 12.034 | 6.009 | 798.4 | 636.5 | 90.6 | 98.1 | 7.44 |
| T6 | 9.516 | 4.613 | -9.469 | -3.742 | 46.8 | 870.9 | 90.6 | 83.5 | 3.37 |
| Line2-5 | -18.930 | -8.901 | 19.685 | 9.737 | 754.4 | 835.4 | 93.7 | 98.4 | 4.78 |
| Line5-6 | 6.124 | 2.794 | -6.014 | -2.752 | 109.8 | 42.0 | 93.7 | 91.7 | 1.94 |
| T7 | 6.403 | 3.054 | -6.368 | -2.517 | 34.6 | 536.9 | 93.7 | 90.4 | 3.25 |
| T8 | 6.403 | 3.054 | -6.368 | -2.517 | 34.6 | 536.9 | 93.7 | 90.4 | 3.25 |
| T9 | 3.007 | 1.376 | -2.993 | -1.183 | 14.2 | 193.0 | 91.7 | 89.3 | 2.46 |
| T10 | 3.007 | 1.376 | -2.993 | -1.183 | 14.2 | 193.0 | 91.7 | 89.3 | 2.46 |
| T1 | 23.248 | 10.163 | -9.842 | -4.868 | 8.5 | 0.5 | 98.5 | 98.4 | 0.02 |
|  |  |  | -13.397 | -5.295 |  |  | 98.5 | 98.4 | 0.04 |
| T2 | 23.248 | 10.163 | -9.842 | -4.868 | 8.5 | 0.5 | 98.5 | 98.4 | 0.02 |
|  |  |  | -13.397 | -5.295 |  |  | 98.5 | 98.4 | 0.04 |
| T25 | 24.217 | 11.277 | -12.034 | -6.009 | 88.7 | 11.4 | 98.3 | 98.1 | 0.25 |
|  |  |  | -12.094 | -5.256 |  |  | 98.3 | 97.9 | 0.39 |
| T26 | 25.473 | 11.073 | -13.770 | -6.935 | 86.1 | 23.4 | 98.3 | 98.0 | 0.28 |
|  |  |  | -11.617 | -4.115 |  |  | 98.3 | 97.9 | 0.39 |
| Total |  |  |  |  | 3831.8 | 8193.6 |  |  |  |

Table (4.2)

### 4.2.1. Improvement of the maximum load state:

When the original condition analyzed we noticed that there is a drop voltage in most of the buses. in table (4.3) the buses and the drop voltage in each.

|  |  | Critical Report |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| ID | Device Type | Rating | Unit | Calculated | %Mag. | Condition |
| Bus LOAD 4 | Bus | 6.600 | kV | 6.247 | 94.7 | Under Voltage |
|  |  | Marginal Report |  |  |  |  |
| ID | Device Type | Rating | Unit | Calculated | %Mag. | Condition |
| Bus 1 | Bus | 110.000 | kV | 110.707 | 100.6 | Under Voltage |
| Bus LOAD 3 | Bus | 6.600 | kV | 6.488 | 98.3 | Under Voltage |
| Bus LOAD 5 | Bus | 6.600 | kV | 6.710 | 101.7 | Under Voltage |
| Bus LOAD 6 | Bus | 6.600 | kV | 6.636 | 100.5 | Under Voltage |
| Bus4 | Bus | 110.000 | kV | 111.812 | 101.6 | Under Voltage |

Table (4.4)

This is the analysis of the network:

The calculated voltages those shown in the table are not acceptable because of the extra drop voltage in the distribution networks; and the voltages should be adjusted to                       VMAX= (1.05-1.1) VNOM. This is required in max load for better performance of the network, because of the drop we are going to increase the tabs of the 3 winding T.R and 2 winding T.R. and because that the tabs didn't satisfy the condition we add capacitors to the low voltage buses, we increase the tabs 2% in the T.R. and we added a capacitor bank as the following:

- At bus load 3 we added 9 Mvar.

- At bus load 4 we added 12 Mvar.

- At bus load 5 we added 3 Mvar.

- At bus load 6 we added 3 Mvar.

After this addition to the network we get these results in table (4.5):

| CKT / Branch | From-To Bus Flow |  | To-From Bus Flow |  | Losses |  | % Bus Voltage |  | Vd % Drop in Vmag |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| ID | MW | Mvar | MW | Mvar | kW | Kvar | From | To |  |
| Line 1-3 | -13.230 | 5.375 | 14.003 | -4.778 | 772.4 | 597.6 | 105.9 | 109.5 | 3.63 |
| Line1-4 | -1.758 | -1.770 | 1.782 | 1.720 | 23.1 | -50.0 | 105.9 | 107.2 | 1.31 |
| T5 | 14.989 | -3.605 | -14.955 | 4.401 | 33.5 | 795.1 | 105.9 | 107.0 | 1.19 |
| Line15 | -47.304 | -13.421 | 47.558 | 14.035 | 254.4 | 613.3 | 108.9 | 110.0 | 1.11 |
| Line A-1 | -50.838 | 1.830 | 51.108 | -0.889 | 269.9 | 941.2 | 109.5 | 110.0 | 0.52 |
| Line 3-4 | -11.751 | 7.220 | 12.455 | -6.683 | 703.6 | 537.1 | 107.2 | 109.5 | 2.38 |
| T6 | 9.970 | -8.939 | -9.916 | 9.938 | 53.7 | 999.1 | 107.2 | 107.5 | 5.19 |
| Line2-5 | -19.401 | -2.065 | 19.916 | 2.603 | 515.5 | 538.1 | 105.7 | 108.9 | 3.16 |
| Line5-6 | 6.264 | -0.595 | -6.189 | 0.591 | 75.0 | -3.3 | 105.7 | 104.6 | 1.15 |
| T7 | 6.568 | 1.330 | -6.544 | -0.954 | 24.3 | 376.1 | 105.7 | 104.3 | 1.39 |
| T8 | 6.568 | 1.330 | -6.544 | -0.954 | 24.3 | 376.1 | 105.7 | 104.3 | 1.39 |
| T9 | 3.094 | -0.296 | -3.085 | 0.427 | 9.7 | 131.2 | 104.6 | 104.8 | 0.19 |
| T10 | 3.094 | -0.296 | -3.085 | 0.427 | 9.7 | 131.2 | 104.6 | 104.8 | 0.19 |
| T1 | 23.652 | 6.711 | -9.958 | -1.302 | 6.8 | 0.5 | 108.9 | 108.9 | 0.01 |
|  |  |  | -13.687 | -5.409 |  |  | 108.9 | 108.9 | 0.04 |
| T2 | 23.652 | 6.711 | -9.958 | -1.302 | 6.8 | 0.5 | 108.9 | 108.9 | 0.01 |
|  |  |  | -13.687 | -5.409 |  |  | 108.9 | 108.9 | 0.04 |
| T25 | 24.648 | -1.097 | -12.455 | 6.683 | 59.8 | 22.7 | 109.5 | 109.5 | 0.06 |
|  |  |  | -12.133 | -5.563 |  |  | 109.5 | 109.0 | 0.46 |
| T26 | 26.190 | -0.733 | -14.003 | 4.778 | 64.1 | 20.8 | 109.5 | 109.5 | 0.00 |
|  |  |  | -12.123 | -4.024 |  |  | 109.5 | 109.0 | 0.46 |
| Total |  |  |  |  | 2906.7 | 6027.5 |  |  |  |

Table (4.5).

And this is the schematics of the network after the addition:

Before the improvement the power loss = 3831.8KW

And after the improvement the power loss decreased to = 2906.7

∆P loss = 925.1 KW.

And the full report after  and before the improvement from the program is in appendix A

## 4.3. Minimum load state:

In this case we will study the original minimum load case and we will select the solution for the study.

### 4.3.1. Original minimum load state:

In this case the network will be studied in its minimum load that the load will be decreased by 60% that we will multiply the real and reactive power by 0.4 at each load and the swing bus supplied by 220 Kv, and the data for the minimum case is in table (4.6).

| Bus |  | Initial Voltage |  |  | Motor Load |  | Static Load |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| ID | Type | kV | % Mag. | Ang. | MW | Mvar | MW | Mvar |
| Bus 1 | Load | 110.000 | 100.0 | 0.0 |  |  |  |  |
| Bus2 | Load | 220.000 | 100.0 | 0.0 |  |  |  |  |
| Bus3 | Load | 220.000 | 100.0 | 0.0 |  |  |  |  |
| Bus4 | Load | 110.000 | 100.0 | 0.0 |  |  |  |  |
| Bus 5 | Load | 110.000 | 100.0 | 0.0 |  |  |  |  |
| Bus6 | Load | 110.000 | 100.0 | 0.0 |  |  |  |  |
| Bus7 | Load | 110.000 | 100.0 | 0.0 |  |  |  |  |
| Bus8 | Load | 110.000 | 100.0 | 0.0 |  |  |  |  |
| Bus11 | Swing | 220.000 | 100.0 | 0.0 |  |  |  |  |
| Bus 12 | Load | 110.000 | 100.0 | 0.0 |  |  |  |  |
| Bus LOAD 1 | Load | 6.600 | 100.0 | 0.0 | 3.515 | 1.389 | 0.391 | 0.154 |
| Bus LOAD 2 | Load | 6.600 | 100.0 | 0.0 | 9.676 | 3.824 | 1.075 | 0.425 |
| Bus LOAD 3 | Load | 6.600 | 100.0 | 0.0 | 5.307 | 2.097 | 0.590 | 0.233 |
| Bus LOAD 4 | Load | 6.600 | 100.0 | 0.0 | 8.789 | 3.473 | 0.977 | 0.386 |
| Bus LOAD 5 | Load | 6.600 | 100.0 | 0.0 | 4.670 | 1.846 | 0.519 | 0.205 |
| Bus LOAD 6 | Load | 6.600 | 100.0 | 0.0 | 2.260 | 0.893 | 0.251 | 0.099 |
| Total Nunmber of Buses: 16 |  |  |  |  | 34.217 | 13.523 | 3.802 | 1.503 |

Table(4.6)

After we run the program we get the results that is in Appendix B, and from table (4.7) we can see that some voltages is less then nominal  voltages (220 ,110 ,6.6 ).

| CKT / Branch | From-To Bus Flow |  | To-From Bus Flow |  | Losses |  | % Bus Voltage |  | Vd % Drop in Vmag |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| ID | MW | Mvar | MW | Mvar | kW | Kvar | From | To |  |
| Line 1-3 | -7.130 | -3.155 | 7.416 | 3.344 | 285.5 | 189.2 | 94.8 | 99.2 | 4.40 |
| Line1-4 | 1.298 | 0.686 | -1.288 | -0.732 | 10.3 | -46.1 | 94.8 | 94.0 | 0.86 |
| T5 | 5.832 | 2.469 | -5.825 | -2.302 | 7.1 | 167.2 | 94.8 | 93.8 | 1.05 |
| Line15 | -18.526 | -7.502 | 18.576 | 7.432 | 50.3 | -69.5 | 99.4 | 100.0 | 0.57 |
| Line A-1 | -20.006 | -9.053 | 20.068 | 9.249 | 61.1 | 195.5 | 99.3 | 100.0 | 0.66 |
| Line 3-4 | -8.280 | -3.847 | 8.679 | 4.135 | 398.8 | 287.9 | 94.0 | 99.2 | 5.24 |
| T6 | 9.568 | 4.579 | -9.524 | -3.764 | 43.8 | 815.1 | 94.0 | 86.8 | 3.25 |
| Line2-5 | -7.675 | -3.189 | 7.785 | 3.258 | 109.4 | 68.5 | 97.6 | 99.4 | 1.77 |
| Line5-6 | 2.512 | 0.998 | -2.496 | -1.042 | 16.4 | -44.2 | 97.6 | 96.9 | 0.74 |
| T7 | 2.582 | 1.096 | -2.577 | -1.018 | 5.0 | 77.2 | 97.6 | 96.5 | 1.18 |
| T8 | 2.582 | 1.096 | -2.577 | -1.018 | 5.0 | 77.2 | 97.6 | 96.5 | 1.18 |
| T9 | 1.248 | 0.521 | -1.246 | -0.492 | 2.1 | 28.9 | 96.9 | 96.0 | 0.92 |
| T10 | 1.248 | 0.521 | -1.246 | -0.492 | 2.1 | 28.9 | 96.9 | 96.0 | 0.92 |
| T1 | 9.263 | 3.751 | -3.892 | -1.629 | 1.3 | 0.1 | 99.4 | 99.4 | 0.01 |
|  |  |  | -5.369 | -2.122 |  |  | 99.4 | 99.4 | 0.01 |
| T2 | 9.263 | 3.751 | -3.892 | -1.629 | 1.3 | 0.1 | 99.4 | 99.4 | 0.01 |
|  |  |  | -5.369 | -2.122 |  |  | 99.4 | 99.4 | 0.01 |
| T25 | 10.482 | 4.482 | -8.679 | -4.135 | 5.2 | 19.5 | 99.3 | 99.2 | 0.12 |
|  |  |  | -1.798 | -0.327 |  |  | 99.3 | 99.2 | 0.11 |
| T26 | 9.524 | 4.571 | -7.416 | -3.344 | 6.4 | 12.5 | 99.3 | 99.2 | 0.10 |
|  |  |  | -2.102 | -1.214 |  |  | 99.3 | 99.2 | 0.11 |
| Total |  |  |  |  | 1011.2 | 1808.0 |  |  |  |

Table (4.7)

### 4.3.2 Improvement of minimum load state:

When the original minimum condition analyzed we noticed that there is a drop voltage in most of the buses. In table (4.8) the buses and the drop voltage in each.

|  |  | Critical report |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| ID | Device Type | Rating | Unit | Calculated | %Mag. | Condition |
| Bus 1 | Bus | 110.000 | kV | 104.317 | 94.8 | Under Voltage |
| Bus LOAD 3 | Bus | 6.600 | kV | 6.190 | 93.8 | Under Voltage |
| Bus LOAD 4 | Bus | 6.600 | kV | 5.728 | 86.8 | Under Voltage |
| Bus4 | Bus | 110.000 | kV | 103.376 | 94.0 | Under Voltage |
|  |  | Marginal Report |  |  |  |  |
| ID | Device Type | Rating | Unit | Calculated | %Mag. | Condition |
| Bus 12 | Bus | 110.000 | kV | 109.366 | 99.4 | Under Voltage |
| Bus 5 | Bus | 110.000 | kV | 107.413 | 97.6 | Under Voltage |
| Bus LOAD 1 | Bus | 6.600 | kV | 6.549 | 99.2 | Under Voltage |
| Bus LOAD 2 | Bus | 6.600 | kV | 6.561 | 99.4 | Under Voltage |
| Bus LOAD 5 | Bus | 6.600 | kV | 6.367 | 96.5 | Under Voltage |
| Bus LOAD 6 | Bus | 6.600 | kV | 6.335 | 96.0 | Under Voltage |
| Bus2 | Bus | 220.000 | kV | 218.748 | 99.4 | Under Voltage |
| Bus3 | Bus | 220.000 | kV | 218.539 | 99.3 | Under Voltage |
| Bus6 | Bus | 110.000 | kV | 106.602 | 96.9 | Under Voltage |
| Bus7 | Bus | 110.000 | kV | 109.162 | 99.2 | Under Voltage |
| Bus8 | Bus | 110.000 | kV | 109.135 | 99.2 | Under Voltage |

Table (4.8)

This is the analysis of the network:

The calculated voltages those shown in the table are not acceptable because of the extra drop voltage in the distribution networks; and the voltages should be adjusted to                       VMAX= (1.00-1.05) VNOM. This is required in min load for better performance of the network, because of the drop we are going to increase the tabs of the 3 winding T.R and 2 winding T.R. and because that the tabs didn't satisfy the condition we add capacitors to the low voltage buses, we increase the tabs 2% in the T.R. and we added a capacitor bank as the following:

- At bus load 3 we added 3 Mvar.

- At bus load 4 we added 12 Mvar.

After this addition to the network we get these results in table (4.9):

| CKT / Branch | From-To Bus Flow |  | To-From Bus Flow |  | Losses |  | % Bus Voltage |  | Vd % Drop in Vmag |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| ID | MW | Mvar | MW | Mvar | kW | Kvar | From | To |  |
| Line 1-3 | -7.266 | 3.191 | 7.517 | -3.041 | 251.5 | 150.9 | 103.2 | 105.1 | 1.91 |
| Line1-4 | 1.324 | -2.458 | -1.293 | 2.419 | 30.4 | -39.6 | 103.2 | 103.5 | 0.33 |
| T5 | 5.942 | -0.733 | -5.937 | 0.859 | 5.3 | 126.2 | 103.2 | 103.4 | 0.20 |
| Line15 | -18.703 | -7.535 | 18.749 | 7.425 | 46.3 | -109.4 | 104.5 | 105.0 | 0.54 |
| Line A-1 | -20.484 | 6.760 | 20.536 | -6.597 | 52.7 | 162.9 | 105.0 | 105.0 | 0.04 |
| Line 3-4 | -8.595 | 5.608 | 9.013 | -5.313 | 417.9 | 294.9 | 103.5 | 105.2 | 1.65 |
| T6 | 9.889 | -8.026 | -9.837 | 8.995 | 52.1 | 968.8 | 103.5 | 103.6 | 4.82 |
| Line2-5 | -7.751 | -3.196 | 7.852 | 3.247 | 100.5 | 51.5 | 102.8 | 104.4 | 1.70 |
| Line5-6 | 2.536 | 0.996 | -2.521 | -1.048 | 15.0 | -51.7 | 102.8 | 102.0 | 0.71 |
| T7 | 2.608 | 1.100 | -2.603 | -1.029 | 4.6 | 71.0 | 102.8 | 101.6 | 1.13 |
| T8 | 2.608 | 1.100 | -2.603 | -1.029 | 4.6 | 71.0 | 102.8 | 101.6 | 1.13 |
| T9 | 1.260 | 0.524 | -1.258 | -0.497 | 2.0 | 26.6 | 102.0 | 101.2 | 0.88 |
| T10 | 1.260 | 0.524 | -1.258 | -0.497 | 2.0 | 26.6 | 102.0 | 101.2 | 0.88 |
| T1 | 9.351 | 3.767 | -3.926 | -1.624 | 1.2 | 0.1 | 104.5 | 104.4 | 0.01 |
|  |  |  | -5.424 | -2.144 |  |  | 104.5 | 104.4 | 0.01 |
| T2 | 9.351 | 3.767 | -3.926 | -1.624 | 1.2 | 0.1 | 104.5 | 104.4 | 0.01 |
|  |  |  | -5.424 | -2.144 |  |  | 104.5 | 104.4 | 0.01 |
| T25 | 10.179 | -4.250 | -9.013 | 5.313 | 1.9 | 23.1 | 105.0 | 105.2 | 0.12 |
|  |  |  | -1.163 | -1.040 |  |  | 105.0 | 104.9 | 0.18 |
| T26 | 10.305 | -2.510 | -7.517 | 3.041 | 6.2 | 11.1 | 105.0 | 105.1 | 0.04 |
|  |  |  | -2.782 | -0.520 |  |  | 105.0 | 104.9 | 0.18 |
| Total |  |  |  |  | 995.4 | 1784.1 |  |  |  |

Table (4.9)

And this is the schematics of the network after the addition:

Before the improvement the power loss = 1011.2KW

And after the improvement the power loss decreased to=995.4 KW

∆P loss = 15.8 KW.

And the full report after  and before the improvement from the program is in appendix B.

## 4.4 After fault condition:

In this section we will assume that the network is affected by a fault condition in some location of the transmission lines of the network, after the fault occurs we will try to optimize the problem.

### 4.4.1 Fault at line (A-1)

This line is one of the most important lines in the network, which is connecting the sub-station to the half of the network and carries max power.

It will be assumed that a fault happened at one line of the double line, because of that the resistance and capacitance will be multiplied by 2 and we will divide the admittance by 2.

After we change the data and run the program we get this data in table (4.10):

| CKT / Branch | From-To Bus Flow |  | To-From Bus Flow |  | Losses |  | % Bus Voltage |  | Vd % Drop in Vmag |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| ID | MW | Mvar | MW | Mvar | kW | Kvar | From | To |  |
| Line 1-3 | -13.921 | -6.545 | 14.959 | 7.380 | 1038.7 | 835.0 | 98.1 | 106.6 | 8.47 |
| Line1-4 | -2.143 | -1.010 | 2.167 | 0.971 | 24.4 | -39.1 | 98.1 | 99.4 | 1.29 |
| T5 | 16.064 | 7.554 | -16.012 | -6.328 | 51.7 | 1226.1 | 98.1 | 95.2 | 2.95 |
| Line15 | -47.103 | -20.188 | 47.380 | 20.886 | 277.6 | 697.4 | 108.6 | 110.0 | 1.38 |
| Line A-1 | -52.036 | -23.167 | 52.739 | 24.192 | 703.0 | 1025.7 | 106.9 | 110.0 | 3.11 |
| Line 3-4 | -12.036 | -5.625 | 12.791 | 6.214 | 754.7 | 588.2 | 99.4 | 106.7 | 7.21 |
| T6 | 9.869 | 4.655 | -9.828 | -3.884 | 41.4 | 770.4 | 99.4 | 92.1 | 3.14 |
| Line2-5 | -19.304 | -8.786 | 19.929 | 9.455 | 625.7 | 669.7 | 104.3 | 108.6 | 4.33 |
| Line5-6 | 6.238 | 2.753 | -6.147 | -2.740 | 90.9 | 12.8 | 104.3 | 102.5 | 1.76 |
| T7 | 6.533 | 3.016 | -6.504 | -2.571 | 28.8 | 445.8 | 104.3 | 101.3 | 2.93 |
| T8 | 6.533 | 3.016 | -6.504 | -2.571 | 28.8 | 445.8 | 104.3 | 101.3 | 2.93 |
| T9 | 3.073 | 1.370 | -3.061 | -1.210 | 11.8 | 160.0 | 102.5 | 100.3 | 2.22 |
| T10 | 3.073 | 1.370 | -3.061 | -1.210 | 11.8 | 160.0 | 102.5 | 100.3 | 2.22 |
| T1 | 23.551 | 10.094 | -9.965 | -4.728 | 7.1 | 0.4 | 108.6 | 108.6 | 0.02 |
|  |  |  | -13.580 | -5.367 |  |  | 108.6 | 108.6 | 0.03 |
| T2 | 23.551 | 10.094 | -9.965 | -4.728 | 7.1 | 0.4 | 108.6 | 108.6 | 0.02 |
|  |  |  | -13.580 | -5.367 |  |  | 108.6 | 108.6 | 0.03 |
| T25 | 25.232 | 11.708 | -12.791 | -6.214 | 80.1 | 11.7 | 106.9 | 106.7 | 0.24 |
|  |  |  | -12.361 | -5.483 |  |  | 106.9 | 106.5 | 0.37 |
| T26 | 26.804 | 11.459 | -14.959 | -7.380 | 77.3 | 25.6 | 106.9 | 106.6 | 0.27 |
|  |  |  | -11.768 | -4.053 |  |  | 106.9 | 106.5 | 0.37 |
| Total |  |  |  |  | 3861.0 | 7035.8 |  |  |  |

Table(4.10)

### 4.4.2 Improvement of after fault condition:

The calculated voltages those shown in the table are not acceptable because of the extra drop voltage in the distribution networks; and the voltages should be adjusted to                       VMAX= (1.05-1.10) VNOM. This is required in min load for better performance of the network, because of the drop we are going to increase the tabs of the 3 winding T.R and 2 winding T.R. and because that the tabs didn't satisfy the condition we add capacitors to the low voltage buses, we increase the tabs 2% in the T.R. and we added a capacitor bank as the following:

- At bus load 3 we added 9 Mvar.

- At bus load 4 we added 9 Mvar.

- At bus load 6 we added 3 Mvar.

This is data after the addition of the capacitors table (4.11).

| CKT / Branch | From-To Bus Flow |  | To-From Bus Flow |  | Losses |  | % Bus Voltage |  | Vd % Drop in Vmag |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| ID | MW | Mvar | MW | Mvar | kW | Kvar | From | To |  |
| Line 1-3 | -14.176 | 3.231 | 15.011 | -2.577 | 834.7 | 653.6 | 103.6 | 108.5 | 4.83 |
| Line1-4 | -2.174 | -0.816 | 2.195 | 0.767 | 21.1 | -48.8 | 103.6 | 104.8 | 1.17 |
| T5 | 16.350 | -2.415 | -16.310 | 3.368 | 40.2 | 953.4 | 103.6 | 104.4 | 0.79 |
| Line15 | -47.086 | -16.811 | 47.350 | 17.458 | 263.6 | 646.7 | 108.8 | 110.0 | 1.24 |
| Line A-1 | -52.270 | -3.443 | 52.852 | 4.026 | 581.8 | 582.4 | 108.5 | 110.0 | 1.50 |
| Line 3-4 | -12.272 | 4.072 | 12.918 | -3.583 | 645.9 | 489.3 | 104.8 | 108.5 | 3.69 |
| T6 | 10.077 | -4.839 | -10.038 | 5.567 | 39.1 | 728.0 | 104.8 | 102.9 | 2.81 |
| Line2-5 | -19.349 | -5.490 | 19.905 | 6.075 | 555.2 | 585.7 | 105.0 | 108.7 | 3.75 |
| Line5-6 | 6.265 | -0.541 | -6.189 | 0.539 | 75.9 | -1.5 | 105.0 | 103.8 | 1.17 |
| T7 | 6.542 | 3.015 | -6.514 | -2.575 | 28.4 | 440.7 | 105.0 | 102.1 | 2.91 |
| T8 | 6.542 | 3.015 | -6.514 | -2.575 | 28.4 | 440.7 | 105.0 | 102.1 | 2.91 |
| T9 | 3.094 | -0.270 | -3.085 | 0.403 | 9.8 | 132.9 | 103.8 | 104.0 | 0.15 |
| T10 | 3.094 | -0.270 | -3.085 | 0.403 | 9.8 | 132.9 | 103.8 | 104.0 | 0.15 |
| T1 | 23.543 | 8.406 | -9.952 | -3.038 | 6.9 | 0.5 | 108.8 | 108.7 | 0.02 |
|  |  |  | -13.584 | -5.369 |  |  | 108.8 | 108.7 | 0.04 |
| T2 | 23.543 | 8.406 | -9.952 | -3.038 | 6.9 | 0.5 | 108.8 | 108.7 | 0.02 |
|  |  |  | -13.584 | -5.369 |  |  | 108.8 | 108.7 | 0.04 |
| T25 | 25.400 | 1.874 | -12.918 | 3.583 | 67.5 | 14.7 | 108.5 | 108.5 | 0.01 |
|  |  |  | -12.415 | -5.442 |  |  | 108.5 | 108.0 | 0.45 |
| T26 | 26.870 | 1.569 | -15.011 | 2.577 | 67.1 | 21.4 | 108.5 | 108.5 | 0.04 |
|  |  |  | -11.792 | -4.125 |  |  | 108.5 | 108.0 | 0.45 |
| Total |  |  |  |  | 3282.5 | 5773.2 |  |  |  |

Table (4.11)

Losses before optimization= 3861.0 MW.

Losses after optimization= 3282.5 MW.

And the full report after  and before the improvement from the program is in appendix B.

## 4.5 The economical benefit of using the capacitors:

If we make a comparative study between the losses that occurs in the network caused by the T.L and the other component in the Max-load study and the capacitor we installed to improve the losses which is equal to 3831.8 KW and after the installation of the capacitors which is equal to2906.7 KW the difference in the losses equal to 925.1 KW. And from previous we know that every 1 MWh charged for 160 Ruble, if we calculated the losses per one year equals to ∆P loss * Ʈ = 0.9251 MW * 2405 H= 2224.865 MWH the cost will equal to 2224.865 * 160 =355978.5 Ruble

And for the cost of the capacitors which costs for every 3 MVAR is 18*103 Ruble the total # of the capacitors is 27 MVAR which costs 9*18*103 = 162000 Ruble

The saving is about 355978.5 –162000=193978.5 =194*103 Ruble.