## Slide 1
بسم الله الرحمن الرحيم
Water supply services Management
for tubas governorate
Prepared by
Ameen Khabass Ameer qab
Qasim Bsharat Laith thaher
Supervisor
Dr. Anan Jayyousi

## Slide 2: Content
Objective
Overview of Tubas Governorate
Future population
Consumption rates
Future demand, supply and water gap
Gap reduction
Long-term solutions
Packages of investment plan
Bardala water distribution network

## Slide 3: Objectives
Analyze the current water situation of Tubas Governorate
Estimate the water gap in the future
Discuss probable solutions to cover the gap
Suggest an investment plan
Design a network for one un-served locality

## Slide 4: Overview of Tubas Governorate
Location

## Slide 5: Overview of Tubas Governorate
Classification | Area (km2) | Percentage
Palestinian Built-up Area | 6.2 | 1.7
Israeli Colony | 7.7 | 2.1
Israeli Military Base | 15.8 | 4.3
Arable Land | 99.3 | 27.1
Permanent Crops | 70.5 | 19.3
Heterogeneous Agriculture | 1.9 | 0.5
Mine, Dump & Construction Sites | 0 | 0
Forest | 2.4 | 0.7
Open Space | 30.2 | 8.3
Shrub and/or herbaceous vegetation association | 12.5 | 3.4
Pastures | 119.6 | 32.7
Total | 366 | 100
Land Use

## Slide 6: Overview of Tubas Governorate
Topography
Max. elevation is 548 AMSL and min elevation is 182 BMSL.

## Slide 7: Overview of Tubas Governorate
Climate
Avg. rainfall depth is 329 mm

## Slide 8: Future Population
Clusters

## Slide 9: Future Population
r = 3.2 %
Cluster | Cluster Name | 2016 | Short Term (2020) | Intermediate Term (2025) | Long Term (2035)
1 | Bardala | 4,825 | 5,477 | 6,417 | 8,809
2 | Tubas | 34,807 | 39,512 | 46,298 | 63,566
3 | Tammun | 26,527 | 30,113 | 35,285 | 48,445
4 | Khirbet ar Ras al Ahmar | 694 | 788 | 922 | 1,265
Total |  | 66,853 | 75,890 | 88,922 | 122,085

## Slide 10: Consumption Rate -Urban-
Target year |  |  | 2016 | 2020 | 2025 | 2035
Urban | Domestic consumption | Rate (L/c/d) | 66 | 75 | 90 | 120
 |  | Ratio of M&I (%) | 79 | 79 | 79 | 79
 | Public consumption | Rate (L/c/d) | 7 | 8 | 10 | 14
 |  | Ratio of M&I (%) | 8 | 8 | 8.5 | 9
 | Livestock consumption | Rate (L/c/d) | 5 | 5 | 5 | 5
 |  | Ratio of M&I (%) | 6 | 5.5 | 4.5 | 3.5
 | Industrial consumption | Rate (L/c/d) | 6 | 7 | 9 | 13
 |  | Ratio of M&I (%) | 7 | 7.5 | 8 | 8.5
 | Total M&I consumption Rate (L/c/d) |  | 84 | 95 | 114 | 152
 | Physical losses (%) |  | 29 | 25 | 15 | 15
 | Total demand Rate (L/c/d) |  | 118 | 127 | 134 | 179

## Slide 11: Consumption Rate -Rural served-
Target year |  |  | 2016 | 2020 | 2025 | 2035
Rural Served | Domestic consumption | Rate (L/c/d) | 50 | 65 | 80 | 110
 |  | Ratio of M&I (%) | 79 | 79 | 79 | 79
 | Public consumption | Rate (L/c/d) | 3 | 4 | 5 | 6
 |  | Ratio of M&I (%) | 5 | 5 | 4.5 | 4.5
 | Livestock consumption | Rate (L/c/d) | 6 | 9 | 11 | 16
 |  | Ratio of M&I (%) | 10 | 10.5 | 11 | 11.5
 | Industrial consumption | Rate (L/c/d) | 4 | 5 | 6 | 7
 |  | Ratio of M&I (%) | 6 | 5.5 | 5.5 | 5
 | Total M&I consumption Rate (L/c/d) |  | 63 | 82 | 101 | 139
 | Physical losses (%) |  | 29 | 25 | 15 | 15
 | Total demand Rate (L/c/d) |  | 89 | 110 | 119 | 164

## Slide 12: Consumption Rate -rural unserved-
Target year |  |  | 2016 | 2020 | 2025 | 2035
Rural Unserved | Domestic consumption | Rate (L/c/d) | 30 | 45 | 70 | 100
 |  | Ratio of M&I % | 79 | 79 | 79 | 79
 | Public consumption | Rate (L/c/d) | 2 | 3 | 5 | 6
 |  | Ratio of M&I % | 6 | 6 | 5.5 | 5
 | Livestock consumption | Rate (L/c/d) | 4 | 6 | 10 | 15
 |  | Ratio of M&I % | 10 | 11 | 11.5 | 12
 | Industrial consumption | Rate (L/c/d) | 2 | 2 | 4 | 5
 |  | Ratio of M&I % | 5 | 4 | 4 | 4
 | Total M&I consumption rate |  | 38 | 57 | 89 | 127
 | physical losses (%) |  | 5 | 5 | 15 | 15
 | Total demand rate (L/c/d) |  | 40 | 60 | 104 | 149

## Slide 13: Future demand
Cluster | Cluster name | Short Term (2020) | Intermediate Term (2025) | Long Term (2035)
1 | Bardala | 328.6 | 667.4 | 1,312.5
2 | Tubas | 4,687.3 | 5,912.3 | 1,0978.0
3 | Tammun | 3,312.4 | 4,199.0 | 7,945.0
4 | Khirbet ar Ras al Ahmar | 60.1 | 100.4 | 194.7
Total |  | 8,388.4 | 10,879.1 | 20,430.2
(Unit: 1000 m3)

## Slide 14: Water supply
Water Resource |  | Quantity (Million m3/year)
Pumping from groundwater wells | Domestic | 1.4
 | Agricultural | 1.3
Discharge of springs water |  | 0.9
Purchasing from Israeli water company (Mekorot) |  | 5.4
Cluster | Cluster name | Supply
1 | Bardala | 151
2 | Tubas | 1,402
3 | Tammun | 825
4 | Khirbet ar Ras al Ahmar | 22
(Unit: 1000 m3)

## Slide 15: Future Water Gap (2020)
Gap = Demand – Supply
Total Gap = 704.8*103 m3

## Slide 16: Future Water Gap (2025)
Total Gap = 1,570.8*103 m3

## Slide 17: Future Water Gap (2035)
Total Gap = 5,057.0*103 m3

## Slide 18: Gap reduction
Near future solutions:
Loss reduction program
Rainwater harvesting
Long-term solutions:
Utilizing Groundwater
Utilizing Jordan River
Development of Non-Conventional Water Resources

## Slide 19: Loss reduction program
Our aim is to decrease the loss by 5%
Cluster | Cluster name | Water saved (1000 m3)
1 | Bardala | 0.0
2 | Tubas | 68.1
3 | Tammun | 41.3
4 | Khirbet ar Ras al Ahmar | 0.4
Total |  | 109.8

## Slide 20: Rainwater harvesting
Avg. family size is 5.6 capita.
No. of floor in each building is 2 floors
Each floor contain 2 apartments.
Avg. area of each apartment is 150 m2.
Avg. annual rainfall is 329 mm.
The rainwater collecting percentage 80%.

## Slide 21: Rainwater harvesting
Cluster | Cluster name | 2020 | 2025 | 2035
1 | Bardala | 2.3 | 5.6 | 14
2 | Tubas | 16.6 | 40.5 | 101.4
3 | Tammun | 12.6 | 30.9 | 2.7
4 | Khirbet ar Ras al Ahmar | 0.3 | 0.8 | 2
Total |  | 31.8 | 77.8 | 120.1
(Unit: 1000 m3)

## Slide 22: Remaining gap
Cluster | Cluster name | 2020 | 2025 | 2035
1 | Bardala | 0.0 | 86.6 | 313.6
2 | Tubas | 233.5 | 647.6 | 2,435.7
3 | Tammun | 330.1 | 635.5 | 1,956.4
4 | Khirbet ar Ras al Ahmar | 2.7 | 13.7 | 46.9
Total |  | 566.4 | 1,383.4 | 4,752.6
(Unit: 1000 m3)

## Slide 23: Long-Term Solutions
Utilizing Groundwater
Tubas governorate is located over the Eastern and the North-Eastern Aquifers
The most important development options for improving water quantities
Utilizing Jordan River
The Palestinian portion of Jordan river water is 250 Mcm/year
Surface water needs treatment

## Slide 24: Long-Term Solutions
Non-Conventional Water Resources
Water harvesting of seasonal floods
Tubas Governorate characterized by low rainfall rates and high temperatures
Can be used in irrigation and feeding groundwater
Wastewater Treatment
Sewerage networks are not available
Treated wastewater can be used for agricultural uses

## Slide 25: Utilizing Groundwater
The remaining gap is 4.75 Mcm/year in year 2035
According to PWA, there are 8 location for proposed new wells
New well is 300m depth and produces 1.00 Mcm/year

## Slide 26: New Groundwater wells

## Slide 27: Packages of investment plan
Based on estimated future water demand, Different projects will be implemented to cover this demand
Package components will vary according to the required action

## Slide 28: Packages of investment plan
Determine the diameter of transmission pipeline using continuity equation
Q = V * A
The head loss in transmission pipelines is calculated using the following equation
HL = 0.01 L
The pump head calculated using Energy Conservation principle (Bernoulli Equation)
HP = ∆Z + HL

## Slide 29: Packages of investment plan
The pumps power calculated by using following equation.
γ : Specific weight of water ( 9810 N/m3).
µ : Pump efficiency (assumed to be 75%).
Coding
WS- (first two latter of cluster name) C/ (package number)

## Slide 30: Sample of proposed Packages

## Slide 31: Cash flow of investment plan
Chart: Cash Flow
| 2020 | 2025 | 2030 | 2035
total cost | 8.513 | 10.12 | 5.793 | 1.52

## Slide 32: Cash flow of investment plan

## Slide 33: Bardala water distribution network
Bardala is located 13 km northeast of Tubas city.
The total area is 20,000 dunums (4 % of the Tubas Governorate area)
Built-up area = 480 dunums
Agricultural area = 10,000 dunums
Confiscated area = 400 dunums

## Slide 34: Bardala water distribution network
Population
Bardala represents only about 3.3% of Tubas Governorate in 2035.
Year | 2007 | 2016 | 2020 | 2025 | 2035
Population (capita) | 1,637 | 2177 | 2,471 | 2,895 | 3,974
r = 3.2 %

## Slide 35: Bardala water distribution network
Design Parameters:
Assumed head at the beginning = 140 m H2O
The design period is 19 years until 2035.
Maximum daily factor = 1.8
Average daily demand =100 L/c.d
Ductile iron pipes with Hazen-Williams coefficient (CHW = 130).
Min diameter = 1 inch.

## Slide 36: Bardala water distribution network
Demand calculation
The proposed daily water demand in the year of 2035 will be 100 L/c.d
The total demand
Demand definition
Using demand area and theisen polygon method

## Slide 37: Bardala water distribution network
Network layout

## Slide 38: Bardala water distribution network
Results
Parameter | Max. Value | Min. Value | Note
Demand | 2.82 m3/hr | 0.02 m3/hr | ــــــــــــــــــــــــ
Pressure | 95 m H2O | 20 m H2O | We used pressure reducing valve at the beginning of the network
Velocity | 1.52 m/s | 0.032 m/s | It's less the 0.3 m/s but it’s accepted since the network is used for drinking water and it's more than 0.01 m/s
Diameter (in) | Total Length (m)
4.0 | 979
2.0 | 3726
1.0 | 3244
Total | 7949

## Slide 39: Conclusion
The population of Tubas Governorate will become about 120,000 capita in 2035
The gap of water is about 5 Mcm/year in year 2035
To bridge this gap:
0.23 Mcm/year from near-future solutions
4.77 Mcm/year from long-term solutions
The total investment cost is 26 million dollar
The average investment per year around 1.53 Million$/year