## Slide 1: Analysis and design of engineering college
Supervisor :
D.Loay Dwaikat
Prepared by :
Hiba Shakhsheer
Maram Shehadeh
Mahmoud Abu Hanyia

## Slide 2: OUTLINES
Introduction
Site description
Architectural design
Structural design
Environmental design
mechanical design
Electrical design
Quantity surveying
Life cycle

## Slide 3
INTRODUCTION

## Slide 4: Site description
Site Location:
The project is located in the western part of the Nablus city, in bait wazan area specifically in the north about 500 meters from the new campus of Al-Najah University.

## Slide 5: Site description
Traffic and entrances of the site

## Slide 6: Site description
Analysis of adjacent buildings

## Slide 7: Architectural Design

## Slide 8: Site plan :

## Slide 9: Architectural Design
Site :

## Slide 10
GROUND FLOOR
AFTER
BEFORE

## Slide 11: First floor :

## Slide 12: Second floor :

## Slide 13: Third floor

## Slide 14: Fourth floor

## Slide 15: Architectural Design

## Slide 16: Architectural Design

## Slide 17: Architectural Design

## Slide 18: Architectural Design

## Slide 19: Architectural Design

## Slide 20: Structural analysis
Codes
- ACI 318-14
- ASCE 7-10
Material
- Compressive strength ( fʹc ) = 28 MPa
- Yielding strength of steel (fy) = 420 Mpa.
Bearing capacity = 150 kN /m2
Designed load
SID = 4.5 KN/m2
Live load = 5 KN/m2

## Slide 21: SEISMIC LOAD analysis
The seismic load will be designed according to ASCE 7-10 code, and using response spectrum approach for design, the following steps were taken to design the load:
mass source including 100% of dead and super imposed load and 25% of live loads
a. Seismic zone is 2B (Z=0.2) because the building is on Nablus
*SS = spectral response acceleration parameter at short periods.
Ss = 0.7
*S1 = spectral response acceleration parameter at a period of 1 s.
S1 = 0.18
site classification = SD (stiff soil )
site coefficient Fa and Fv according to Ss and S1
Fa = 1.24
Fv = 2.08

## Slide 22: SEISMIC LOAD analysis
Design Spectral Acceleration Parameters
SDs = 1.24*0.7*2/3 = 0.578
SD1= 2.08*0.18*2/3 = 0.25
I = the importance factor = 1
R = the response modiﬁcation factor
R = 6 (special reinforced concrete shear walls )
Design category : D

## Slide 23: SEISMIC LOAD analysis
Checks
Compatibility check
Equilibrium check
Internal Forces check
Deflection check
Modal mass participation ratio check
20 modes satisfy percentages higher than 90%.
Base shear check
ok
ok
ok
ok
ok
ok

## Slide 24
Checks
Drift Check
P delta check
This check is for story stiffness
ok
ok

## Slide 25: Structural analysis
Slab structural system :
Slab thickness =450mm

## Slide 26: Structural analysis
Slab structural system :
Slab thickness =620mm

## Slide 27: Structural analysis
Columns :

## Slide 28: Structural analysis

## Slide 29: Structural analysis
Shear Wall :

## Slide 30: Structural analysis
Footing design :

## Slide 31: Structural analysis

## Slide 32: Structural analysis
Tie beams :

## Slide 33: Structural analysis
Stairs :

## Slide 34: Structural analysis
Water tank:

## Slide 35: Structural analysis
Problems and challenges:- During the analysis of origin in terms of construction emerged a lot of problems and challenges
One of the most important problems that we cant add any column in the site .
So we use inclined columns
Add inclined columns extending from the ground floor to the second floor reduced the cantilever length

## Slide 36: Structural analysis

## Slide 37: Environmental design

## Slide 38: MATERIAL Properties
U-value for Building envelope
U-value(W/m2.K) | Component
0.457 | External Wall
2.097 | Internal Wall
0.344 | Floor
1.530 | Glass

## Slide 39: 3D Module in Design Builder

## Slide 40
Louvers system
Shading system

## Slide 41: Shading system
In Summer Day
21 June at 8:00 AM
21 June at 12:00 PM

## Slide 42: Shading system
In Winter Day
21 January at 8:00 AM
21 January at 12:00 AM

## Slide 43: Thermal comfort
Comfort PMV-set

## Slide 44: Thermal Design
Heating and cooling loads
  cooling load is 466.1 Kw
  Heating load is 356.6 Kw
Site and source Energy
Energy per conditioned building area[KWh/m2] | Energy per total Building area[KWh/m2] | Total Energy[KWh] | 
95.94 | 95.94 | 478532.14 | Total site Energy
95.94 | 95.94 | 478532.14 | Net Site Energy
229.95 | 229.95 | 1146925.12 | Total Source Energy
229.95 | 229.95 | 1146925.12 | Net Source Energy

## Slide 45: Thermal Design
Comfort set point not met Summery
Facility [Hrs.] | 
153.50 | Time set point not met during occupied heating
58.00 | Time set point not met during occupied cooling
918.00 | Time not comfortable based on simple ASHREAE 55-2004

## Slide 46: Acoustical design
Absorption coefficient

## Slide 47: Acoustical design
Reverberation time {Rt60}
Assessment | Recommended range | Rt60 Range at 500Hz | Volume(m3) | Room
ok | 0.7 – 0.9 | 0.79 | 137.4 | Lecture room
ok | 1.2 – 1.4 | 1.21 | 663.5 | Theater
ok | 0.4 – 0.7 | 0.41 | 592.12 | Computer lab
ok | 0.4 – 0.6 | 0.5 | 65.88 | office

## Slide 48: Acoustical design
Sound transmission class [STC]
assessment | STC Value(dB) | Type
Ok | 43 | Classroom wall External
Ok | 47 | Wall between classrooms
Ok | 47 | Wall (Between Classroom and Corridor)
Ok | 55 | Computer lab wall external
Ok | 47 | Office wall external
Ok | 47 | Wall between office and corridor
ok | 55 | External glass wall

## Slide 49: Acoustical design
Impact Insulation Class (IIc)
Assessment | IIC (db.) | Type
ok | 58 | floor

## Slide 50: Acoustical design
Loud speakers
  Type used : PRO-10RPC In-ceiling Speakers

## Slide 51: Acoustical design
Speakers distribution in cafeteria

## Slide 52: Mechanical design
Water system
Drainage system
Fire Figting
HVAC system
Elevators

## Slide 53: Water supply system
System used is underground tank with electrical pump
Total water consumption for building is : 19.2 m3
Fixture unit
Fourth floor | Third floor | Second floor | First floor | Ground floor | floor
50 | 50 | 47 | 30 | 45 | Zone 1
- | - | 52 | 35 | 52 | Zone 2
68 | 68 |  |  | - | Zone 3
118 | 118 | 99 | 65 | 97 | 
Total Fu in building = 497 |  |  |  |  | 

## Slide 54: Water supply system
Pipes Diameter and losses
Zone 3 | Zone 2 | Zone 1 | 
2” | 2” | 2” | Vertical pipe
1.5” | 1.5” | 1.5” | Horizontal pipe
¾” | ¾” | ¾” | Branch pipe
2.35 psi | 5.92 psi | 8.72 psi | Total loss
9.95 psi | 38.2 psi | 38.2 psi | Allowable loss
Ok | Ok | OK | assessment

## Slide 55: Water supply system
Water supply system plan {ground floor}

## Slide 56: Drainage system
Drainage system diameters
Type of Pipe | Slope | Diameter | Pipe
PVC | 0 % {90} | 4” | Vent
PVC | 1 % | 4” | Drainage
PVC | 0 %{90} | 4” | Stack
PVC | 2 % | 2” | Sewer

## Slide 57: Drainage system
Manholes plan

## Slide 58: Drainage system
Rain water plan

## Slide 59: Hvac Design
Total cooling load is 466 Kw
Total Heating load is 366 K
System used is VRV(variable refrigerant volume) for first three floors
VAV system was used for third and fourth floor

## Slide 60: Hvac Design
HVAC system plan (first floor)

## Slide 61: Hvac Design
HVAC system plan (third floor)

## Slide 62: Elevator design
Required number = 5
Car capacity = 2500 lb.
Car speed 350 fpm
Car passenger capacity = 13 person.

## Slide 63: Electrical design
Socket distribution
Artificial lighting

## Slide 64
Power for first floor plan

## Slide 65: Artificial lighting The artificial lighting is an important aspect in buildings, it has a major effect on productivity and working in buildings.

## Slide 66
Lighting for first floor plan

## Slide 67
Illuminance standard
Area | Recommended illuminance(lux)
Theater | 22
Office | 19
Drawing room | 22
Classroom | 19
Conference room | 19
Glare standard
2. Glare
1. Illuminance
Design illuminance(lux) | Recommended illuminance(lux) | area
204 | 150 | Cafeteria
372 | 300 | Theater
488 | 500 | Office
635 | 500 | Drawing room
532 | 400 | Classroom
253 | 100 | Corridor
578 | 300 | Conference room
152 | 100 | bathroom

## Slide 68
Uniformity:
It describes the ratio between the minimum and average illuminance, it should be greater than 0.6.
4. Reflection factors
The reflection is defined as the ratio between the luminous flux reflected by the surface and the luminous from the lamp, the reflection factors for surfaces in the building are listed in table
surface | Reflection factor(%)
Walls | 50%
Ceilings | 75%
Floors | 65%

## Slide 69: The firefighting systems that we used: 1.sprinkler suppression system 2.fire extinguisher(Co2&Helium) auxiliary system) )3.Hose station

## Slide 70
Fire plan for Ground floor

## Slide 71
Evacuation plans

## Slide 72
Evacuation plan
for Ground floor

## Slide 73
Evacuation plan
for First floor

## Slide 74
Evacuation plan
for second floor

## Slide 75
Evacuation plan
for Third floor

## Slide 76
Evacuation plan
for Fourth floor

## Slide 77
Tilt angle=27
Area available =1800 m²
Initial Cost for PV system.=180,000$
Monthly production =22,500 Kwh
Price per kwh=0.43 NIS
FOR PV system:

## Slide 78
The payback period =6.6 years
= 6 years&7 month
Total Present worth of energy 407566.99 NIS=saving

## Slide 79
Pv-distribution plan

## Slide 80: Quantity surveying

## Slide 82
Quantity surveying
Unit cost (NIS/m2) | Total cost (NIS) | Item
598.22 | 12,276,626.88 | Structural work
61.73 | 1,266,760.40 | Mechanical work
7.20 | 147,680.00 | Electrical work
31.38 | 644,000.00 | Environmental work
698.52 | 14,335,067.28 | Total cost of building

## Slide 83: Life cycle cost analysis

## Slide 84
Present Value (PV) | Future value | Year
331390.76 | 347960.3 | 1
315610.25 | 347960.3 | 2
300581.19 | 347960.3 | 3
286267.80 | 347960.3 | 4
272636.00 | 347960.3 | 5
259653.33 | 347960.3 | 6
247288.89 | 347960.3 | 7
235513.23 | 347960.3 | 8
224298.31 | 347960.3 | 9
213617.44 | 347960.3 | 10
203445.18 | 347960.3 | 11
193757.32 | 347960.3 | 12
184530.78 | 347960.3 | 13
175743.60 | 347960.3 | 14
167374.85 | 347960.3 | 15
159404.62 | 347960.3 | 16
151813.93 | 347960.3 | 17
144584.69 | 347960.3 | 18
137699.71 | 347960.3 | 19
131142.58 | 347960.3 | 20
124897.69 | 347960.3 | 21
118950.18 | 347960.3 | 22
113285.89 | 347960.3 | 23
107891.32 | 347960.3 | 24
102753.64 | 347960.3 | 25
Annual energy recurring cost
= 95 kWh/m². year *8518 m²* 0. 43 NIS/kWh =347,960.3 NIS
# Annual energy consumption=95 kWh/m²
Life cycle cost analysis for our design

## Slide 85
Life cycle cost analysis for our design
# Design and construction cost =14,335,067.28 NIS
# Annual energy recurring cost=347960.3 NIS
# Net present for energy value =4904133.18 NIS
# LCC = Construction cost + PV (Energy cost) =
= 14,335,067.28 +4904133.18
=19,239,200.46 NIS
= 5,419,493.1 $