## Slide 1
PROJECT NAME:
“Mechanical System for school of optical” (An-Najah university College)
Prepared by:
Abdulla Alawneh
Islam Salahat
Mohammed Jaber
Majdi Shwawra

## Slide 2: INTRODUCTION:
The aim of our project is to design installation of heating, ventilation and air condition system (HVAC) for the school of optical which will be built in Nablus city / Palestine. The school consist of six floors, two floor up the ground, three basement and aground. There are different rooms inside the building .

## Slide 3: Building’s Description
Location
Country : Palestine / west bank .
City: Nablus.
Street Al_Jonead Nablus .
Elevation : 569.45 m above sea level
Latitude: 32N
Longitude : 35 E
Building face sits at north orientation.
The wind speed in Nablus above 5 m/s

## Slide 4: nORTH east elevation:

## Slide 5: Results: heating
Floor No. | Heating Load (Kw) | Heating Load (TON) | Heating Load (CFM)
Basement 3 | 73.7 | 21.0 | 8422.8
Basement 2 | 60.9 | 17.4 | 6960.0
Basement 1 | 79.6 | 22.7 | 9097.1
Ground Floor | 75.6 | 21.6 | 8640.0
First Floor | 82.7 | 23.6 | 9451.4
Second Floor | 95.3 | 27.2 | 10891.4
Total heating load | 467.8 | 133.6 | 53462.8

## Slide 6: Cooling:
Floor No. | Cooling Load (Kw) | Cooling Load (TON) | Cooling Load (CFM
Basement 3 | 80.1 | 22.9 | 9160.4
Basement 2 | 103.2 | 29.4 | 11798.7
Basement 1 | 116.3 | 33.2 | 13293.4
Ground Floor | 90 .0 | 25.7 | 10285.7
First Floor | 76.0 | 21.7 | 8685.7
Second Floor | 65.0 | 18.5 | 7428.5
Total Cooling load | 507 | 145 | 60652.7

## Slide 7
AUTOCAD DRAWING

## Slide 8: Data of designing drainage system
Floor No. | Fixture Units
Basement 2 | 125
Basement 1 | 158
Ground Floor | 117
First Floor | 120
Second Floor | 100
Total | 620
The main Bulding Drain is 6 in.
And the size of stack as in table is 4 in .

## Slide 9
AUTOCAD DRAWING

## Slide 10: Demand of potable water system
Floor No. | Fixture Units
Basement 3 | 105
Basement 2 | 109
Basement 1 | 99
Ground Floor | 96
First Floor | 94
Second Floor | 98
Total | 601
Total NO of F.U =601 F.U, From table no 3.3 the total demand is 170 gpm.
    The cold water demand = 170 × 0.75 = 127.5 GPM
    The hot water demand = 170 × 0.25 = 42.5 GPM.
-Domestic water =8.7 kw.
-Flush water tank 380 f.u = 105 gpm.
-Domestic water tank 221 f.u =70 gpm = 70*0.25= 17.5 GPM = 3.97 m3/h

## Slide 11
AUTOCAD DRAWING

## Slide 12: Fire system
In our project we use the fire hose cabinet which distributed in each floor such as each cabinet cover (15 m) with 50 gpm.
And we use Carbon Dioxide (CO2) extinguishers Dry chemical Extinguishers.

## Slide 13
AUTOCAD DRAWING

## Slide 14: EQUIPMENTS SELECTION
Fan Coil Units Selection
In Our project we used Ducted FCU or Room air from Petra catalogs is CBP type or P as shown in the code.
Chiller Selection
- The Total sum of cooling load = 508 KW = 145 Ton
So we select 150 ton R 134-a chiller it’s manufactured with three compressors and with the same compressors type.
The Chiller code is: W P S a 150 2 S

## Slide 15: Boiler Selection and Ignition flame
- The Boiler is selected from Lamborghini company, the catalog of Lamborghini company is used to selections depending on the Total sum of Heating load total in KW
Total heating = Q)Heating load 514 kw +Q)domestic
= 514+8.7 = 522 KW
Q) Boiler total =1.1*522.7= 575 KW
-from Lamborghini company catalogs we choose boiler and ignition flame, are
1- BIG –FK 650
2- ECO70 /2

## Slide 16: PUMP SELECTION
The pumps is selected from WILO Company, by using programe:
Description of PUMP | Flow rate | Head H (m) | TYP OF PUMP
FLUSH | 105(gpm) | 120 | COR-2MVIE5205/VR
DOMESTIC | 70(gpm) | 120 | COR-2MVIE9504/ER-PN16
FIRE | 600 (L/S) | 120 | SCP 400/660DV
CHILLER | 5.5(L/S) | 120 | NL 40/315
HEATING | 8.5(L/S) | 120 | NL 50/315

## Slide 17
THE END