## Slide 1
An-Najah National University
Faculty of Engineering and Information Technology
Building Engineering
Graduation Project (2)
" integrated design for Nablus municipality building "
Prepared by:
Sally Mahamdeh
Abed Allateef Rabaya
Saja Salem
Supervisor Name: Eng. Moayad Salhab
2021/2022

## Slide 2
Architectural Aspects
Environmental
Aspects
Site Analysis
Introduction
Content

## Slide 3
Electrical Aspects
Quantity surveying
Content
Structural
Aspects
Mechanical Aspects

## Slide 4
Introduction
Nablus municipality on Yaffa Street
The main objective of this project is to study and analyze the building to
Reach an integrated design and nearly zero energy building

## Slide 5
Site analysis
Site Analysis
content

## Slide 6
The building is located on a 3250 square meters of land and is supposed to be designed inside Nablus - Yaffa Street.
And it is located on longitude 35.25° and latitude 32.22°

## Slide 7
Climatic conditions

## Slide 8
Architectural aspect
content

## Slide 9
Basement 1 floor after
Basement floor before
Architectural modification
Our project contain one basement floor
35 parking spaces

## Slide 10
Basement 2 floor after
Architectural modification

## Slide 11
Ground floor before
Ground floor after
No main entrance
Emergency stair & Road for the disabled
public service hall

## Slide 12
Fist Floor Before
First Floor After
Connected bridge
Bidding room

## Slide 13
Second Floor Before
Second Floor After

## Slide 14
Third Floor Before
Third Floor After
archive rooms and conference rooms.

## Slide 15
Fourth Floor Before
Fourth Floor After
Emergency ladder

## Slide 16
3D model after modification
After
After

## Slide 17: North Elevation
Elevations and sections after modification
East Elevation

## Slide 18
West Elevation
South Elevation

## Slide 19: Section A-A
Section B-B

## Slide 20
Environmental Aspect
content

## Slide 21: The important parameter of environmental assessment
Environmental Adjustments
PV Design
Acoustical design
Daylight factor
content
Energy Simulation and Thermal Comfort

## Slide 22: Environmental Adjustments

## Slide 23: Daylight analysis
Ground Floor

## Slide 24
First Floor

## Slide 25
Second Floor

## Slide 26
Third Floor

## Slide 27
Fourth Floor

## Slide 28: Energy Simulation and thermal comfort
External Wall Without Insulation
U-value = 2.207 W/m^2.K
External Wall With Insulation
U-value = 0.359 W/m^2.K
Material Properties

## Slide 29: Energy Simulation and thermal comfort
Flat Roof Without Insulation
U-value = 1.75 W/m^2.K
Flat Roof With Insulation
U-value = 0.298 W/m^2.K
Material Properties

## Slide 30: Energy Simulation and thermal comfort
Internal Partitions
U-value = 2.31 W/m^2.K
Under Ground Wall
U-value = 2.68 W/m^2.K
Material Properties

## Slide 31: Energy Simulation and thermal comfort
Glazing Area U-value = 1.63 W/m^2.K
Material Properties

## Slide 32: Energy Simulation and thermal comfort
Thermal analysis
Case | Description | Heating Load(kW) | Cooling Load(kW) | Load/Area(w/m2)
Case 1 | Without Insulation | 979.32 | 322.62 | 75.53
Case 2 | With Insulation | 110.52 | 126.71 | 40.2

## Slide 33
Heating load
Heating Load = 110.52 kW

## Slide 34
Cooling load
Cooling Load = 126.71 kW

## Slide 35
Thermal Comfort
Thermal Comfort for Building
predicted mean vote

## Slide 36
Thermal Comfort
 | Facility [Hours]
Time Setpoint Not Met During Occupied Heating | 12.83
Time Setpoint Not Met During Occupied Cooling | 145.33
Time Not Comfortable Based on Simple ASHRAE 55-2004 | 1026.50

## Slide 37
Energy Consumption
 | Total Energy [kWh] | Energy Per Total Building Area [kWh/m2]
Without Insulation | 335514.6 | 113.62
With Insulation and Environmental Adjustments | 129173.897 | 39.37

## Slide 38
Energy Consumption
Chart: Consumption kWh
| Heating | cooling | Interior Lighting | Interior Equipment
Sales | 15550.9 | 36589.65 | 25912.3 | 22182.88

## Slide 39: Acoustical analysis
The spaces that were designed acoustically in the faculty
1) Office
2) Fees collection hall
3) Multipurpose hall
The absorption coefficient for the element

## Slide 40: Reverberation time (RT60)
The reverberation time for the fees collection hall
Frequency | 125 Hz | 250 Hz | 500 Hz | 1000 Hz | 2000 Hz | 4000 Hz
RT 60 (Second) | 1.65 | 1.5 | 1.43 | 1.21 | 1.15 | 1
The Standard 0.4 to 1.8 second
All reverberation time at all frequency are ok.
The reverberation time for the multipurpose hall
The Standard 0.4 to 1.8 second
Frequency | 125 Hz | 250 Hz | 500 Hz | 1000 Hz | 2000 Hz | 4000 Hz
RT 60 (Second) | 1.55 | 1.51 | 1.45 | 1.39 | 1.36 | 1.35
Frequency | 125 Hz | 250 Hz | 500 Hz | 1000 Hz | 2000 Hz | 4000 Hz
RT 60 (Second) | 2.41 | 2.30 | 2.15 | 2.0 | 1.82 | 1.68
Reverberation time at all frequency are not ok,
So we need an acoustic treatment for this space.

## Slide 41: Sound Transmission loss (STC)
The sound transmission loss (STC) for the internal walls between different spaces
The OITC for the external walls =58 dB more than the required = 55 dB , so it is ok for the external walls.
* Sound transmission loss
* STC and transmission loss

## Slide 42: Impact Insulation Class (IIC)
The impact insulation class for the floor =65 dB more than the IIC required = 60 dB , so it is ok.
* Impact sound level for the floor

## Slide 43: Loud Speaker
The speaker type: AFMG CM20T 2WAY speaker
Multipurpose hall
The direct SPL distribution in the multipurpose hall

## Slide 44: PV-System
Specific photovoltaic power output | PVOUT_specific | 1792 | kWh/kWp
Direct normal irradiation | DNI | 2198 | kWh/m²
Global horizontal irradiation | GHI | 2032 | kWh/m²
Diffuse horizontal irradiation | DIF | 601 | kWh/m²
Global tilted irradiation at optimum angle | GTI_opta | 2254 | kWh/m²
Air temperature | TEMP | 18.4 | °C
Optimum tilt of PV modules | OPTA | 28 | °
Terrain elevation | ELE | 555 | m

## Slide 45: PV-System
E | 129173.897 | kWh/Year
E | 353.901088 | kWh/day
G | 6.1 | Hr./Day
Efficiency | 0.7 | -
System Size | 83.90 | kWp
Wpv | 480 | Wp
No. of Module | 174.79 | Module
E | 129173.897 | kWh/Year
Yearly Total | 1792 | kWh/kWp
System Size | 72.08 | kWp
Wpv | 480 | Wp
No. of Module | 150.17 | Module
We chose the smallest number, which is 150, but it has resulted from the design that 154 cells are required

## Slide 46: PV-System
Results for parking cover

## Slide 47: PV-System
Results for Roof

## Slide 48: PV-System
Monthly Production for Roof
Monthly Production for Parking cover

## Slide 49: PV-System
Parking cover
Shadow

## Slide 50
Structural Aspect
content

## Slide 51
Marital, Codes & Loads
Material
Concrete with compressive strength of 28 MPa
Steel rebar with yielding strength of 420MPa
Design Codes
ACI 318-14, ( Building Code Requirements for Structural Concrete )
Seismic design UBC 97 ( Uniform Building Code )
ASCE 7 for load design (American Society of Civil Engineers )
Loads
Live 5 KN/m²
SID 4.266 kN/m²
EQ Loads (UBC97):
I= 1 (Importance factor)
Cv=0.4 (Seismic coefficient )
R= 5.5 (Response modification)
Ca=0.28 (Seismic coefficient )
Z= 0.2 (Seismic zone factor)
Ct= 0.0488 (Seismic coefficient )

## Slide 52
The structural system use two way voided slab ( U-Boot slab)
We divided the building into three blocks {Block A, Block B, Block C}, taking into account the seismic design.

## Slide 53
Checks
Compatibility check
Equilibrium check
Stress σ & Strain ɛ check
Period check
Modal mass participation
ratio check
Base shear check
Drift check
P−∆ Effects check
Structural analysis

## Slide 54
Thickness of slab for all blocks = 40 cm according shear check .

## Slide 55
Compatibility check
For block A
For block C
For block B

## Slide 56
Equilibrium Checks
For block A
For block C
For block B
Loads (KN) | manual | Etabs | %Error
Dead | 24697.51 | 24422.05 | 1.128
Live | 10630.58 | 10631.45 | 0.008
SID | 9586.806 | 9587.475 | 0.007
Loads (KN) | manual | Etabs | %Error
Dead | 14324.89 | 14069.77 | 1.813
Live | 8859.9 | 8860.79 | 0.010
SID | 7659.744 | 7660.502 | 0.010
Loads (KN) | manual | Etabs | %Error
Dead | 15107.75 | 15238.17 | 0.856
Live | 7123.04 | 7123.337 | 0.004
SID | 6405.599 | 6405.337 | 0.004

## Slide 57
Internal forces checks
For edge column
Loads (KN) | manual | Etabs | %Error
Dead | 1906.87 | 1843.68 | 3.43
Live | 955.55 | 905.19 | 5.56
SID | 859.96 | 811.62 | 5.96
Axial force manual |  | 
Dead | Live | Sid
1906.87 | 955.55 | 859.96
Axial force Etabs |  | 
Dead | Live | Sid
1843.68 | 905.19 | 811.62

## Slide 58
Period check.
TB = 0.764 sec.
TA = Ct (hn) ^ (¾)
TA = 0.0488 (27) ^ (¾)=0.57 sec
1.4 TA = 0.79 sec.
TB ≤ 1.4 TA so the check is ok.
For Block A

## Slide 59
Modal mass participation ratio check.
sum UX= 0.9008.
sum UY= 0.952.
sum of UX and UY ≥ 0.9 so the check is ok.
For Block A

## Slide 60
Base shear check.
EQX main = 3391.75 KN
EQY main = 3423.61 KN
EQ ≥ V its ok.
For Block A
soil | SD
I | 1
Ca | 0.28
Cv | 0.4
R | 5.5
Ω | 2.8
Ct | 0.0488
hn | 27
Ta | 0.578
1.4Ta | 0.809
Tetabs | 0.76
w | 35324.83
Vmain | 3380.366
Vsecondry | 1126.789

## Slide 61
Drift check.
max δx inelastic ≥ δx inelastic : 50 ≥ 4.68 mm , so it ok
For Block A
Drift in X |  |  |  |  |  |  | 
#of story | R | H floor (mm) | T structure (second) | δx elastic (mm) | total δx inelastic(mm) | max. δx inelastic(mm) | Result
9 | 5.5 | 2500 | 0.76 | 24.459 | 4.68545 | 50 | safe
8 | 5.5 | 3700 | 0.76 | 23.242 | 8.90505 | 74 | safe
7 | 5.5 | 3700 | 0.76 | 20.929 | 15.7157 | 74 | safe
6 | 5.5 | 3700 | 0.76 | 16.847 | 17.9949 | 74 | safe
5 | 5.5 | 3700 | 0.76 | 12.173 | 17.9872 | 74 | safe
4 | 5.5 | 3700 | 0.76 | 7.501 | 15.11125 | 74 | safe
3 | 5.5 | 3700 | 0.76 | 3.576 | 13.7676 | 74 | safe
2 | 5.5 | 2500 | 0.76 | 0 | -1.64395 | 50 | safe
1 | 5.5 | 2500 | 0.76 | 0.427 | 1.64395 | 50 | safe
Drift in Y |  |  |  |  |  |  | 
#of story | R | H floor (mm) | T structure (second) | δy elastic (mm) | Total δy inelastic(mm) | max. δy inelastic(mm) | Result
9 | 5.5 | 2500 | 0.76 | 15.419 | -32.1552 | 50 | safe
8 | 5.5 | 3700 | 0.76 | 23.771 | 13.7214 | 74 | safe
7 | 5.5 | 3700 | 0.76 | 20.207 | 17.23645 | 74 | safe
6 | 5.5 | 3700 | 0.76 | 15.73 | 18.04495 | 74 | safe
5 | 5.5 | 3700 | 0.76 | 11.043 | 17.0016 | 74 | safe
4 | 5.5 | 3700 | 0.76 | 6.627 | 13.33255 | 74 | safe
3 | 5.5 | 3700 | 0.76 | 3.164 | 12.1814 | 74 | safe
2 | 5.5 | 2500 | 0.76 | 0 | -2.66805 | 50 | safe
1 | 5.5 | 2500 | 0.76 | 0.693 | 2.66805 | 50 | safe
max δx inelastic ≥ δx inelastic : 50mm ≥ 32.155mm, so it is ok.

## Slide 62
P−∆ Effects check.
θx = (P X Ux)/(Ex X H)=0.0015 0.1 so its ok .
For Block A
θy = (P X Uy)/(Ey X H)=0.0072 ≤ 0.1 so its ok .
P-Delta -EQX |  |  |  |  |  |  | 
#of story | H floor (mm) | P gravity load combination(KN) | Ex (KN) | Ux (mm) | ∆X (mm) | ƟX | Result
9 | 2500 | 424.5652 | 157.59 | 25.568 | 1.471 | 0.00158525 | NO P-DELTA
8 | 3700 | 4201.0749 | 936.85 | 24.097 | 2.487 | 0.00301416 | NO P-DELTA
7 | 3700 | 9296.7837 | 1802.2 | 21.61 | 4.256 | 0.00593391 | NO P-DELTA
6 | 3700 | 14392.5035 | 2418.8 | 17.354 | 4.837 | 0.00777864 | NO P-DELTA
5 | 3700 | 19488.2235 | 2871.6 | 12.517 | 4.811 | 0.00882421 | NO P-DELTA
4 | 3700 | 24485.2776 | 3186.7 | 7.706 | 4.022 | 0.0084 | NO P-DELTA
3 | 3700 | 28600.2989 | 3344.8 | 3.684 | 3.684 | 0.0085 | NO P-DELTA
2 | 2500 | 30691.6546 | 3371.8 | 0 | -0.4 | 0.0015 | NO P-DELTA
1 | 2500 | 35011.993 | 3391.8 | 0.402 | 0.402 | 0.0017 | NO P-DELTA
P-Delta -EQY |  |  |  |  |  |  | 
#of story | H floor (mm) | P gravity load combination(KN) | EY (KN) | Uy (mm) | ∆y (mm) | ƟY | Result
9 | 2500 | 424.5652 | 111.36 | 16.014 | -4.75 | 0.0072394 | NO P-DELTA
8 | 3700 | 4201.0749 | 907.95 | 20.761 | 2.605 | 0.00325767 | NO P-DELTA
7 | 3700 | 9296.7837 | 1772.4 | 18.156 | 3.729 | 0.00528653 | NO P-DELTA
6 | 3700 | 14392.5035 | 2402.4 | 14.427 | 4.06 | 0.00657384 | NO P-DELTA
5 | 3700 | 19488.2235 | 2862 | 10.367 | 3.923 | 0.00721966 | NO P-DELTA
4 | 3700 | 24485.2776 | 3175.8 | 6.444 | 3.412 | 0.0071 | NO P-DELTA
3 | 3700 | 28600.2989 | 3344.3 | 3.032 | 3.032 | 0.0070 | NO P-DELTA
2 | 2500 | 30691.6546 | 3379.8 | 0 | -0.48 | 0.0017 | NO P-DELTA
1 | 2500 | 35011.993 | 3423.6 | 0.476 | 0.476 | 0.0019 | NO P-DELTA

## Slide 63
Structural analysis
Detailing:
Slab details

## Slide 64
Structural analysis
Detailing:
Columns details.

## Slide 65
Structural analysis
Detailing:
Columns details.

## Slide 66
Structural analysis
Detailing:
Shear wall details.

## Slide 67
Structural analysis
Detailing:
Single Footing details.

## Slide 68
Structural analysis
Detailing:
Single Footing details.

## Slide 69
Structural analysis
Detailing:
Matt Footing details.

## Slide 70
Structural analysis
Detailing:
Matt Footing details.

## Slide 71
Water Tank details

## Slide 72
Water Tank details

## Slide 73
Basement wall details

## Slide 74
Electrical design
content

## Slide 75
Socket distribution
Artificial lighting
board distribution and low voltage
Electrical design

## Slide 76
The electrical load of power, lighting in the ground floor
Sockets plan for the fees collection hall
The electrical symbols
Distribution of the circuit breaker in distribution board 1
Main distribution board of circuit breaker in the ground floor

## Slide 77
The electrical load of power, lighting in the main distribution board 1
The electrical load of elevators and HVAC system in the main distribution board
The main distribution board for the faculty
The system UPS in the Ground Floor
The main UPS distribution board 1
HVAC and Elevator |  |  |  |  |  |  |  |  | 
Main DB | M.D.B | Normal load | Light load | Total power | I load | I C.B | I cable | C.B | Cable (IEC )
3 phases | H-VAC C.B | Total load |  | 28000.00 | 44.91 | 51.64 | 59.39 | 63 | (77A) , 25 mm^2
3 phases | Elevators C.B | Total load |  | 44000.00 | 70.57 | 81.15 | 93.32 | 100 | (117A) , 50 mm^2
3 phases | M.D.B | Total load |  | 72000.00 | 115.47 | 132.79 | 152.71 | 160 | (180A) , 95 mm^3

## Slide 78
First Floor
Electrical Plan
Electrical power distribution of spaces

## Slide 79
Electrical Plan
Third Floor
Electrical power distribution of spaces

## Slide 80
Artificial lighting
multipurpose hall

## Slide 81
Artificial lighting
Mayor office

## Slide 82
Artificial lighting
Meeting room

## Slide 83
Mechanical design
content

## Slide 84: Mechanical design
Water system
Fire Fighting
Drainage system
content
HVAC system

## Slide 85: Water System
Water Tanks
Distribution tanks

## Slide 86
Total FU | Floor
65 | Ground Floor
56 | First Floor
56 | Second Floor
56 | Third Floor
34 | Fourth Floor
267 | Total
Total Fu
Water supply system distribution

## Slide 87: Drainage system
Diameter of pipe(Inch) | Slope | Material pipe | Type fixture
4" | 1.00% | PVC | Stack
2" | 1.00% | PVC | Sewer
4" | 0.00% | PVC | Vent
6" | 1.00% | PVC | Between Manhole
Summary for diameter and pipe slop
Water drainage system distribution

## Slide 88
Drainage pipe and Manhole on the site
Manhole on the site
Drainage system

## Slide 89: HVAC system
From the Design Builder program:
Total Heating Load = 112.03 kW.
Total Cooling Load = 113.81 kW.
Total Flowrate = 6.65 /s
content

## Slide 90: Distribution of Indoor unit in ground floor.

## Slide 91: Distribution of Indoor unit in first floor.

## Slide 92: Distribution of Indoor unit in third floor.

## Slide 93: Fire Fighting System:

## Slide 94
Fire Fighting System:

## Slide 95
Fire Fighting System:

## Slide 96
Quantity surveying
& Cost Estimate
content

## Slide 97: The total cost of the project is 12105301 ₪ , And the unit cost is 1931.1 ₪/m2
Percentage % | Unit Cost (Nis/SM) | Budget Cost | Work
13.8 | 267.3 | 1675312 | Sub-Structure
20.3 | 392.6 | 2461008 | Super Structure
24.4 | 471.5 | 2955836 | Finishing
18.9 | 364.4 | 2284205 | Mechanical Work
5.8 | 111.7 | 700343 | Electrical Work
16.8 | 323.6 | 2028599 | Details
100.0 | 1931.1 | 12105301 | Total Budget Cost
Project cost

## Slide 98
Thank you
content