## Slide 1
An-Najah National University Hospital
Engineering College
Graduation Project II
Prepared by : Jamila Bani Odeh
Safaa’ Abu Qassidu
Somaya Yaseen
Submitted to : Dr . Imad Al-Qasem

## Slide 2: Contents
Overview
Elements of Structural System
Materials
Computer Programs Used
Design Codes
Loads
Combinations
Preliminary Design
3-D Model Analysis
Seismic loads
Columns Design
Foundation Design

## Slide 3: Overview
An-Najah National University Hospital which is located in Assira Street in Nablus. The project have a three blocks (A, B and C) which consist of a five basements, and ground floor.

## Slide 4: Overview
The hospital consists of one ground floor and five basements

## Slide 5: Overview

## Slide 6: Elements of Structural System
Each structural system consists of main structural elements as follows:
1) Slabs (Two way solid slab).
2) Beams (Drop Beams, T- section).
3) Columns (Short Columns).
4) Footings (Single and Strip footings).

## Slide 7: Materials
Concrete
The values of compressive strength (f'c) were used in the project is 24 MPa for beams and slabs and 28 MPa for columns and footings
.
-Reinforcement Steel
Fy: Yielding strength = 420 MPa

## Slide 8: Computer Programs Used
SAP2000 used to modeling the building using equivalent depth of slabs and make checks then the results will be taken for design . Also, AutoCAD will be used to get out the design as a drawings and ready for execution

## Slide 9: Design Codes
1-American concrete institute code according to 2008 updating (ACI-318-08) .
2-UBC-97 (Uniform Building Code).

## Slide 10: Loads
Gravity Loads , which include :
*Dead Loads :
-Own weight of the structure.
-super imposed dead load (SID).
Live Loads :
-Human being.
-Furniture

## Slide 11: Combinations
1) Wu = 1.4DL
2)Wu = 1.2DL + 1.6LL
3)Wu = 0.9DL +1 EL + or – 1.6WL
4)Wu = 1.2DL +1 EL +1 LL + or – 1.6 WL
5)Wu = 1.2DL +0.5 LL + 1.6 SL

## Slide 12: Preliminary Design
Block B

## Slide 13: Preliminary Design

## Slide 14: Preliminary Design
Determining thickness of slab
We used h slab = 0.25 m =25 cm.

## Slide 15: Preliminary Design
Design of beam (preliminary dimension):
we used h Beam =750 mm.
by using b w =400 mm , clear transvers span =7.5 – 0.6 = 6.9 m (columns are 600*600 mm).

## Slide 16: Preliminary Design

## Slide 17: Preliminary Design
Assume then :
.

## Slide 18: Preliminary Design
Design frames in X – Direction:

## Slide 19: Preliminary Design
Live load on slab = 5 KN/m2

## Slide 20: Preliminary Design

## Slide 21: Preliminary Design

## Slide 22: Preliminary Design
Check the slab for shear :

## Slide 23: Preliminary Design

## Slide 24: Preliminary Design

## Slide 25: Preliminary Design
According to ACI -318 tables :

## Slide 26: Preliminary Design
Design beam for shear
Own weight of beam =0.4*0.5*25*1.2 =6 KN/m.
Wu =7.5*20.048 =150.36 KN/m.

## Slide 27: Preliminary Design
=
=
=
Beam size is OK.

## Slide 28: Preliminary Design
Design beam for shear
After calculations that shown in the report we obtained the following result:

## Slide 29: Preliminary Design
Column strip

## Slide 30: Preliminary Design
Positive moment = 514.36 KN.m
Negative moment = 693.05KN.m

## Slide 31: Preliminary Design
Top steel :
Bottom steel :

## Slide 32: Preliminary Design
Middle Strip

## Slide 33: Preliminary Design
Positive moment = 171.45 KN.m
→ .
Negative moment = 231KN.m
.

## Slide 34: Preliminary Design
Top steel :
Bottom steel :

## Slide 35: Preliminary Design
Moment of Beam

## Slide 36: Preliminary Design
Negative moment : Mu=589.1 KN.m

## Slide 37: Preliminary Design
Positive Moment Mu=437.21 KN.m

## Slide 38: Preliminary Design
Top Steel :
Bottom Steel :

## Slide 39: 3-D Model Analysis
Block A

## Slide 40: 3-D Model Analysis
Checks for 3D –modal
Compatibility check: OK
Equilibrium check :
Area = 3838.83 m2
**Dead load(manual ) = .
**live load (manual)= 3838..82*5 =19194.112 KN
** superimposed (manual) =3838.82* 3.79 =14549.12 KN

## Slide 41: 3-D Model Analysis
Loads from SAP

## Slide 42: 3-D Model Analysis
%of error (Dead load) =3.69 % < 5% OK
%of error (live load) = 4 % OK
%of error (superimposed) =4 % OK

## Slide 43: 3-D Model Analysis
Stress – strain relationships :
Mu(manual) = .
:** Mu ( From SAP)
% of error =7.11 % < 10% OK

## Slide 44: 3-D Model Analysis
Deflection check:
** from live load
From SAP :
Deflection from live load = 10.69 mm < 21 mm→ OK

## Slide 45: 3-D Model Analysis
from service load(Dead + Live)
Deflection from SAP :
Deflection from service load = 30.89 mm < 31.25 mm OK

## Slide 46: 3-D Model Analysis
Period :
T= 0.326 sec < 2 sec OK.

## Slide 47: 3-D Model Analysis
Block B(part 1) :

## Slide 48: 3-D Model Analysis
Checks for 3D –modal :
Compatibility check: OK
Equilibrium check:
Area = 2485.47 m2
** dead load =
**live load (manual)= 2485.47*5 =12427.35 KN
** superimposed (manual) =2485.47* 3.79 =9419.931 KN

## Slide 49: 3-D Model Analysis
Loads From SAP :

## Slide 50: 3-D Model Analysis
%of error (Dead load) =1% < 5% OK
%of error (live load) = 0% OK
%of error (superimposed) =0% OK

## Slide 51: 3-D Model Analysis
Stress – strain relationships:
Mu ( From SAP ) :
% of error =6% < 10% OK .

## Slide 52: 3-D Model Analysis
Deflection check
** from live load :
.
Deflection from SAP :
Deflection from live load = 7.5mm < 21 mm OK

## Slide 53: 3-D Model Analysis
** from service load(Dead + Live)
.
From SAP :
Deflection from service load = 23.74 mm < 31.25 mm OK

## Slide 54: 3-D Model Analysis
Period :
T = 0.745 sec < 2 sec OK.

## Slide 55: 3-D Model Analysis
Block B(part 2):

## Slide 56: 3-D Model Analysis
Block C :

## Slide 57: 3-D Model Analysis
Checks for 3D –modal :
Compatibility check → OK
Equilibrium check :
Area =5793.17 m2
** Dead load ( Manual ) = .
** Live load (manual)= 5793.17*5 =28965.9 KN
** Superimposed (manual) =5793.17* 3.79 =21956.1 KN

## Slide 58: 3-D Model Analysis
Loads From SAP :

## Slide 59: 3-D Model Analysis
%of error (Dead load) =4.5% < 5% OK
%of error (live load) = 5.3% OK
%of error (superimposed) =5.3% OK

## Slide 60: 3-D Model Analysis
Stress – strain relationships
Mu(manual) =
Mu (from SAP):
% of error =7% < 10% OK .

## Slide 61: 3-D Model Analysis
Deflection check:
** from live load
Deflection from SAP:
Deflection from live load =0.454 mm < 23 mm OK

## Slide 62: 3-D Model Analysis
from service load(Dead + Live) :
Deflection from SAP :
Deflection from service load =2.01 mm < 33.8 mm → OK .

## Slide 63: 3-D Model Analysis
Period :
T = 0.23203 sec < 2 sec OK .

## Slide 64: Seismic loads
Seismic load will be calculated depending on UBC-97. According to the location of this project (Nablus), soil type (rock) and according to Palestine seismic map
For our project seismic zone is 2B thus the value of zone factor is (Z=0.2).

## Slide 65: Seismic loads

## Slide 66: Seismic loads
Determination of structure period (Block B):
Ct = 0.0488
hn= 22.57 m
T= 0.505 sec.

## Slide 67: Seismic loads
Determination of base shear :
W= the total seismic dead load
I= the importance factor =1.25
R= the response modification =5.5
Cv = seismic coefficient = 0.2
0.09 w

## Slide 68: Seismic loads
Ca= seismic coefficient =0.2
0.0275 W< V < 0.114 W → OK

## Slide 69: Seismic loads
Vertical component of seismic load:
shall not be taken less than 1.0 and need not be greater than 1.5. When calculating drift, or when the structure is located in Seismic Zone 0,1 or 2, shall be taken equal to 1.
Eh= the earthquake load due to the base shear, v.
Ev= the load effect resulting from the vertical component of the earthquake ground motion and is equal to an addition of o.5CaID to the

## Slide 70: Seismic loads
Response spectrum :

## Slide 71: Seismic loads
Response spectrum:
R=5.5 ( Sway Intermediate )

## Slide 72: Seismic loads
First we define function of earthquake (response spectrum UBC-97).

## Slide 73: Seismic loads
Then we define load pattern .

## Slide 74: Seismic loads
Then we define load cases :

## Slide 75: Seismic loads

## Slide 76: Columns Design
*Columns grouping (Block A):
Group number | Column number | Axial force range (KN)
1 | C1,C2,C4,C6,C7,C8,C9 | 100-600
2 | C3 | 600-1000
3 | C5,C15 | 1000-2000
4 | C11,C12,C13,C14,C18,C19,C21 | 2000-3000
5 | C10,C16,C17,C20 | 3000-5000

## Slide 77: Columns Design
check buckling
slenderness effects shall be permitted to be neglected in the following cases:
For compression members not braced against sideway when:
For compression members braced against sideway when:

## Slide 78: Columns Design
In this structure, columns are braced then the second equation will be used
K= 0.57, using figure (R10.10.1.1) in ACI-318-11
Lu: Unbaked length of the column = 4
r= Radius of gyration for cross section of column.

## Slide 79: Columns Design
M1: the smaller design end moment on the column.
M1= 0.7469 KN.m
M2: the larger design end moment on the column.
M2 = 8.6233 KN.m
→ the column is short and slenderness can be neglected.

## Slide 80: Columns Design
Column number 5 from group 3 (in Block A) will be taken as a sample
For computing gross area of the column, assume →
Where Pu = 1573.689 KN
As: Area of steel in column, (As=ρ Ag)→ assuming ρ=0.01 then As=0.01 Ag

## Slide 81: Columns Design
→ (330*330)mm
Column dimensions are (400*400)mm
As=0.01* Ag =0.01*(400*400)= 1600mm2
Use 816

## Slide 82: Columns Design
For stirrups, using stirrups with diameter
Use (110/ 200mm).

## Slide 83: Columns Design
Block A
Group# | Critical column # | Pn (KN) | Ag (mm2) | Dimension (mm) | As (mm2) | Reinforcement | Ties (mm)
1 | C2 | 547 | 37851 | (300*300) | 900 | 812 | 110/ 200
2 | C3 | 821 | 56825 | (350*350) | 1225 | 814 | 110/ 200
3 | C5 | 1574 | 108981 | (400*400) | 1600 | 816 | 110/ 200
4 | C14 | 2968 | 205523 | (500*500) | 2500 | 820 | 110/ 200
5 | C16 | 4333 | 300053 | (550*550) | 3025 | 1218 | 110/ 200
Group# | Critical column # | Pn (KN) | Ag (mm2) | Dimension (mm) | As (mm2) | Reinforcement | Ties (mm)
1 | C2 | 547 | 37851 | (300*300) | 900 |  | 
2 | C3 | 821 | 56825 | (350*350) | 1225 |  | 
3 | C5 | 1574 | 108981 | (400*400) | 1600 |  | 
4 | C14 | 2968 | 205523 | (500*500) | 2500 |  | 
5 | C16 | 4333 | 300053 | (550*550) | 3025 |  | 

## Slide 84: Columns Design
Block B (part 1).
Group# | Critical column # | Pn (KN) | Ag (mm2) | Dimension (mm) | As (mm2) | Reinforcement | Ties (mm)
1 | C31 | 599 | 41482 | (300*300) | 900 | 812 | 110/ 200
2 | C13 | 943 | 65305 | (350*350) | 1225 | 814 | 110/ 200
3 | C12 | 1979 | 137050 | (400*400) | 2025 | 816 | 110/ 200
4 | C11 | 3044 | 210803 | (500*500) | 2500 | 820 | 110/ 200
5 | C15 | 6219 | 430679 | (700*700) | 4900 | 1620 | 110/ 200
Group# | Critical column # | Pn (KN) | Ag (mm2) | Dimension (mm) | As (mm2) | Reinforcement | Ties (mm)
1 | C31 | 599 | 41482 | (300*300) | 900 |  | 
2 | C13 | 943 | 65305 | (350*350) | 1225 |  | 
3 | C12 | 1979 | 137050 | (400*400) | 2025 |  | 
4 | C11 | 3044 | 210803 | (500*500) | 2500 |  | 
5 | C15 | 6219 | 430679 | (700*700) | 4900 |  | 

## Slide 85: Columns Design
Block B (part 2)
Group # | Critical column # | Pn (KN) | Ag (mm2) | Dimension (mm) | As (mm2) | Reinforcement | Ties (mm)
1 | C12 | 483 | 33449 | (300*300) | 900 | 812 | 110/ 200
2 | C24 | 943 | 65305 | (350*350) | 1225 | 814 | 110/ 200
3 | C14 | 2125 | 147161 | (400*400) | 2025 | 816 | 110/ 200
4 | C16 | 4431 | 306856 | (600*600) | 3600 | 1220 | 110/ 200
5 | C15 | 7660 | 530471 | (750*750) | 5625 | 1225 | 110/ 200
Group # | Critical column # | Pn (KN) | Ag (mm2) | Dimension (mm) | As (mm2) | Reinforcement | Ties (mm)
1 | C12 | 483 | 33449 | (300*300) | 900 |  | 
2 | C24 | 943 | 65305 | (350*350) | 1225 |  | 
3 | C14 | 2125 | 147161 | (400*400) | 2025 |  | 
4 | C16 | 4431 | 306856 | (600*600) | 3600 |  | 
5 | C15 | 7660 | 530471 | (750*750) | 5625 |  | 

## Slide 86: Columns Design
Block C
Group# | Critical column # | Pn (KN) | Ag (mm2) | Dimension (mm) | As (mm2) | Reinforcement | Ties (mm)
1 | C65 | 784 | 54308 | (300*300) | 900 | 614 | 110/ 200
2 | C47 | 948 | 65668 | (350*350) | 1225 | 814 | 110/ 200
3 | C28 | 1426 | 98779.2 | (400*400) | 1600 | 816 | 110/ 200
4 | C54 | 1976 | 136878 | (450*450) | 2025 | 818 | 110/ 200
5 | C14 | 2040 | 141312 | (450*450) | 2025 | 818 | 110/ 200
Group# | Critical column # | Pn (KN) | Ag (mm2) | Dimension (mm) | As (mm2) | Reinforcement | Ties (mm)
1 | C65 | 784 | 54308 | (300*300) | 900 |  | 
2 | C47 | 948 | 65668 | (350*350) | 1225 |  | 
3 | C28 | 1426 | 98779.2 | (400*400) | 1600 |  | 
4 | C54 | 1976 | 136878 | (450*450) | 2025 |  | 
5 | C14 | 2040 | 141312 | (450*450) | 2025 |  | 

## Slide 87: Foundation Design
In our project we used two type of footing:
Single footing
Strip footing
The combinations that we used to calculate service load on footing :

## Slide 88: Foundation Design
footing grouping
The footings were classified as groups according to the range of the axial loads. As a result, the same groups of the columns were adopted.

## Slide 89: Foundation Design
footing design (Single footing):
Block C
Footing dimension
Use square footing then
Use L=B=1.7m

## Slide 90: Foundation Design
Calculate (d) depending on wide beam shear.
Pu= 1470 KN.

## Slide 91: Foundation Design
Then
d=0.3 m
check punching shear:

## Slide 92: Foundation Design
→
Use h=500 mm →d=430 mm
Then use h=500 mm

## Slide 93: Foundation Design
Sap2000 analysis
*Deflection:

## Slide 94: Foundation Design
*Bearing capacity:
→OK

## Slide 95: Foundation Design
*Check wide beam shear:

## Slide 96: Foundation Design
Vu =279.9 KN (for total width of footing= 1.7 m).
→ OK

## Slide 97: Foundation Design
Check punching shear
.

## Slide 98: Foundation Design
From SAP :
As , punching shear is OK.

## Slide 99: Foundation Design
Flexural design :

## Slide 100: Foundation Design
Bottom steel
Mu=182.1 KN.m

## Slide 101: Foundation Design
Use As= 1146 mm2
Use
Top steel
Use half of the shrinkage steel in each direction
in each direction .

## Slide 102: Foundation Design
Check development length:
→
→ No need to have hook

## Slide 103: Foundation Design
Block A:
Number Of footing | Reinforcement |  | Dimensions |  |  | 
 | Shrinkage steel (top steel) | main steel (bottom steel) | depth(m) | width(m) | length(m) | foundation
7 | 1Ø12/200mm | 1Ø12/150 mm | 0.3 | 1 | 1 | F1
1 | 1Ø12/200 mm | 1Ø12/150 mm | 0.4 | 1.35 | 1.35 | F2
2 | 1Ø12/200mm | 1Ø14/150 mm | 0.5 | 2 | 2 | F3
7 | 1Ø12/200mm | 1Ø18/200 mm | 0.6 | 2.45 | 2.45 | F4
4 | 1Ø12/200 mm | 1Ø18/200 mm | 0.6 | 1.5 | 1.5 | F5

## Slide 104: Foundation Design
Block B (part 1):
Number of footings | reinforcement |  | Dimensions |  |  | 
 | shrinkage steel (top steel) | main steel (bottom steel) | depth(m) | width(m) | length(m) | foundation
4 | 1Ø12/200 mm | 1Ø12/200 mm | 0.3 | 1 | 1 | F1
2 | 1Ø12/200 mm | 1Ø12/150mm | 0.35 | 1.35 | 1.35 | F2
1 | 1Ø12/200mm | 1Ø14/150 mm | 0.5 | 2 | 2 | F3
4 | 1Ø12/200mm | 1Ø16/150 mm | 0.6 | 2.45 | 2.45 | F4
2 | 1Ø12/150 mm | 1Ø20/150 mm | 0.8 | 3.45 | 3.45 | F5
4 | in x:1Ø16/150mm | in x:1Ø18/150mm | 0.7 | 1.6 | 2 | F6
 | in Y:1Ø12/150mm | in Y:1Ø14/150mm |  |  |  | 

## Slide 105: Foundation Design
Block B (part 2):
Number of footings | reinforcement |  | Dimensions |  |  | 
 | shrinkage steel (top steel) | main steel (bottom steel) | depth(m) | width(m) | length(m) | foundation
4 | 1Ø12/200 mm | 1Ø12/200 mm | 0.25 | 1 | 1 | F1
3 | 1Ø12/200 mm | 1Ø12/150mm | 0.35 | 1.4 | 1.4 | F2
4 | 1Ø12/200mm | 1Ø14/150 mm | 0.5 | 1.8 | 1.8 | F3
4 | 1Ø12/150mm | 1Ø18/150 mm | 0.7 | 2.95 | 2.95 | F4
2 | 1Ø14/150 mm | 1Ø20/150mm | 0.9 | 3.85 | 3.85 | F5
6 | in x:1Ø12/150mm | in x:1Ø18/150mm | 0.7 | 1.6 | 2 | F6
 | in Y:1Ø14/150mm | in Y:1Ø14/150mm |  |  |  | 

## Slide 106: Foundation Design
Block C
Number of footing | reinforcement |  | Dimensions |  |  | 
 | shrinkage steel (top steel) | main steel (Bottom steel) | depth(m) | width(m) | length(m) | foundation
7 | 1Ø12/200 mm | 1Ø14/200 mm | 0.5 | 1.4 | 1.4 | F1
8 | 1Ø12/200 mm | 1Ø14/200 mm | 0.5 | 1.5 | 1.5 | F2
9 | 1Ø12/200mm | 1Ø14/200 mm | 0.5 | 1.7 | 1.7 | F3
10 | 1Ø12/200mm | 1Ø14/200 mm | 0.6 | 2 | 2 | F4
10 | 1Ø12/200 mm | 1Ø14/200 mm | 0.6 | 2 | 2 | F5