## Slide 1: Structural Analysis and Design of Jalal Safarini Building in Tulkarem-Palestine
By
Ameed Hythm Hindia
Ghassan Mohammed Ewais
Mo’men Yousef Ashayer
Mohammad Adnan Darwazeh
Under supervision of: Dr. Ibraheem Erman

## Slide 2: Content
Chapter 1: Introduction
Chapter 2: Preliminary design
Chapter 3: Seismic load
Chapter 4: Three dimensional analysis
Chapter 5: Design of structural concrete members

## Slide 3
Project Description
The architectural drawings are shown in Appendix-A.
The modified and structural drawings are shown in Appendix-B.
The building is consisted of six floors (garage at the basement and the other five floors each of them consisted of two apartments), it has a total area about 1400 m2.
Floor | Use of floor | Area (m2) | Height (m) | Repeated Stairs (m2)
Basement | Garage |  | 3.25 | -
Ground to Third floor | Residential |  | 3.25 | -
Fourth floor | Residential |  | 3.25 | 18.27

## Slide 4
Materials
Structural materials
Concrete:
Compressive strength:
f 'c=28 MPa (B350) for columns.
f 'c=24 MPa (B300) for slabs & beams.
Modulus of Elasticity
Unit weight (ɣ)
Reinforcing Steel:
The steel used in this project is Grade-60 which has a yielding stress of 420MPa.
Modulus of elasticity (E)
Unit Weight (ɣ)
200,000 MPa .
(plain concrete , reinforced concrete)
(ɣ) = 77 KN/m3

## Slide 5
Non- Structural materials
Blocks
Tiles
Plastering

## Slide 6
Bonding Agents & Adhesive Products
The most common material in this field is Cetox H
Advantages:
• Bonds strongly on various surfaces as cement or wood.
• Ready to use, easy to apply.
• Can be used as well as a levelling mortar for exterior and interior use before painting.
Is especially suitable for thin bed fixing of ceramic tiles

## Slide 7
False-ceiling
It has a weight of 0.1KN/m2
Material | Unit weight (KN/m3)
Block | 12
Tiles | 24
Plastering | 23
Mortar | 23
Bonding Agents & Adhesive Products | 15

## Slide 8
Soil Properties
The type and characteristics of the soil must be known in order to be able to design the footings by choosing appropriate type and it is also needed for the design of seismic load.

## Slide 9
Codes and Standards
The following codes and standards are used in this study:
ASCE 7-10 (American Society of Civil Engineers).
ACI318-14 (American Concrete Institute):
IBC2015 (International Building Code).
ISRAELI STANDARD SI 413

## Slide 10
Loads
Gravity loads
Dead load
permanent loads that consist of the own weight of the structural members.
superimposed dead loads include the weight of the finishing like the tiles, plastering, cement, blocks and fall-ceiling.

## Slide 11
Floor Slab
For SLAB |  | 
Material | Unit weight (KN/m3) | Thickness (mm)
Block | 12 | 100
Ceramic Tiles | 24 | 15
Bonding Agents & Adhesive Products | 15 | 4
Plastering (for blocks) | 23 | 40
SD = 3.5 KN/m2

## Slide 12
Slab for Staircase
There is only fall-ceiling to be considered as superimposed dead load
Superimposed Dead Load = 0.1 KN/m2
Perimeter Wall
SD = 17.8 KN/m
For Perimeter Wall |  | 
Material | Unit weight (KN/m3) | Thickness (mm)
Block | 25 | 200
Plastering | 23 | 40

## Slide 13
Live load:
For the roof stair case, it is assumed that the water tanks will be above the roof.
So, Live Load = 10 KN/m2
ASCE 7-10: Table 4-1
3 KN/m2

## Slide 14
Snow and wind load:
Considering the nature of the area, it can be neglected.
Lateral loads, which include seismic loads

## Slide 15
Load combinations
* Ultimate load combinations
1- U=1.4D
2- U= 1.2D + 1.6L
3- U= (1.2+f)D + 1.0L + ρ (Ey+ 0.3 Ex)
4- U= (1.2+f)D + 1.0L + ρ (Ex+ 0.3 Ey)
5- U= 0.9D- f D + ρ (Ey+ 0.3 Ex)
6- U= 0.9D- f D + ρ (Ex+ 0.3 Ey)
* Allowable (service) load combinations
1- U= (1.0 + 0.14SDS)D + 0.7 ρ QE
2- U= (1.0 + 0.10SDS)D + 0.525 ρ QE + 0.75L
3- U= (0.6 – 0.14SDS)D + 0.7ρ QE
Where:
f : 0.2 SDs (Vertical differences).
SDS = design spectral response acceleration parameter at short periods
ρ : Redundancy factor equals 1.3.
D: dead load.
L: live load.
E: QE : earthquake Load.

## Slide 16: CHAPTER 2: Preliminary design

## Slide 17
Introduction
We do the preliminary design to calculate the preliminary dimensions of structural elements instead of putting a completely random dimensions.
We choose to design using one way slab system.

## Slide 18
We choose the solid slab for its advantages in comparison with ribbed slabs:
* Its capability to carry gravity loads and the dynamic loads( seismic).
* Its easier to repair and more economical for short spans.

## Slide 19: 2.2 Preliminary dimension

## Slide 20: Slab
L=5.6m (Both ends continuous) L/28=0.2 m (Approximately two-way)
L=4.7m (One end continuous) L/24=0.2 m (Approximately two-way)
L = 3.9m (One end continuous) L/24=0.16 m (One-way)
Take h=0.16 m

## Slide 22: 2.2.2 Slab for stairs
L=2.8m (Simply supported)
L/28=0.1 m
Take h=0.16 m

## Slide 24: Beams

## Slide 25
B1:
L=5.15m (Both ends continuous) L/21=0.25 m
L=3.55 m (One end continuous)
L/18.5=0.2 m
h =0.25m =>Assume bw = 250 mm

## Slide 27
B2:
L=5.15m (Both ends continuous)
L/21=0.25 m
L=3.55 m (One end continuous)
L/18.5=0.2 m
h =0.25m =>Assume bw = 250 mm

## Slide 29
B3:
L=3.75 m (Both ends continuous)
L/21=0.18 m
L=3.7 m(One end continuous)
L/18.5=0.2 m
h =0.2m =.Assume bw = 250 mm

## Slide 31
B4:
L=3.75 m (Both ends continuous)
L/21=0.18 m
L=3.7 m (One end continuous)
L/18.5=0.2 m
h =0.2m =>Assume bw = 250 mm

## Slide 33
In SAP we choose to take all beams to be 0.4*0.25 (m*m)

## Slide 34: Columns

## Slide 37: seismic analysis
define the seismic in the building
structural irregularities
base shear and equivalent static calculations
response spectrum analysis
Chapter three :

## Slide 38
The mapped spectral accelerations for a one- second period:
S1 = 1.25 * Z = 1.25 * 0.15 = 0.1875 sec. Israel standard SI 413 -202.1.2-2b
The mapped spectral accelerations for short period:
Ss = 2.5 * Z = 2.5 * 0.15 =0.375 sec. Israel standard SI 413 -202.1.2-2a
Definitions:
Fa=1.2 Fv=1.6125
the site class C
10% probability of exceedance.

## Slide 39
Seismic Design Category Based on Short Period and One Second Period Response Acceleration Parameter
D
0.3
0.45

## Slide 40
The seismic force-resisting system is:
Special reinforced concrete shear walls in Y-direction
Special reinforced concrete moment frames in X-direction

## Slide 42
structural irregularities
Plan Structural Irregularities
1a - Torsional Irregularity
1b - Extreme Torsional Irregularity
LOAD CASE EXD
LOAD CASE EYD

## Slide 43
Re-entrant Corners

## Slide 44
Diaphragm Discontinuity

## Slide 45
Out-of-plane Offsets

## Slide 46
Nonparallel Systems

## Slide 47
vertical Structural Irregularities
1A- Stiffness Irregularity -Soft Story
1B - Stiffness Irregularity-Extreme Soft Story

## Slide 48
Weight (Mass) Irregularity

## Slide 49
Vertical Geometry Irregularity

## Slide 50
In-plane Discontinuity in Vertical Lateral Force Resisting Elements

## Slide 51
5A - Discontinuity in Lateral Strength-Weak Story irregularity
5B - Discontinuity in Lateral Strength-Extreme Weak Story irregularity

## Slide 52
Definition of mass source
In Y-direction
𝐶𝑡 = 0.0488, 𝑥 = 0.75
Ta = 0.553 sec
In X-direction
𝐶𝑡 = 0.0466, 𝑥 = 0.9
Ta = 0.858 sec

## Slide 53
Calculate Base shear :
𝑉 = 𝐶𝑠∗𝑊 ASCE 7 – equation (12.8_1)
Where:
Cs=the seismic response coefficient.
W=the effective seismic weight.
Cs=SDS I/R
Csmax=SD1 I/T*R
Csmin=0.044 SDS I
For Y-direction
For X-direction
W: Effective weight
Slabs ,Beams ,Columns ,Walls
Super imposed dead load
Vx=Csx*w =0.0437*21318.3= 931.6 KN
Vy=Csy*w =0.075*21318.3=1598.8 KN

## Slide 55
Modal Mass Participation Ratio

## Slide 56
Base Reaction
The values of response spectrum as seen is less than equivalent static method,
Difference percentage in X = (931.6 - 884.85 / 931.6) *100% = 5.01%  OK.
Difference percentage in Y = (1598.8 -1540.45/ 1598.8 ) *100% = 3.6%  OK.
EXD=710 KN <884
And EYD= 1150 <1540

## Slide 57
9.81/8
*0.85

## Slide 58: CHAPTER 4: THREE DIMENSIONAL STRUCTURAL ANALYSIS AND DESIGN
Figure 4.1: 3D model of the structure in ETABS.

## Slide 59: 4.1 Introduction
3D model will be constructed for whole structure using ETABS
The modeling starts with defining: material, sections (columns, beams, slabs and shear walls), and loads, then drawing elements and making mesh to form a 3D complete model.
make checks that the model is built correctly and the program gives reliable results by comparing values from ETABS with hand calculations

## Slide 60: 4.2 Modeling
Material
Concrete B300 Concrete B350
Figure 4.2: Properties of the concrete in ETABS (B300)
Figure 4.3: Properties of the concrete in ETABS (B350)

## Slide 61: 4.2.2 Sections on ETABS
We enter preliminary sections (for beams, columns, slabs and shear walls) on ETABS.
beams
Figure 4.4: Beam (250*400) definition and its modifiers in ETABS.

## Slide 62
Columns
Figure 4.5: Column definition 400*600 and its modifiers in ETABS.
Figure 4.6: Column definition 300*400 and its modifiers in ETABS.

## Slide 63
Slab
Figure 4.7: Slab definition and modifiers in ETABS.

## Slide 64
Shear walls
Figure 4.8: Shear wall 200 definition and modifiers in ETABS.
Figure 4.9: Shear wall 300 definition and modifiers in ETABS.

## Slide 65: 4.2.3 Loads on ETABS
Figure 4.10: Load patterns definition on ETABS

## Slide 66: 4.3 ETABS model and verification
Compatibility check
This check aims to decide whether the parts and elements of the structural model is acting as a one unit in a realistic way
Figure 4.11: Compatibility Check

## Slide 67: Equilibrium Check
This check aims to ensure that the base reactions resulting from the analysis of different types of loadings assigned to the structural model match the hand calculation with a difference percentage of less or equal 5%
Table 4.1: base reactions taken from different types of load patterns.

## Slide 68: Hand Calculation
Table 4.2: Live & SD loads in the structure
Table 4. 3: Dead loads in the structure
The difference in values:-

## Slide 69: 4.3.3 Check for columns
We choose to check C9 as representative column
Figure 4.12: Columns layout in the structure.
1- Manual axial load

## Slide 70
2- Axial load from ETABS = 1729.58 KN
Difference percentage
Figure 4.13: Axial load on columns from ETABS.
= 5.06 % ≈ 5%  Ok
=

## Slide 71: 4.3.4 Internal forces check (stress strain)
One span in frame in x-direction will be checked, the frame is in the basement floor slab (at elevation Z=1m).
Figure 4.14: Frame in X-direction from ETABS model.

## Slide 72
From manual calculation, Mo :
Mo =
Where :
L2: frame width. (L2 =
= 4.75 m )
Ln: span length face to face. (Ln = 3.7-0.2-0.2 = 3.3 m).
Mo =

## Slide 73
From ETABS, Mo :
The moment M11 from (1.2dead+1.6lived) load combination was chosen, and by making three section-cut in the transverse direction.
Figure 4.15: The left negative moment (M1) of the frame

## Slide 74
Figure 4.16: The right negative moment (M2) of the frame.
Figure 4.17: The positive moment (M3) of the frame.
Mo =
= 104.34 kN.m
=
difference percentage =
= 11.83 %

## Slide 75: 4.3.5 Check moments in beam
From manual calculation:
We get static moment factors using table 13.6.3.3 from ACI 318-14 code
Figure 4.18: Static moment factors in an end span.
Mo =
Mo =

## Slide 77
Figure 4.19: Manual moments on beam.

## Slide 78
From ETABS:
Figure 4.20: Bending Moment Diagram for the Beam to Be Checked for Internal Forces .
M, ETABS =
+ 19.37 = 45.77 KN.m
difference percentage =
= 10.3 % ≈ 10 %  OK

## Slide 79: 4.3.6 Deflection Check
We make a check for deflection of the ground floor slab (at Z=1m).
Deflection from ETABS:
Δ dead = 3.40 mm.
Figure 4.21: Maximum deflection from Dead load.

## Slide 80
 Δ Sustained Live = ΔDead+ Sustained Live – Δdead = 4.62 – 3.4
= 1.22 mm
The long-term deflection is determined by assuming:
No compression steel (ρ compression = 0).
We have 50 % sustained live load.
ΔDead+Sustained Live = 4.62 mm
Figure 4. 22 : Maximum deflection from Dead and Sustained live loads.

## Slide 81
ΔDead+Live = 5.85 mm
 Δ Unsustained Live = ΔDead+Live - Δ Dead+ Sustained Live
= 5.85 – 4.62
= 1.23 mm
Figure 4. 23 : Maximum deflection from Dead and live loads.

## Slide 82
Δ Long term = ΔL-Unsustained+ (λ∞ * ΔD) + (λt*ΔSL)
Live load assumed to be sustained for (5 -∞) years. That means λ∞ =λt.
λ =
𝜉=2 from Figure ‎4.27 from ACI code.
 λ = =2
Δ Long term = 1.23 + (2 * 3.40) + (2*1.22)
=10.47 mm
Figure 4.24: ACI Code multipliers for long term deflections.
: multiplier for long term deflection.
ρ` : compression steel ratio.

## Slide 83
Length of the span = 5590 mm
According to ACI-318
The allowable deflection = = = 23.29 mm > 10.47 mm
Table 4.4: Allowable deflection according to ACI-318.

## Slide 84: 4.3.9 Check for drift
The difference of the deflections at top and bottom of the story.
The drift of building in Y-direction is okay due to shear walls.
𝜹𝒙 = * δxe
Where:
C d: The deflection amplification factor. it equals 5.5.
𝜹𝒙𝒆: The deflection at the location of level x determined by an elastic analysis, will be obtained from ETABS.
Ie: Importance factor. it equals 1.00.

## Slide 85
Δallowable = 0.02 hSX = 0.002* 3250 = 65 mm.
The story drift calculations due to earthquake load in the X-direction, are summarized in Table 4.5.
All calculated stories drift are Ok
Table 4.5: Story drift calculations due to earthquake load in X-direction.

## Slide 86: 4.3.10 Check soil equilibrium
Bearing capacity:20 KN/m^3 Φ=30 W,live=20 KN/m2
1) Kactive=(1-sin Φ )/(1+sin Φ )=1/3
Seismic earth pressure =Δp= 0.40Kh ¥tHrw (ASCE-41-13)
Kh=Sxs/2.5 and Sxs=SDS=Fa*SS
Where:
Δp: additional earth pressure caused by seismic shaking, which is assumed to be a uniform pressure.
Kh: horizontal seismic coefficient in the soil.
¥t: total unit weight of soil.
Hrw : height of the retaining wall.
Sxs: spectral response acceleration parameter.
Δp=0.4*(0.45/2.5)*20*2.25=3.24 KN

## Slide 87
2) Kstatic=(1-sin Φ ) = 1/2
As we can see the static earth pressure is the largest so we use it for design.
the resultant force from soil pressure is zero, because there are two forces have the same magnitude but with opposite direction.
Figure 4. 25: Base reaction due to soil.

## Slide 88: Design of Structural Concrete Members
Design for Beams
Design of Ground Beams
Design of slabs
Design of columns
Design of shear walls
Design of footings
Design of stairs
Design of infill walls

## Slide 89: Design for Beams
Flexure check:
ρ = (1-)
ρ = (1-)
ρ = 0.00396
Area of steel (As) = ρ × b × d = 0.00396× 250× 340 = 336.6 mm2

## Slide 90
Shear force check:
Vp=
Ф𝑀𝑛= Ф𝐴𝑠𝐹𝑦(𝑑− 𝑎/2)
𝑎= As Fy/ 0.85 𝑓′𝑐 𝑏
Vp=42.13+25/3.3=20.5 KN
Vg=WuL/2
Vg=30.67×3.3/2=50.6 KN
V Design=Vp+Vg =20.5+50.6=71.1 KN
Ф𝑉𝑛= Ф(𝑉𝑐+𝑉𝑠)
= = 0.321mm2/mm

## Slide 91
Torsional Check:
𝑇𝑡ℎ= 0.75**1 () = 2355278.6 N.mm = 2.35 KN.m
Tu<𝑇𝑡ℎSo, there is no need torsion reinforcement

## Slide 92
Code specifications
Dimensional limits
4
bw min of
Longitudinal reinforcement
at least 2 continuous bars at both top and bottom faces
max of
Spacing of the transverse reinforcement enclosing the lap-spliced bars min of .
Lap splices shall not be used in joints (Within a distance of twice the beam depth from the face of the joint).

## Slide 93
Reinforcement Detailing:

## Slide 96
Design of Ground Beams
the smallest cross-sectional dimension shall be at least equal Ln/20
Closed ties shall be provided at a spacing not to exceed the lesser of one-half the smallest orthogonal cross-sectional dimension and 300 mm
all ties shall have a design strength in tension or compression at least equal to a force
Cs or Ts=10% × SDs × largest axial factored dead and live
(As)min larger than
area of steel depending on seismic requirement

## Slide 98: Design of Columns Checks of Columns
Column 9 will be checked as a sample, because it is a critical column, Figure 5.18 shows the location of C9.

## Slide 99
KLu/r ≤ 34 – 12 (M1/M2) (5.11)
≤ 40
Check slenderness of columns
(Column9 in second floor has the highest slenderness ratio)
* About X- axis: M1 equal -37.02 kN.m, and M2 equal 37.1 kN.m.
* About Y- axis: M1 equal -3.58 kN.m, and M2 equal 5.09 kN.m.

## Slide 100
Assume K =1
Lu = 3.25 – 0.4 = 2.85 m
r = 0.3 h ,h=0.4
By applying (5.11):
* About X- axis:
KLu/r = 23.75 ≤ 34 – 12 ×M1/M2 = 45.9
≤ 40
* About Y- axis:
KLu/r = 15.83 ≤ 34 – 12 ×M1/M2 = 42.44
≤ 40
 The column is short in two directions, then will be neglect the effect of slenderness.

## Slide 101: Check columns design (Reciprocal Load Method)
=

## Slide 102
Po =
Ag = 400x600 = 240000 mm2
= 2400 mm2
 Po = 3464.69 KN
That means Pni > Pu. So, the design of ETABS is ok.
Where:

## Slide 103
Chart: M3 (kN.m)
| 0 | 103.24860000000002 | 163.5256 | 208.93459999999999 | 238.75200000000001 | 256.02229999999969 | 278.54070000000002 | 286.27889999999923 | 217.61459999999914 | 100.2734 | 0
dsvsdv | 3456.8171 | 3456.8171 | 3205.6482 | 2702.7901 | 2166.8627 | 1577.5988 | 1402.0922 | 1070.5559 | 491.7551 | -314.1959 | -893.5606
Chart: M2 (kN.m)
| 0 | 144.11479999999995 | 234.32240000000121 | 299.1490000000021 | 342.08390000000003 | 365.30840000000001 | 408.44749999999999 | 430.02349999999899 | 330.34290000000038 | 188.60140000000001 | 0
dsvsdv | 3456.8171 | 3456.8171 | 3252.6648 | 2773.8623 | 2258.2486 | 1695.9951 | 1458.2929 | 1129.3359 | 489.2024 | -173.5315 | -893.5606
Figure 5. 22: Interaction diagram for C9 at 90 ◦
Figure 5. 21 : Interaction diagram for C9 at 0 ◦

## Slide 104
Load Combination | Pu | M2 | M3 | Pnx | Pny | Po | Pni | Pni>Pu
 | kN | KN.m | KN.m | KN | KN | KN | KN | ??
1.4D | 1455.74 | 4.85 | 11.75 | 3456.82 | 3456.82 | 3464.69 | 3448.98 | ok
1.2D+1.6L | 1786.01 | 4.73 | 15.37 | 3456.82 | 3456.82 | 3464.69 | 3448.98 | ok
1.29D+1L+1.3EXD | 1697.01 | 5.61 | 20.95 | 3456.82 | 3456.82 | 3464.69 | 3448.98 | ok
1.29D+1L+1.3EYD | 1698.73 | 7.66 | 17.35 | 3456.82 | 3456.82 | 3464.69 | 3448.98 | ok
0.81D+1.3EXD | 861.47 | 3.58 | 21.45 | 3456.82 | 3456.82 | 3464.69 | 3448.98 | ok
0.81D+1.3EYD | 863.20 | 5.63 | 11.31 | 3456.82 | 3456.82 | 3464.69 | 3448.98 | ok

## Slide 105: Code specifications
I. Longitudinal Reinforcement.
* Area of longitudinal reinforcement, Ast, shall be at least 0.01Ag and shall not exceed 0.06Ag.
* Lap splices are permitted only within the center half of the member length, and shall be designed as tension lap splices and enclosed within transverse reinforcement conforming to transverse reinforcement.

## Slide 106
II. Transverse Reinforcement.
* Transverse reinforcement shall be provided over a length Lo from each joint face and on both sides of any section, the length Lo shall not be less than the largest of:
Lo = max
* Transverse reinforcement shall be provided by either single or overlapping hoops, spirals, circular hoops or rectilinear hoops, with or without crossties.
*Each end of the crossties shall engage a peripheral long reinforcing bar.
* Consecutive crossties shall be alternated end for end and along the longitudinal reinforcement.
* Spacing of cross ties or legs of rectilinear hoops hx, within a cross section of the member shall not exceed 350 mm on center.
* Spacing of transverse reinforcement (So) along the length of lap splicing:
100 mm
So = 100 +

## Slide 107
* Spacing of transverse reinforcement (S1) along the length Lo of the member shall not exceed the minimum of:
* According to ACI 318-14 table 18.7.5.4, the total cross-sectional area of rectangular hoop reinforcement shall not be less than that required by the following equation:
Where:
Ash: Total cross-sectional area of transverse reinforcement, including crossties, within spacing s and perpendicular to dimension bc, mm2.
bc: Cross-sectional dimension of member core measured to the outside edges of the transverse reinforcement composing area Ash, mm.
Ag: Gross cross-sectional area of concrete section, mm2.
S: Center-to-center spacing of transverse reinforcement measured along the longitudinal axis of the structural member.
Ach: Cross-sectional area of a member measured to the outside edges of transverse reinforcement, mm2.
𝐴𝑠ℎ = 𝑚𝑎𝑥. 𝑜𝑓:

## Slide 108
Figure 5. 23: Example on Transverse Reinforcement in Columns

## Slide 109
* Beyond the length Lo, the column shall contain spiral or hoop reinforcement with center-to-enter spacing (S2) not exceeding the smaller of six times the diameter of the smallest longitudinal column bars and 150 mm.
Figure 5. 24: Longitudinal and horizontal cross sections for column in special moment frame explain the lap splice details and confinement requirements at column ends for rectangular hoop reinforcement.

## Slide 110: Design Sample
Column 9 and column 4 will be designed as representative samples for the two column sections used in the building, C1 (400x600mm) and C2 (300x400mm), as shown in Figure 5.18.
Longitudinal Reinforcement for Column 9:
From ETABS, the required area for reinforcement is 2400 mm2, use 10Ø18.
* Lap Splice for longitudinal bars shall be extended the value of 1.3 development length:
Ldt =
Lap splice Ls = 1.3 x 686 = 892 mm, use 900 mm
= 686 mm
Ldt =

## Slide 111
* Distance (Lo):
= max
 Lo = 600 mm.
Lo = max

## Slide 112
* Spacing between bars:
Spacing in x-direction =
= 132 mm <150 mm  only one steel bar between two tied bars can be left without placing ties on it.
= 155 mm > 150 mm  ties must placed on every steel bar.
Spacing in y-direction =
Spacing between bars =

## Slide 113
Transverse Reinforcement for Column 9:
Stirrups of a diameter Ø10 will be used for this column.
* hx = 350 mm
So = 100 +
 So = 100 mm.
minimum of
* Stirrups spacing beyond the distance Lo, (S2)
minimum of
Referring to Figure 5.23, to calculate Ash,1 and Ash,2 from Eq. (5.13):
* 100 mm
* Stirrups spacing within the distance Lo, (S1)
 S1 = 100 mm.
 S2 = 100 mm.

## Slide 114
𝐴𝑠ℎ,1 = 𝑚𝑎𝑥.𝑜𝑓
 𝐴𝑠ℎ,1 = 283 mm2
 𝐴𝑠ℎ,2 = 460 mm2
Where: bc1 = 400 – 2x40 = 320 mm.
bc2 = 600 – 2x40 = 520 mm.
𝐴𝑠ℎ,2 = 𝑚𝑎𝑥.𝑜𝑓

## Slide 115
According to the column cross section shown in Figure 5.25.
𝐴𝑠ℎ,1, calculated = 2x78.5 = 157 mm2 < 283 mm2
𝐴𝑠ℎ,2, calculated = 4x78.5 = 314 mm2 < 460 mm2
 increase diameter of stirrups or increase the number of legs to φ12.
Figure 5. 25 : cross section for column 9.

## Slide 116
Longitudinal Reinforcement for Column 4:
From ETABS, the required area for reinforcement is 1200 mm2, use 8Ø14.
* Lap Splice for longitudinal bars shall be extended the value of 1.3 development length:
Ldt =
534 mm
Ldt =
Lap splice Ls = 1.3 x 534 = 695 mm, use 700 mm

## Slide 117
Lo = max
 Lo = 475 mm
* Spacing between bars:
Spacing between bars =
Spacing in x-direction =
= 136 mm <150 mm  only one steel bar between two tied bars can be left without placing ties on it.
Spacing in y-direction =
= 86 mm > 150 mm  only one steel bar between two tied bars can be left without placing ties on it.

## Slide 118
Transverse Reinforcement for Column 4:
Stirrups of a diameter Ø10 will be used for this column.
* hx = 350 mm
* 100 mm
So = 100 +
= 100
 So = 100 mm
* Stirrups spacing within the distance Lo, (S1)
minimum of
 S1 = 75 mm.
* Stirrups spacing beyond the distance Lo, (S2)
minimum of
 S2 = 75 mm.

## Slide 119
Referring to Figure 5.23, to calculate Ash,1 and Ash,2 from Eq. (5.13):
 𝐴𝑠ℎ,1 = 451 mm2
𝐴𝑠ℎ,1 = 𝑚𝑎𝑥.𝑜𝑓
𝐴𝑠ℎ,2 = 𝑚𝑎𝑥.𝑜𝑓
 𝐴𝑠ℎ,2 = 310 mm2
Where: bc1 = 400 – 2x40 = 320 mm.
bc2 = 300 – 2x40 = 220 mm.

## Slide 120
Figure 5. 26 : cross section for column 4.
𝐴𝑠ℎ,1, calculated = 2x78.5 = 157 mm2 < 451 mm2
𝐴𝑠ℎ,2, calculated = 2x78.5 = 157 mm2 < 310 mm2
 increase diameter of stirrups or increase the number of legs
Acording to the column cross section shown in Figure 5.26.

## Slide 121
Figure 5. 27: The detailing for longitudinal reinforcement and distribution of stirrups.

## Slide 122: 5.4 Design of slabs
5.4.1 Code specifications :
Flexural Capacity for slab:
∅Mn = ∅As×𝑓𝑦×(d −a/2) , a =
Shear Capacity of concrete in slab
∅Vc =∅×1/6 × × bw × d
Reinforcement Ratio of steel
𝜌 = (1- ) , 𝜌𝑚𝑖𝑛 = 0.0018

## Slide 123
5.4.2 Design Sample :
The ultimate minimum moment in both direction X and Y:
∅Mn = ∅As×𝑓𝑦×(d −a/2) , a =
Where :
depth of slap (H) = 160 mm.
width of slap section (b) = 1000 mm.
effective depth of the slap (d) = 120 mm.
As min = 0.0018 x 1000 x 160 = 288 mm2
a = = 5.929 mm.
 ∅Mn = = 12.74 kN.m

## Slide 124
Check for the ultimate moment in X- direction (M11):
There are two zones where the moment is more than the ultimate minimum moment.
Mu for zone A = 19.35 kN.m.
 𝜌 = 0.003689  As = 442.68 mm2
Then As for zone A = 4∅12/ 1m.
Mu for zone B = 41 kN.m.
𝜌 = 0.008214  As = 985.71 mm2
Then As for zone B = 9∅12/ 1m.
Figure 5. 28 : The ultimate moment in X- direction (M11) for the slab in fifth floor.

## Slide 125
The area of steel of Slabs in X- direction:
* Use a bottom steel equal 4Ф10/1m and top steel equal 4∅12/ 1m in zone A.
* Use a bottom steel equal 4Ф10/1m and top steel equal 9∅12/ 1m in zone B.
* Use a bottom and top steel equal 4Ф10/1m for the other zones.
Figure 5. 31: Reinforcement of Slab in the X-direction.

## Slide 126
II. Check for the ultimate moment in Y- direction (M22):
There are three zones where the moment is more than the ultimate minimum moment.
Mu for zone A = 43 kN.m.
 𝜌 = 0.008658  As = 1039 mm2
Then As for zone A = 9∅12/ 1m.
Mu for zone B = 40 kN.m.
𝜌 = 0.007994  As = 959.28 mm2
Then As for zone B = 9∅12/ 1m.
Figure 5. 29: The negative ultimate moment in y- direction (M22) for the slab in Fifth floor.
Figure 5. 30 : The positive ultimate moment in y- direction (M22) for the slab in Fifth floor.
Mu for zone C = 15 kN.m.
 𝜌 = 0.002833  As = 340 mm2
Then As for zone A = 5∅10/ 1m.

## Slide 127
The area of steel of Slabs in Y- direction:
* Use a top steel equal 9∅12/ 1m in zone A.
* Use a top steel equal 9∅12/ 1m in zone B.
* Use a bottom steel equal 5Ф10/1m in zone C.
* Use a bottom and top steel equal 4Ф10/1m for the other zones.
Figure 5. 32 : Reinforcement of Slab in the Y-direction.

## Slide 128: Design of Shear Wall
The definition of wall pier in according to ACI 318-14 code section 2.3 :-
A vertical wall segment within a structural wall, bounded horizontally by two openings or by an opening and an edge.
The definition of wall spandrel :-
A horizontal wall segment within a structural wall, bounded vertically by two openings or by an opening and an edge.

## Slide 129
Concrete shear capacity in walls can be calculated from
For the detailed equations to calculate the shear capacity, Table 22.5.5.1 from ACI 318-14 illustrates that, table 5.3 shows the equations.
Vc |  | 
Least of (a),(b) and (c) |  | (a)
 |  | (b)
 |  | (c)

## Slide 130
Nominal shear capacity (Vn) for walls
Vn shall not exceed 0.83 ℎ 𝑑
Which,
h: Thickness of wall
d: Shall be taken equal to 0.8
For Spandrel
For Pier
Where:
Acv: Gross area of shear wall cross section, which equal bw x Lw.
𝛼𝑐: Coefficient = 0.25 For ≤ 1.5.
= 0.17 For ≥ 2.0.
Varies linearly between 0.17 and 0.25 for between 1.5 and 2.0.
𝜌𝑡: Transverse reinforcement ratio.

## Slide 131
𝜌𝑡 𝑚𝑖𝑛 = 0.0025.
𝜌𝑙 𝑚𝑖𝑛 = 0.0025.
𝜌𝑡 𝑚𝑖𝑛 = 0.0025.
𝜌𝑙 𝑚𝑖𝑛 = 0.0025 + 0.5 (2.5 - ) (𝜌𝑡 − 0.0025) ≥ 0.0025.
Where:
Acv = gross area of concrete section bounded by web thickness and length of section in the direction of shear force considered in the case of walls in mm2

## Slide 132
      Spacing of longitudinal reinforcement:
Spacing (SL) of longitudinal bars in cast-in-place walls shall not exceed the lesser of:
3h
450 mm
.
Where lw: length of entire wall, or length of wall segment or wall pier considered in direction of shear force, mm
      Spacing of transverse reinforcement:
Spacing St of transverse reinforcement in cast-in-place walls shall not exceed the lesser of:
3h
450 mm.
.
  Reinforcement spacing each way in structural walls shall not exceed 450 mm.
At least two curtains of reinforcement shall be used in a wall if or

## Slide 133
Boundary Elements for Special Shear Walls.
According to ACI 318-14 section 18.10.6, the special boundary elements shall be provided at edges and boundaries of the walls if the maximum compressive stress corresponding to load combinations including earthquake effect (E) exceeds 0.2 f'c.

## Slide 134
Wall Pier Demand/Capacity Ratio
The wall pier demand/capacity ratio is a factor that gives an indication of the stress condition of the wall with respect to the capacity of the wall.
If OL = OC (or D/C = 1), the point (Pu, M3u) lies on the interaction curve and the wall pier is stressed to capacity.
If OL < OC (or D/C < 1), the point (Pu, M3u) lies within the interaction curve and the wall pier capacity is adequate.
If OL > OC (or D/C > 1), the point (Pu, M3u) lies outside of the interaction curve and the wall pier is overstressed.

## Slide 135
* Sample calculations for Wall pier
W5

## Slide 136
Internal forces in shear wall
Width = 2800 mm
Depth = 200 mm
Vu = 7.1 KN
ФVc >Vu OK

## Slide 137
Ultimate moment in wall pier
Mu = 12.8 kN
Calculating the reinforcement ratio (ρ) by the following equation:
Take ρ =0.0025

## Slide 138
Ultimate axial force in wall pier
Pu = 874.13 KN

## Slide 139
For horizontal reinforcement:
For two curtains (layers) of reinforcement with Ø 10 mm

## Slide 140
For vertical reinforcement:
For two curtains (layers) of reinforcement with Ø 10 mm

## Slide 141
For the D/C ratio =0.003<1, the point (Pu, M3u) lies within the interaction curve and the wall pier capacity is adequate.
Another approach for checking the adequacy of the wall pier which is the interaction diagram.
After dropping the values of axial force and bending moment in the x-axis and y-axis the point was in the curve so the section is adequate.

## Slide 142
Chart: Interaction diagram at 0 degree
| 0 | 128200000000 | 197300000000 | 252300000000 | 294400000000 | 326200000000 | 370900000000 | 405200000000 | 346100000000 | 263100000000 | 0
0 degree | -8031000000 | -8031000000 | -7608000000 | -6595000000 | -5529000000 | -4376000000 | -3968000000 | -3256000000 | -1855000000 | -667100000 | 2085000000
Chart: Interaction diagram at 90 degree
| 0 | 1795000000000 | 2763000000000 | 3532000000000 | 4123000000000 | 4567000000000 | 5194000000000 | 5675000000000 | 4848000000000 | 3686000000000 | 0
90 degree | -8031000000 | -8031000000 | -7608000000 | -6596000000 | -5530000000 | -4377000000 | -3969000000 | -3258000000 | -1856000000 | -667400000 | 2085000000

## Slide 143
Special boundary elements check
Special boundary elements are needed if the stress σ > 0.2 f'c
σ = 0.2 x 28= 5.6 MPa.
To compute stress from Equation below
Where:
I: Moment of inertia equal 𝑏ℎ3/12 = 200 × 28003/12= 3.66*1011
C: Equal 0.5*Lw = 0.5*2800 = 1400 mm
Therefore, there is no need for boundary elements.

## Slide 144
Sample calculation for Wall spandrel

## Slide 145
Width = 912.5 mm, Depth = 200 mm and Height = 1393 mm
Vu = 80.4767 KN
ØVc = 161 KN > Vu = 80.4767 KN OK.
Mu = 13.19 KN

## Slide 146
Design for Vertical reinforcement.
For horizontal reinforcement:

## Slide 147
No need for coupling beams

## Slide 148
Design for Footings
(q all = 350 kN/m2)

## Slide 149
Modeling and design calculations for single footings

## Slide 150
Check bearing capacity
Check one-way shear
Check two-way shear
Design for flexure

## Slide 152
Design calculations for wall footings

## Slide 153
Bearing capacity:
qmax=
qmin=
2. Wide beam shear check:
Vu=qu(L1-d)
3. Design for flexure
Mu=)

## Slide 155
Design calculations for pile foundation
As a result of analysis the reaction was P tension=-34 KN P compression= 856 KN
Refer to empirical laws of foundations there are 3 methods to know the capacity of each single pile of them.
C=0(sand soil)
Ф=30 ֠ c
Assume diameter =0.6m and length=15m
1- Meyerhof’s method
2- Vesic’s method
3- Method of Coyle and Castello

## Slide 156
Meyerhof’s method
Qp=463 KN
Vesic’s method
Qp=1976.1 KN
Method of Coyle and Castello
Qp=2544.5 KN
It appears Qp obtained from the Meyerhof’s method is too small so it will be excluded from calculation.
Qp avarege= 2260.3 KN
Qp allowable = Qp avarege /F. S =2260.3/2.5=904.12 KN
Qp allowable =904.12 KN > P compression= 856 KN
then No Failure

## Slide 157
Po =
where :
Ag = 3.14 * 3002 = 282743.3 mm2
= 2827.4 mm2
Po=4483.5 KN >856 KN OK.
Use 920
For spiral reinforcement:
S
Where:
Asp: cross-sectional area of spiral wire.
Ag: gross area of pile.
Ach: core area of the pile.
Fyt: yielding strength of spiral steel.
dc: diameter of pile core outside to outside of spiral reinforcement.
So use 1 8/100 mm
For longitudinal reinforcement:

## Slide 159: 5.7 Design of stairs
Figure 5. 57: Plan of stairs in story 1.
5.7.1 Loads on stairs:
The thickness of slab is assumed to be 0.16 m.
 The total loads on stairs are:
Own weight of stairs = 0.16 × 25 = 4 kN/m2.
Live load = 5 kN/m2.
SD = 3.5 kN/m2.

## Slide 160
5.7.2 Modeling of stairs:
Stairs will be represented by ETABS as one-way solid slab with thickness 0.16 m, and loads will be added to check deflection and shear due to ensure that slab thickness is enough. Then it will be designed.
Figure 5. 58: 3D Model of stairs on ETABS.

## Slide 161
Checks of the model:
I. Check defection:
Δ,allowable ≤ = = 11.25 mm.
Δmax = 0.533 mm < 11.25 mm  ok
Figure 5. 59: Max Deflection in Stairs.

## Slide 162
II. Check for shear:
Shear capacity of stair slab:
ФVc = 0.75× 1/6 × × b × d
= 0.75×1/6× ×1000× 130 / 1000 = 79.6 kN
Vu = 69.347 kN < 79.6 kN  ok.
So, No need for shear reinforcement.
Figure 5. 60: Ultimate max shear for Stairs.

## Slide 163
5.7.3 Design for flexural:
The stair slab is defined as one-way solid slab with y-direction.
Design of flight:
M22 in the flight (positive) = 13.446 KN.m (Bottom steel).
ρ = 0.00215  As = ρ b d = 0.00215x1000x130 = 279.5 mm2.
As min = ρmin b h = 0.0018 ×1000 × 160 = 288 mm2 > 279.5 mm2
 Use As = 288 mm2 (4∅10 /1m) for all longitudinal steel (main steel) in the flight.
Figure 5. 61 : Maximum positive moment M22 in the flight.

## Slide 164
II. Design of landing:
M22 in the Landing (negative) = 25.241 kN.m (Top steel)
ρ = 0.00412  As = ρ b d = 0.00412x1000x130 = 535.6 mm2.
As min = ρmin b h = 0.0018 ×1000 × 160 = 288 mm2 < 535.6 mm2
 Use As = 535.6 mm2 (5∅12 /1m).
Figure 5. 62: Maximum negative moment M22 in the landing.

## Slide 165
III Design for Transverse steel:
M11 = 2.256 KN.m  Use minimum steel
As min = ρmin b h = 0.0018 ×1000 × 160 = 288 mm2 (4∅10 /1m).
Figure 5. 63: Maximum transverse steel M11.

## Slide 166
Figure 5. 64 : Longitudinal section of stair.

## Slide 167: Design of Block Wall
The block walls shall be designed seismically according to chapter 13 in ASCE 7-10.
Seismic Design Force (Fp)
The horizontal seismic design force (FP) shall be applied at the component's center of gravity and distributed relative to the component's mass distribution and shall be determined in accordance with
FP is not required to be taken as greater than
and FP shall not be taken as less that

## Slide 168
Where:
FP = Seismic design force.
SDS = Spectral acceleration, short period.
ap = component amplification factor that varies from 1.00 to 2.50 (select appropriate value from table )
IP = Component importance factor that varies from 1.00 to 1.50
WP= Component operating weight.
RP = Component response modification factor that varies from 1.00 to 12 (select appropriate value from table )
z = Height in structure of point of attachment of component with respect to the base.
h = Average roof height of structure with respect to the base.
SDS = 0.45 (From chapter 3)
For the values of (RP & ap) table 13.5-1 in ASCE 7-10 code illustrate it, but to be in the safe side, take RP =1.5 & ap =2.5, to maximize the seismic force.
For IP section 13.1.3 in ASCE7-10 code illustrate that IP shall be taken as 1.5 if the component is required to function for life-safety purposes after an earthquake.
WP = 5.92 KN/m2 (exterior wall) and 3.42 KN/m2 (interior wall) (From chapter 1)
For the value of z / h, to be in the safe side, equal 1, that indicates the value for the last floor.

## Slide 169
According to the limitations, take FP = 6.4 KN/m2
According to the limitations, take FP = 3.7 KN/m2

## Slide 170
For exterior walls:
h = Height of the block wall = 3.00 m.
FP= 6.4 KN/m2
= Assume it 6 MPa
As = ρ*b*d = 333.33 mm2

## Slide 171
The type of bolts that will be used is A325-N
Shear capacity of bolt (Fnv) =330 MPa
Tensile capacity of bolt (Fnt) = 620 MPa
nsp = Number of shear planes = 1.
Ф= 0.75
V= 9.6 KN
T= 9.6 KN
Checks :-

## Slide 172
Check for pull out failure in anchor bolt:-
From outside of the wall
Where:
lo= The distance the anchor bolt is in the concrete.
From bottom of the block wall.
Assume lo = 150 mm

## Slide 173
For interior walls:
h = Height of the block wall = 3.00 m.
FP= 3.7 KN/m2
= Assume it 6 MPa
As = ρ*b*d= 0.00577*1000*50 = 288.5 mm2

## Slide 174
There is two bolts per meter length in each side, the calculation for their capacity is for shear capacity.
The type of bolts that will be used is A325-N
Shear capacity of bolt (Fnv) =330 MPa
Tensile capacity of bolt (Fnt) = 620 MPa
nsp = Number of shear planes = 1.
Ф = 0.75
V= 5.55/2=2.775 KN (because each face of the wall exposes a shear force, so divide it)
T= 2.775 KN
Checks :-

## Slide 175
Check for pull out failure in anchor bolt:-
From bottom of the block wall.
Assume lo = 150 mm
Development length and splices:
For the bars in the exterior wall (200 mm thickness).
For the bars in the interior wall (100 mm thickness).

## Slide 176
Notes about Block wall :
Horizontal bar of 8 mm in diameter is used every 600mm in vertical length (3 blocks rows), to preserve the straightness of the bars.
Around the block wall (top, left, right, front & behind) there 5 cm emptiness, to preserve the frame system and not affect it.
From the (top, right & left) there is a compressible material (silicon).
The bolts inserted in the slab, have 10 cm length inside the slab+2cm length plate, for total length 12 cm.
The bolts inserted in the beam from the exterior block wall (outer face) have a length of 19 cm.
For the exterior walls, there is concrete with 20 cm in depth and 20 cm in width to maximize the sportiness of the wall.
For the dowels inserted in the bottom of the block wall, a 15cm of the length of the bar, is inserted in the beam below the block wall.

## Slide 177
References:
ACI Committee 318 “Building Code Requirements for Structural Concrete (ACI 318M-14)” American concrete institute, Michigan, 2011.
ASCE Committee (2010), “American Society of Civil Engineers, Minimum Design Loads for Buildings and Other Structures” American Society of Civil Engineers, Virginia 20191, 2010.
IBC Committee, “the International Building Code. “The International Code Council (ICC), California, 2015.
Nilson, Arther H., David Darwin, Charles W. Dolan.” Design of concrete structures. Fourteenth edition”. New York: McGraw-Hills Companies, Inc., 2010.
Israeli Standard SI 413. June 1995. ,Amendment No.3, September 2009.
International Masonry Institute ( www.imiweb.org ).

## Slide 178
Thank you
