## Slide 1: An-Najah National University Faculty of Engineering and Information Technology
Graduation project report II
Water and Sewer Network design for Hajah Village
Prepared by :
Ameer Eid
Rana Jabir
Supervisor: Dr. Anan Jayousi

## Slide 2: Main Objective
Analyze the existing water network in Hajah village.
Redesign the water network to meet the requirements for the next 30 years.
Design a sewer network for part of the village for the next 30 years.

## Slide 3: Study area
hajah is a Palestinian village in Qalqilya Governorate, 18 Km southwest Nablus.
It is 425 m above sea level.
The total area of urban village is about 23 Km2 ( 15.2 %
as urban area)
The total population of the village is about 3700 capita in 2016.

## Slide 5: Water status
90% of hajah houses are provided with water by the West Bank Water Department through the public water network established in 2009.
In 2014 the water network was renovated.
The percentage of losses reduced up to 5%.
Thus, the quantity of water supplied to hajah now is 80300 m3 /year.
The rate of the water consumption per capita became 56.48 L/C/day.
According to the World Health Organization, the minimum quantity of consumption is 100 L/C/day.

## Slide 6: Network components
Booster Station , Reservoir and pumps.

## Slide 7
Pipes :
Transition pipe
Main pipes 4 and 6 in.
The transition pipe has a total length of 1134 meter.
Distribution pipes
The distribution pipes have different diameters (1, 2, 3, 4 and 6 inches).
The total length of these pipes is around 13924 meter.

## Slide 8: Methodology

## Slide 9: Questionnaire outputs
Chart: Relation between Number of Family members and Monthly Water Consumption
| 3 | 3 | 5 | 5 | 6 | 7 | 7 | 7 | 8 | 9 | 9 | 2 | 3 | 4 | 5 | 7 | 7 | 7 | 8 | 8 | 8 | 9 | 10 | 11 | 4 | 7 | 8 | 9 | 12 | 13
3 3 5 5 6 7 7 7 8 9 9 2 3 4 5 7 7 7 8 8 8 9 10 11 4 7 8 9 12 13 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 200 | 200 | 200 | 200 | 200 | 200
Chart: Relationship Between House Area and Monthly Water Consumption
| 100 | 120 | 120 | 120 | 130 | 160 | 180 | 200 | 250 | 300 | 500 | 100 | 110 | 150 | 150 | 200 | 200 | 200 | 300 | 300 | 400 | 400 | 450 | 500 | 150 | 160 | 220 | 250 | 300 | 300
 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 200 | 200 | 200 | 200 | 200 | 200

## Slide 10
Topography Map
Water Network Map

## Slide 11: Calculations
Supply | 80300 meter cubic / year
Consumption | 76285 meter cubic / year
Unaccounted % | 5%
Population Served | 3700 capita
Average water use per capita | 56.48 L /c/day

## Slide 12: Water CAD
Work on topography map and network map and collected data to develop the data needed for WaterCAD program .

## Slide 13: Result from WaterCad
Nodes & junctions
Chart: junction ID
Chart: pipe DI

## Slide 14
Design Water Network
Complete the Network
Estimation Future population
Estimation Future Demand
Modification

## Slide 15: Network design
Estimation of the future population :
Pfuture = P0 (1+i)n
P2046 = P2016 (1+ 0.025)^30
P2046 = 3700 ( 1+ 0.025) ^30
P2046 = 7761 capita

## Slide 16
Future water demand :
F = (P 2046 / P 2016) (water use 2046 / water use 2016)
F= (7761/3700) (120/ 56.48)
F= 4.46
Where F : a factor to calculate the future demand from the current demand.

## Slide 17: Outputs

## Slide 18
Modification :
Law pressure :
Change the diameters of some pipes and set pump
velocity :
Change the diameters of some pipes

## Slide 19
Pump

## Slide 20
Results and cost
cost $ | cost unit $/m | Length | New Dia | Old Dia | pipes ID
1040 | 16 | 65 | 6 | 4 | p-31
352 | 16 | 22 | 6 | 4 | p-32
368 | 16 | 23 | 6 | 4 | p-34
957 | 11 | 87 | 4 | 3 | p-83
1276 | 11 | 116 | 4 | 2 | p-104
22 | 11 | 2 | 4 | 2 | p-106
462 | 11 | 42 | 4 | 2 | p-108
737 | 11 | 67 | 4 | 2 | p-110
825 | 11 | 75 | 4 | 2 | p-112
304 | 16 | 19 | 6 | 3 | p-15
512 | 16 | 32 | 6 | 3 | p-19
4784 | 16 | 299 | 6 | 3 | p-81
816 | 16 | 51 | 6 | 3 | p-79
1232 | 16 | 77 | 6 | 3 | p-77
330 | 11 | 30 | 4 | 2 | p-66
1144 | 11 | 104 | 4 | 2 | p-89
1100 | 11 | 100 | 4 | 2 | p-90
165 | 11 | 15 | 4 | 2 | p-92
70 | 5 | 14 | 2 | 1 | p-93
308 | 11 | 28 | 4 | 2 | p-94
40 | 5 | 8 | 2 | 1 | p-95
∑=16844 |  |  |  |  | 

## Slide 21
Chart: Pressure and ID Numbers
 | 20
 | 100
Chart: 
Chart: 
Outputs

## Slide 22: Sewer network
Existing sewer network components :
Manholes
Conduits
Wastewater treatment plant

## Slide 23
Manholes and conduits :
Was built in 2010 and it services less than 20% of the village.
Established randomly without taking into consideration the Palestinian Specification.
Leakage, incompetence in drainage and no schemes show the locations for the network parts.

## Slide 24
Wastewater treatment plant:
Built in 2014
Ponds system with 4 ponds , two bonds currently are used
Sufficiency can reach 95 %
The treated wastewater is discharged to the Wadi

## Slide 26
Calculations
Water consumption = 120 L/c/d
Peak hour factor= 5*p^(-1/6)= 3.5
WW = 0.8 * water consumption + infiltration
WW = 0.8 * 120*3.5 + 0.2*120*0.8
WW = 355.2 L/C.day

## Slide 27
Compute the area for each manhole and determine the load using GIS program .
Input the data on Sewer CAD V8i program.
Run the model to do the design.

## Slide 28
Constraints
Velocity

## Slide 29
Slope

## Slide 30
Diameters

## Slide 31
Cover depth :

## Slide 32
Results
Velocity
Chart: 

## Slide 33: Slope

## Slide 34: Cover depth

## Slide 35
Profile

## Slide 37: Reusing treated wastewater in Agriculture
The treated water is used to irrigate different types of plants such as, olive, almond, citrus, walnut and pomegranate trees.
80% of the trees in Hajah area is planted olive trees type K18 and almond trees.
Each donum needs 500 m3/year.
Hajah wastewater treatment plant can irrigate around 435 donum of agricultural areas.

## Slide 38
Thanks…