## Slide 1: An-Najah National University Faculty Of Engineering Civil Engineering Department Graduation Project II
Analysis and Redesign of Water Distribution Network and Design of Wastewater Network for Zaita Village
Prepared By :
Ahmad Shtaiwi
Ahmad Zaid
Ali Al-Khateeb
Date :30/12/2020
Supervision of Eng. Hamees Tubeileh

## Slide 2: Outline:
Objective of the project.
Study area.
Questionnaire analysis.
Analyzing the water distribution network.
Redesign of water distribution network.
Design of wastewater collection network.
Summary.

## Slide 3: Objective
Analyze the existing water network.
Redesign the water network in the town.
Design of wastewater collection network.

## Slide 4
Study area

## Slide 5: Study area
Location : Zaita town is located 14 kilometers to the north of Tulkarm.
Climate : The annual average maximum temperature is 27Co and the annual average minimum is 16Co

## Slide 6: Topography

## Slide 7: Study area
Population : The total population of the town was 3500 capita in 2017.
Water resources : Zaita town have three wells and it sells water to the near villages .

## Slide 8: Study area

## Slide 9: Questionnaire analysis

## Slide 10: Questionnaire analysis

## Slide 11: Questionnaire analysis
Chart: 
Chart: Sample distribution according to the neighborhood
Chart: Sample distribution according to the neighborhood
| Eastern | Midtown | Northern | Southern | Tahta | Western
 | 0.1111 | 0.0741 | 0.2778 | 0.1481 | 0.1111 | 0.2778

## Slide 12: Questionnaire analysis
Chart: Sample distribution according to monthly income
| Less than 2500 | 2500-5000 | More than 5000
 | 0.185 | 0.4444 | 0.37037

## Slide 13: Questionnaire analysis
Chart: Quality of Water
Chart: Sample distribution according to daily consumption level
| Low | Medium | High
 | 9 | 37 | 8

## Slide 14: Questionnaire analysis
Chart: Main Water Problem
Chart: Sample distribution (tap drinking)
| yes | no
 | 0.8888 | 0.1112

## Slide 15: Questionnaire analysis
Chart: Problems in WDN
| yes | no
 | 0.2222 | 0.78

## Slide 16: Questionnaire analysis
Chart: Dissatisfaction with water
| yes | no
 | 12 | 42

## Slide 17: Questionnaire analysis
Chart: Reason of dissatisfaction
| taste | color | smell
 | 7 | 3 | 2

## Slide 18: Questionnaire analysis
Chart: Sample distribution according to the taken action
| boiling | adding chlorine | filter with a cloth | use water filter
 | 1 | 1 | 1 | 3

## Slide 19: Analyzing the Network

## Slide 20: Modeling of WDN
Year | Population
1997 | 2852
2007 | 3231
2017 | 3500

## Slide 21: Modeling of WDN
The present population is about 3570 so the growth rate according to the following equation is about 0.9905%
Year | Population
2012 | 3394
2013 | 3428
2014 | 3462

## Slide 22: Modeling of WDN
Year | Flow Rate(M3/Year)
2012 | 155083
2013 | 186913
2014 | 196949

## Slide 23: Modeling of WDN
For example in 2012 Q =155083000 L/year
Consumption =155083000/(3394*365) =125.2 L/C.d
In 2013 and 2014 consumption 149.4 & 155.86 L/C.d respectively
So the average consumption is 143.5 L/C.d
Present population (2019) = 3570 capita
Water consumption average = 143.5 Littre /Capita.day
Percent loss in network from municipality =18%

## Slide 24: Modeling of WDN
From the municipality the agricultural use is about 427 m3/day .
The total use for the town is 1052 m3 /day.

## Slide 25: Modeling of WDN

## Slide 26: Drawing The Network Using WaterCAD

## Slide 27: Drawing The Network Using WaterCAD

## Slide 28: Modeling of WDN

## Slide 29: Demand on Nodes

## Slide 30: The Pattern Demand Values

## Slide 31: Statistics Summary
Reservoirs | 1
Nodes | 102
Pipes | 117
Valves (FCV) | 0

## Slide 32: WDN
Design constraints:
Pressure at junction between (20-100) m.H2O.
Velocity in pipe (0.3-3.0) m/s.

## Slide 33: Result of analysis of WDN
Pressure at minimum demand (4:00 am).
Chart: Nodes

## Slide 34
Pressure at maximum demand (2:00 pm).
Chart: Nodes

## Slide 35: Result of analysis of WDN
Velocities at minimum demand (4:00 am).
Chart: 

## Slide 36
Velocities at maximum demand (2:00 pm).
Chart: 

## Slide 37: Redesign of WDN

## Slide 38: Data of future population
Future population in 2039 = 4348 capita
The average municipal consumption is 120 L/C.D
Demand =120*4348/1000=521.76m3/day
Supply = demand / 1-UFD
=521.76 / 1-0.15
=613.83 m3/day + 427m3/d=1040.83m3/d
For each junction, demand = current demand * factor
Factor = *
= *
= 1.02
= 1.02*1052
= 1073 m3/Day

## Slide 39: Model of WDN

## Slide 40: Drawing The Network Using WaterCAD

## Slide 41: Run statistics summary

## Slide 42: Design Criteria
Pressure criteria from 20 to 100 mH2O.
Velocity criteria from 0.3 to 3 m/sec.

## Slide 43: The pump definition carve

## Slide 44: Results of WDN for Design
pressure at 2:00PM. (high Demand)
Chart: 

## Slide 45: Results of WDN for Design
pressure at 4:00AM. (low Demand)
Chart: 

## Slide 46: Results of WDN for Design
velocity at 2:00PM (Maximum demand)
Chart: 

## Slide 47: Results of WDN for Design
velocity at 4:00AM (Minimum demand)
Chart: 

## Slide 48: Cost estimation
An example :
Pipe 3 length = 27 m
Pipe 3 diameter = 4 inch
The cost of pipe = 27 *65= 1755 NIS
Pump cost depend on pump flow and pump head our pump costs about 25000 NIS
Sum= 25000 +total pipes cost
= 25000 + 371791
= 396791 NIS
=113369$

## Slide 49: Design of Wastewater Network

## Slide 50
WWCN
Conduites
Manholes
Outfalls
Length <=30
Diameter>=8in
Material (PVC)
n
Diameter
Drop Manhole
Material
Loads
Elevation
Location
Elevation
Slope

## Slide 51: Wastewater Generation
From the State Of Palestine Water Authority (PWA), the average municipal consumption is 120 L/C/Day.
Design period 20 years.
PF = so we take PF = 3.
85% of produced waste water from consumed water.
20% infiltration.
Total flow for the town 1419m3/day

## Slide 52: Design Criteria
The velocity : (0.6 – 3 m/sec)
The cover : (1-5m)
The slope : (1-12%)
The distance between manholes are less than 30 m.

## Slide 53: Model of the wastewater network

## Slide 54: Model of the wastewater network

## Slide 55
Loads on manholes
So the load on each manhole is = = 3.256 m3/day.
The load was entered on the manholes equally through sanitary load control center in SewerCAD program.

## Slide 57: Conduit Catalog

## Slide 58: Outfall
After we located the network we put our outfall in the lowest point in the network due to topography and elevation variation.(invert elevation = 64.5m, ground elevation = 65m)

## Slide 59: Profile

## Slide 60: Profile

## Slide 61: Profile

## Slide 62: Results

## Slide 63: Slope Result
Chart: 

## Slide 64: Velocity Result
Chart: 

## Slide 65: Cover Result
Chart: 

## Slide 66: Cost Estimation

## Slide 67: WWCN COST
CONDIUT SIZE (INCH) | COST(NIS)
8 | 75
10 | 105
12 | 160

## Slide 68: WWCN COST
An example of estimation the cost of (WWCN)
conduit 13 length = 17.8 m
conduit 13 size = 8 inch
The cost of conduit = 17.8 *75= 1335 NIS
Total cost = 522610.5 NIS
=149317$

## Slide 69: Summary

## Slide 70: Summary
We designed the water distribution network where the number of nodes 104 is and the number of pipes 118 is with a total cost of conduits just as a material
= 113369$
We designed the waste water collection network with number of manholes 439 and number of conduits 439 with total cost of conduits just as a material
=149317$