## Slide 1: An-Najah National University Faculty Of Engineering Civil Engineering Department
HYDRULIC STUDY OF WATER NETWORK FOR SHWAIKA
Prepared By :Raya Freij
Supervision of Dr. Anan Jayousi

## Slide 2: introduction
Water is the most basic and important need of life

## Slide 3: Objective
Analyze the existing Water network in shweikah and modify it to meet the requirement for 30 years .

## Slide 4
Study area

## Slide 5
Shweika suburb 2.5 km to the north of the city of Tulkarm. The region altitude ranges between 61 MSL in the west and 156 MSL at the east. It follows administratively to the province of Tulkarm
The most popular well is Almesnawe well which supply area with drinking water

## Slide 6
Collecting Data
Topographic map
Water network map
Aerial photo
Data regarding the network
Data regarding water sources in the area.
Population
Tulkarm Municipality

## Slide 7
Questionnaire
110 houses
the questionnaire include questions to measure the per capita water consumption ,the performance of the network ,the problems and the quality of water

## Slide 8
Computing Demand
Population in 2007 according to PCBS is 8540
Population=8540(1+2.5%)^10=10932
From questionnaire the per capita consumption equal 0.118 m^3/c.day
UFW=33%
Supply=(10932*0.118)/(1-0.33)=1925.34 m^3/day

## Slide 9
Modeling
WaterCAD Program
Building the Model using Model Builder tool

## Slide 10
Read elevation of junctions from TRex:

## Slide 11: Demand of each node

## Slide 12
A logical demand pattern and multipliers has been obtained

## Slide 13
The minimum flow is during the period (2am -6.5am)
The maximum flow is during the period (15pm-16pm).

## Slide 14: For modeling pumps we insert it as an elevation to the reservoir: Elevation of Reservoir +head of the pump =99.37+120=219.37m.

## Slide 15: Model for existing net work is ready run

## Slide 16: Pressure results

## Slide 18: Velocity results

## Slide 20: Future Water Supply Network

## Slide 21
Design Criteria
*The velocities should be in the range of (0.2-3.0)m/s. *The pressure limits are in the range of (20-100) m. *Pipes used in the network are made of Steel and HDPE. *Growth rate in the west bank is about 2.5%.

## Slide 22: Growth estimation Design period (n) =30 years. Population now P｡=10932. Growth rate (r) 2.5%.  P｡(1+r)^n =10932 ×1.025^30= 22931.

## Slide 23: Calculating future demand

## Slide 24: Assume Domestic Consumption=120 L/C/D. As Domestic Consumption is 90% of Municipal L/C/D.

## Slide 25: Assume Physical Losses =15%. Supply == 157.64 L/C/D.

## Slide 26: Future Factor (F)= ==2.8 Future Demand =2.8 ×Demand now =2.8×1925.34=5390 /day.

## Slide 27: distribute Future Demand between junctions Run the model

## Slide 28: Future Pressure results

## Slide 30: Future Velocity results

## Slide 31
Chart: Velocity m/s

## Slide 32: Recommendations There is some pipes should be replaced by a larger one to solve velocity problem .

## Slide 33
# | D old | D new
P-271 | 4 | 6
P-78 | 3 | 4
P-2 | 3 | 4
P-3 | 3 | 4
P-16 | 3 | 4
P-17 | 3 | 4
P-221 | 3 | 4
P-222 | 3 | 4
P-280 | 1 | 2
P-18 | 2 | 3
P-286 | 2 | 3
pipes-112 | 2 | 3

## Slide 34: Run

## Slide 35: Pressure results

## Slide 37: Velocity results

## Slide 40: Cost Estimate

## Slide 41
material | D | Cost(shekels)/m
steel | 0.75 | 10.5
steel | 1 | 13
steel | 2 | 34
steel | 3 | 45
steel | 4 | 70
steel | 6 | 105
steel | 8 | 160
steel | 10 | 200
steel | 12 | 240
hdpe | 1 | 13
hdpe | 2 | 25

## Slide 42
# | D old | D new | Length | Cost/m | Cost(shekels)
P-271 | 4 | 6 | 10 | 105 | 1050
P-78 | 3 | 4 | 89 | 70 | 6230
P-2 | 3 | 4 | 381 | 70 | 26670
P-3 | 3 | 4 | 24 | 70 | 1680
P-16 | 3 | 4 | 188 | 70 | 13160
P-17 | 3 | 4 | 129 | 70 | 9030
P-221 | 3 | 4 | 118 | 70 | 8260
P-222 | 3 | 4 | 73 | 70 | 5110
P-280 | 1 | 2 | 336 | 34 | 11424
P-18 | 2 | 3 | 11 | 45 | 495
P-286 | 2 | 3 | 339 | 45 | 15255
pipes-112 | 2 | 3 | 467 | 45 | 21015
 |  |  |  | Σ | 119379