## Slide 1: Design for paltel company in Nablus
Prepared By:
Mohammed halabi basel abbas
Supervisor: Eng. Hind tbaileh
Faculty of Engineering & Information Technology
Department of Building Engineering
An-Najah National University

## Slide 2: Contents:
Site analysis
Architectural Design
Environmental Design ( thermal design )
Mechanical system Design
Safety design
Environmental design ( ACOUSTIC )
Structural system Design
Electrical design

## Slide 3: Architectural design
Site analysis
The site is located at the east of Nablus city, east of Nablus near to (Aljunaid Prison), it’s to the north of Rafidia street, about 520m above sea level and 3.2 kilometers away from city center. The Site has a total area of 1089 m2.

## Slide 4
3D model

## Slide 5
3D model

## Slide 6: Ground Floor

## Slide 7: First Floor (archive)

## Slide 8: Second Floor ( the repeated office floor )

## Slide 9: The 7th Floor

## Slide 10: site plan

## Slide 11: Southern Elevation

## Slide 12: Northern Elevation

## Slide 13: Eastern Elevation

## Slide 14: Section A-A

## Slide 15: Section B-B

## Slide 16: Environmental Design
Thermal Design
Old U value for building envelope
Component | U-value (w/m2-k)
External Wall | 2.624
Partition Wall | 2.685
Floor | 2.585
Roof | 0.85
Windows (Clear glass 4 mm ) | 3.097
Component | U-value (w/m2-k)
External Wall | 0.458
Partition Wall | 1.582
Floor | 0.268
Roof | 0.498
Windows (Double glass, low e, 6 mm) | 1.960
New U value for building envelope

## Slide 17
Design Builder program ( 3D Model )

## Slide 19: Shading
The overhang was used for shading with 0.36 m projection

## Slide 20
Heating and cooling load
Cooling load 85.4 kw
Heating load 41.9 kw
Site and Source Energy
Thermal Design
Old total site energy
New total site energy

## Slide 21
Times not Comfortable
Old time not comfortable
New time not comfortable

## Slide 22: Mechanical Design

## Slide 23: Water demand = 3.225 /day
Water Supply System

## Slide 24
Rain Water Drainage

## Slide 25: (HVAC (System
VRF system
Outdoor unit Selected From Toshiba company with
Cooling capacity 135 kw
Heating capacity 150 kw
(SMMSi ) MODEL NO: MMY-AP4824HT8-E

## Slide 26: (HVAC (System
VRF system
Fan coil From Toshiba company depending
on volumetric flow rate for each space.
great power up to 28 kw

## Slide 27: Second floor HVAC system layout

## Slide 28: Firefighting and Safety Design

## Slide 29
Sprinkler System
Sprinkler System
for Ground Floor

## Slide 31
Sprinkler System
for second Floor

## Slide 32: Quantity Surveying and Cost Estimation for mechanical and finishing

## Slide 33
Directorate of Health | Total labor cost | Total material cost | Total Direct Cost (Nis)
Mechanical Work | 56288 | 185560 | 241,848
Finishing Work | 434031 | 1221283 | 1,655,314
Total direct project cost |  |  | 1897162
Cost Estimation

## Slide 34: Acoustics Design

## Slide 35
RT60 (Reverberation Time)
Old Spaces
New Spaces

## Slide 36
RT60 (Reverberation Time)
Absorption of materials

## Slide 37
RT60 (Reverberation Time)
Recommended
Reception
(0.4-0.8)
Old RT60 Values for Reception
New RT60 Values for Reception

## Slide 38
RT60 (Reverberation Time)
Old RT60 Values for meeting room
New RT60 Values for meeting room
Recommended
meeting room
(0.6-.1.1)

## Slide 39
STC
For External Wall of office
TL = 50 dB
External Wall
Recommended Value 52dB

## Slide 40
STC
For adjacent offices
TL = 46 dB
Internal Wall
Recommended Value 45 dB

## Slide 41
IIC For Ceiling
IIC = 70 dB

## Slide 42: Structural Design

## Slide 43: Codes and Loads
  Loads
  Live Load = 4 kN/𝑚^2
  SID = 4 kN/𝑚^2
  Eq Load coefficients:1.2 DL + 1.2 SID + 1.6 L.L
  R = 5.5 ,
  I = 1
  Z = 2B (Nablus) =.2 ,
  Cv= 0.40 ,
  Ca = 0.28
  Soil Profile ((SD))
Codes
• ACI 318-14 for reinforced concrete elements
• UBC 97 for design of Seismic load, Load combinations.

## Slide 44: Structural system
Materials
Concrete , B350
Steel fy = 420 Mpa
Structural System
One Way Ribbed Slab
Final Design Sections
Slab thickness 35 cm
Beams dimensions ( 35 * 60 & 35* 50 & 80*35 &50*70 &70*70 & 20*50 ) cm
Columns dimensions ( 100*40 & 90*30) cm
Walls Thickness 35 cm

## Slide 45: 3D-Modeling

## Slide 46: Model Checks
1…Compatibility Check

## Slide 47: Model Checks
Done for Dead (.016), SID(.035) and Live load(.035) with difference less than 5 %.
2…Equilibrium Check
3…Internal Forces Check
Done for 2 samples of beams and columns with difference less than 10%

## Slide 48: Model Checks
4…Deflection Check
Limit = L/240
= 6.5/ 240 = 27 mm
14.746

## Slide 49: Model Checks
5…Period Check
Period from ETABS = 0..792 sec.
Period from hand calculation= 0.594
T from ETABS < 1.4 from hand calc.
0.792 sec.< 0.8316 sec.

## Slide 50: Slab Reinforcement

## Slide 51: Slab Reinforcement

## Slide 52
Beams Reinforcement

## Slide 53
Beams Reinforcement
B3
B4
B5ا
B6

## Slide 54
c1
Columns Reinforcement

## Slide 55
Columns Reinforcement

## Slide 56
Footing Reinforcement

## Slide 57
Footing Reinforcement

## Slide 58: Footing Reinforcement

## Slide 59: Ground Beams Detailing

## Slide 60
Shear Wall Reinforcement

## Slide 61
Stairs Reinforcement

## Slide 62: Structural Consumption Estimation
Total | Labor | Material | Type
3250958 | 1100818 | 2150140 | Structural

## Slide 63
Past and New Design
Past
Not Designed For Seismic Load
New Design
Earth quick Design Based
Structural Elements compatible with architectural purposes
Lower construction cost

## Slide 64: Electrical Design

## Slide 65: First Floor socket plan

## Slide 66: First Floor ups plan

## Slide 67: First Floor Lighting Plan

## Slide 68: Luminaires Layout
Old Main Luminaire
New Main Luminaire
95
57
49.4

## Slide 69: 3D Rendering View for Selected Rooms
meeting Room
Receptipn

## Slide 70: meeting Room
Average Illuminance
577 Lux
UGR = 16
Required illuminance 500 lux
Required uniformity (>0.60)

## Slide 71: Power Consumption Estimation
Electricity Consumption Estimation

## Slide 72
Thank You