## Slide 1
Power Electronics Transformer
PET/Solid State Transformer (SST)
Presented by:
Amro Aqra, Marwan Hamad, and Noor Hamdan

## Slide 2
This section will feature a concise and brief introduction to what is a PET. Its importance in terms of applications and various topologies will be discussed as well.
Introduction to PET and its applications
01
This section will talk about the key component within a PET that is needed to achieve many of its desirable characteristics.
Dual Active Bridge (DAB) Convertor
02
This section will discuss all the methods and steps taken in order to bring a functioning model into existence.
Methodology
03
Conclusion and Future Work
06
Results Comparison
05
This section will discuss all the results that were noted in both theoretical and experimental stages and will compare between them.
Hardware Showcase
04
This section will present the hardware used as well as the system built in addition to the codes that will be used.

## Slide 3
Introduction to PET

## Slide 4
A solid-state transformer (SST) is essentially an AC-to-AC converter, a type of electric power converter that replaces a conventional transformer used in AC electric power distribution. The basic idea of the SST is to achieve the voltage transformation by medium to high frequency isolation, therefore to potentially reduce the volume and weight of it compared with the traditional power transformer.
A PET boasts a more complex design than the normal transformer hence its reduction in size. It’s made out of three stages to be exact. A rectifying stage that turns the input AC signal into a DC signal. Then followed by a powerful high frequency transformer (HF) in order to provide the needed isolation and give the ability to step up/step down the voltages in accordance to the needs at hand. Finally, there’s an inverting stage that returns a higher AC voltage.
The solid-state transformer (SST) is one of the key elements in power electronic-based microgrid systems.
The PET opens up the opportunity for an easier integration because it makes use of power electronics in its design, meaning that there will be a significant reduction in the transformer’s volume. It also boasts a number of added features on top such as power management, energy management, fault management, and much more.

## Slide 5
It makes use of the same concept as the type B topology in having two stages implemented. It offers a high voltage DC-link only.
Type C
The above-mentioned topologies has led researchers to investigate a new method in which could equip the PET with the flexibility to be used in various scenarios. This has led to the development of type D; a three-stage PET that utilizes cascaded multi-level converters with the integration of the DAB convertor as well.
Type D
PET Topologies
Fig 1.4: Types of PET.
It’s the earliest form of the PET technology. It offers no DC-link capacitors whatsoever. This topology consists of one stage only. This particular topology boasts the best efficiency. However, this comes at the cost of not making use of any DC devices on the low voltage side nor can it be used for higher voltage applications on the high voltage side.
Type A
It introduced the aforementioned DC-link on the low voltage side. This was done by having this method consist of two stages. This kind of topology enabled the integration of many DC devices with the PET in the form of batteries, PVs, and other DC devices. Though the lack of the high voltage DC-link will render it ill-suited for the integration of high voltage operations.
Type B

## Slide 6
Functional View of PET
Fig 1.5: Type D topology.

## Slide 7
PET Characteristics
Bidirectional power flow
This attribute makes the PET so it can be used to feed the grid with power accumulated from DC storage devices such as batteries or PV systems. The ability of the PET to control the reactive power and provide compensation for it makes it fit for such utility applications by regulating the terminal voltages.
Other attributes
Since the PET is capable of fault isolation, harmonics isolation, power flow control, and status monitoring, it is to be expected that a form of high efficiency fast charger for electric cars to be introduced.
Compact System
The PET operates at higher frequencies as it has been mentioned before. The consequences of this is that the volume is inversely proportional to the frequency. The higher the frequency, the less the volume would be and since the high frequency (HF) transformer doesn't have to maintain a lot of flux when the frequency is high the less the core size will be.
Ability to drive a number of DC devices
It can be used to integrate various renewable energy resources into the network.

## Slide 8
Smart Grid Integration
The PET transformer will enable an easier integration of renewable energy resources and distributed energy storage devices. Only single-stage conversion is needed compared with the normal AC grid.
Fast Charging Station
Normally, a transformer, AC/DC, and DC/DC converter are used to charge the electric vehicle; the efﬁciency of such a system is ∼90%. Using the PET technology, the efﬁciency can be pushed to be >95%. It can also substantially decrease the weight, and cost is reduced to half of the conventional technology
PET Applications
Fig 1.1: PET applications.
Fig 1.2: PET applications.

## Slide 9
Reactive Power Compensation and Active Filtering
The PET can also offer VAr compensation depending on the topology adopted. It can be implemented and provide active power transfer, reactive power compensation, and voltage conversion functions.
Integration of a number of DC devices
With the constant increase and dependability on more clean energy over the fossil fuel counterpart, the PET can also be adopted to directly connect with the distribution systems of tidal, and solar plants alike. This would mean a more compact system that has features such as voltage stabilization capabilities.
Fig 1.3: More applications.

## Slide 10
Dual Active Bridge (DAB) Convertor

## Slide 11
Dual Active Bridge (DAB) Convertor
The DAB convertor is a DC/DC convertor that enables the full potential and a variety of technologies that can be incorporated into the PET. The DAB in particular is an ideal piece of technology that is suitable for bidirectional transfer of power with multiple control strategies that can be used to further improve the efficiency of this device. It’s most essential to the PET in order to give an edge compared to the conventional transformer.
The DAB convertor has two types. A non-isolated version and an isolated version. The former doesn’t have a transformer. That version of the DAB suffers from a significant amount of ripple to the current. The latter however, consist of capacitors, filters, as well as a high frequency transformer.
Fig 2.1: DAB DC/DC convertor circuit.

## Slide 12
During the third interval, switches S3 and S2 are in operation in the first bridge so the voltage across the primary side is equal to –V1 as the current is leaving the transformer. Of course, S5 and S8 are still in operation during that time so the voltage across the secondary side will be equal to –V2 as explained previously.
Third Interval
Finally during the fourth and final interval, switches S3 and S2 are in operation in the first bridge so the voltage across the primary side is equal to –V1 as the current is leaving the transformer. Although in the secondary side, switches S6 and S7 are back in operation making the current leave the transformer resulting in the voltage having the value of V2.
Fourth Interval
The current enters the transformer in the primary side and so the voltage across the primary side is equal to V1. The voltage across the secondary side is equal to V2 also because the switches S6 and S7 make it so that the voltage leaves from the transformer.
First Interval
During the second interval, S1 and S4 are still in operation so the voltage across the primary side is equal to V1. However, the switches working in this interval are S5 and S8. What this entails is that the voltage across the secondary side will be different as the current enters the transformer back, it’ll be negative and be equal to –V2.
Second Interval
PET Characteristics
Switching Sequence

## Slide 13
The figure above depicts the behaviour of each switching interval as well as the overall scheme of the leakage inductance current as well as the voltages on both the primary and secondary sides
Fig 2.2: The complete switching behaviour of the DAB convertor.

## Slide 14
Methodology

## Slide 15
The table below provides the information about the design parameters that were picked for the DAB convertor to fulfil in simulation using Matlab.
DAB Convertor Parameters
Phase shift | -0.44< Φ<0.44 (rad)
Total Leakage Inductance | 616 μH
Turns Ratio | 1:0.625
Load resistance | 66 Ω
Input Voltage | 800 V
Output Voltage | 500 V
Input Current | 12.5 A
Output Current | 20 A
Output Power | 10k W
Table 2.1: Key system constraints.
Table 3.1: DAB parameters.

## Slide 16
Design Considerations
Switching Frequency
The higher the value of the frequency the less losses the system will have. The high frequency will also help in making the system be reduced in size.
Transformer Selection
The transformer is one of the main components in the DAB convertor and the PET transformer as a whole as it replaces the conventional transformer and offers the ability to fulfil the requirements of the high power, high frequency requirements needed for the system. The following table provides information about its parameters:
Selection of Switching Device
The selection of the switching device was opted to be IGBTs and this can be attributed to a number of reasons. They are the best choice when dealing with high voltages (>1000 Volts), they can withstand a high temperature of 100+°C.
Phase Shift
The phase shift is one of the values that impact the power transfer between the two bridges and it also controls the direction of the power.
Capacitor Selection
In the DAB convertor, the DC-link capacitors are used in order to provide a more stable DC voltage, limiting its fluctuations. They also act as a filter to reduce the ripple in the DC link voltage.
Functional specifications | Ratings
Total output power | 10k W
Operating frequency | 5k Hz
Magnetizing inductance | 3000 μH
Magnetizing Resistance | 1000 Ω
Input Voltage of the transformer | 800 V
Primary-to-secondary ratio | 24:15
Primary winding DC resistance | 43m Ω
Secondary winding DC resistance | 16m Ω
Leakage inductance | 315 μH
Table 3.2: High Frequency Transformer parameters.

## Slide 17
The figure below presents the DAB convertor that was constructed using Matlab’s Simulink.
PWM modulation inside of Matlab was as follows:
The formula used in order to set up the PWM goes as follows:
Fig 3.2: PWM modulation inside of Matlab.
Fig 3.1: DAB converter in Matlab.

## Slide 18
Hardware Showcase

## Slide 19
Hardware Showcase
As it has been mentioned before, the system consists of the DAB converter as well as the inverting stage. In order to construct the system, the IC of L298N Motor Driver was used to make the stages. The IC module looks like this:
The block diagram of the L298N Motor Driver IC is as follows:
Fig 4.1: The L298N Motor Driver IC.
Fig 4.2: Block diagram of the L298N IC.

## Slide 20
Hardware Showcase
The hardware that was built will also be shown below. It should be noted that the finished prototype consist of the DAB converter that’s the two IC stages located on the right while the last inverting stage with its transformer is seated on the left
Fig 4.4: The inverter stage.
Fig 4.3: The DAB converter stage.

## Slide 21
Hardware Showcase (DAB Stage Code)
The code that needs to be used in order to operate the first two stages will make use of the the pulses coming from the Arduino. And in order to achieve that, the Interrupt Surface Routine (ISR) functionality within the microcontroller was used. the code will use a counter that have a limit of counting between 0 up until 10 before it resets as it will provide 5 instances of the pulses being at value of HIGH. These will represent half of the 5k Hz frequency. The other 5 instances will represent the value of LOW that represents the remaining half. The code’s flowchart is presented as follows in the upcoming slides.

## Slide 22
Fig 4.5: The flowchart of the Arduino pulses code.
Fig 4.6: The continuation of the flowchart of the Arduino pulses code.

## Slide 23
Hardware Showcase (Inverter Stage Code)
This time around, the code that would make it operate will make use of the SPWM technique. The SPWM technique is implement by having the sinusoidal signal be traced by providing two PWM pulses that have their duty cycle be dynamically changed in order to trace the highest values of a normal sine signal. The implementation of the SPWM signals on the Arduino will make use of an SPWM generating library that can change the fundamental frequency, switching frequency, and amplitude of the PWM. This allows for various outputs without any tap changers.
Fig 4.7: The flowchart of the SPWM code.
Fig 4.8: The continuation of the flowchart of the SPWM code.

## Slide 24
Results Comparison

## Slide 25
Simulation Vs. Experimental
In this section, the results that were obtained from Matlab simulations and the results obtained by having the system be assembled will be put against each other for comparison purposes. The first comparison will be between the results obtained from the output of the first stage of the DAB converter.
These simulation results start with the voltage across the high frequency transformer as can be seen from the figure below. The value of the voltages hovers around 500 volts with very little ripple to distort it.
This following figure however shows the square wave output of the first stage. The input voltage that was around 13 volts. And the figure above confirms that the H-bridge is working correctly as it alternates between giving the positive and negative values of the Vinput. It is easy to notice that the values matched with the theoretical values that were observed during the simulations.
Fig 5.1: The voltage across the High Frequency Transformer.
Fig 5.2: The square wave output of the first stage.

## Slide 26
Simulation Vs. Experimental
The next comparison will be between the results of the voltage obtained from the output of the DAB converter during simulation and the experimental outputs. It should be noted how the two stages of the DAB converter were connected through an inductor for simplicity’s sake instead of a high frequency transformer.
The output voltage of the simulation showed a steady value of 500 Volts DC on the output of the DAB convertor that can be later used to hook different components into it or be used in a control mechanism. The figure below shows that the voltage in question suffers from very little ripple so it’s within the design’s specifications.
The two stages of the DAB converter were made by having connecting the output of the first stage to the second IC through an inductor for simplicity sake. It should be noted that the output of the first stage was connected to the “output” pins of the second stage and the output of the DC-DC converter was measured between the “12 Volts” and “GND” pins of the second IC. As it can be seen above, the DC output can be observed as it trails around just shy of 12 Volts. This would give an observed efficiency of 91%. And it matches the simulated values.
Fig 5.3: The output voltage.
Fig 5.4: DC output of the DC-DC converter.

## Slide 27
Additional Simulations
As it can be seen from the table, the values that were specified for the system have been reached with an efficiency value of almost 97%. Conducting this experiment also showed that the phase shift value is what controls the output current while the duty cycle is what controls the voltages.
The following curve shows the system efficiency as a function of output power.
Input current (A) | Input power (W) | Output current (A) | Output voltage (V) | Output power (W) | Efficiency | Load resistance (Ω)
4.2 | 3360 | 19.91 | 159.2 | 3169.672 | 94.3% | 10
6.875 | 5500 | 19.83 | 266.6 | 5286.678 | 96.1% | 20
11.21 | 8968 | 19.74 | 445.9 | 8802.066 | 98.1% | 50
12.25 | 9800 | 19.72 | 481.8 | 9501.096 | 96.9% | 60
12.71 | 10168 | 19.71 | 500.1 | 9856.971 | 96.9% | 66
Further simulations were conducted using the Matlab model that was built in order to perfect the power output values. Those simulation values are shown in here.
Table 5.1: The results table.
Fig 5.8: The efficiency vs. power.

## Slide 28
Inverter Stage
In the inverter stage, the code that would make it operate will make use of the SPWM technique. The SPWM technique is implement by having the sinusoidal signal be traced by providing two PWM pulses that have their duty cycle be dynamically changed in order to trace the highest values of a normal sine signal.
The implementation of the SPWM signals on the Arduino will make use of an SPWM generating library that can change the fundamental frequency, switching frequency, and amplitude of the PWM. The inverter stage also consisted of the same IC used previously.
By hooking up the pulses of the Arduino to the IC, the output of the H-bridge yielded the following results:
The figure shows the signal that is the output of the inverter as it shows that it needs a filter in order for it to provide a sinusoidal signal at the output.
Fig 5.5: Output of inverter after it’s been given the pulses.

## Slide 29
Simulation Vs. Experimental
The next comparison will be between the results of the voltage obtained from the output of the inverter stage during simulation and the experimental outputs. It should be noted that a filter was constructed in both cases.
The output voltage of the simulation is presented above as the values to pick the correct values for the filter were obtained and thus utilized later on to create the filter needed to obtain such a signal.
By plugging the output of the inverter into an LCL-filter, the figure above was obtained by using the PicoScope. As it was mentioned in the previous slide, this shows how the signal obtained at the output of the inverter stage can be turned into an almost pure sinusoidal signal by using the correct filter values. And clearly the experimental results matches the theoretical ones obtained from simulation.
Fig 5.6: Sinusoidal signal after it’s been filtered in MATLAB.
Fig 5.7: Sinusoidal signal after it’s been filtered.

## Slide 30
Testing The Entire System
Now that comparisons have been done between the simulation and experimental results, it is time to start hooking up the DC-DC conversation stage with the inverter stage in order to observe the system’s behaviour. After having doing that, various values will be put on measuring equipment that trace all the important outputs to look at. And the output of the inverter stage will be also put to a 12V/220V transformer that will be put through a filter.
The input voltage of the DC-DC converter was set to 12.6 Volts this time around. It was hooked to the inverter stage by its “12 Volts” and “GND” pins available on the IC.
The following observations were recorded and put in a table to organize the results. The tests conducted were put into two categorizes. The first testing was done in terms of changing the amplitude of the PWM that is given to the inverter stage that controls the output sinusoidal signal. The second testing was done by observing the output changes when a phase shift was introduced between the pulses in the DAB stage (phase shift between pulses between the first and second stage of DAB).

## Slide 31
01
Results When Changing Amplitude of PWM.
The change in amplitude was done using the code. The Figure shows the output of the signals that have been observed during this test of changing the amplitude of the PWM. First figure shows the output at 80% and the second shows the output signals at 30% amplitude. The yellow signal is the DC output of the first DC-DC converter stage. The red signal is the PWM output that is coming out of the Arduino and is connected the inverter stage. The pink signal represents the output of the inverter. And finally, the blue signal is the unfiltered output after it’s been passed through the transformer and it traces the output of the inverter to form the sinusoidal signal.
PWM Amplitude (%) | Voltage Output (V)
80 | 65
100 | 76
30 | 24
Table 5.2: The PWM amplitude impact on the output voltage.
Fig 5.9: Comparing the output of the different signals.
Fig 5.10: The output signals at 30% amplitude.

## Slide 32
02
Results When Changing The Phase Shift
The following table will provide an insight to what the phase shift does to the output voltage on the inverter. It should be noted that the amplitude of the PWM given to the inverter stage was a constant value of 80% in the code. The data observed using the measuring tools will also follow afterwards. The phase shift changed is that between the first and second bridges in the first DC-DC conversation stage. The results observed were as follows:
Phase Shift Value | Voltage Output (V)
20µ | 65
No Phase Shift | 70
40µ | 52
The first figure shows the output signals at no phase shift. The second one shows the values at 40µ phase shift.
Table 5.3: The phase shift impact on the output voltage.
Fig 5.11: Comparing the output of the different signals at no phase-shift.
Fig 5.12: Comparing the output of the different signals at 40µ phase-shift.

## Slide 33
Conclusion and Future Work

## Slide 34
In essence, this report mentioned why the PET has become an absolute sensation in the industrial section because of the enormous underlying potential it has when it comes to making the smart grids a reality.
PET is the future!
A lot of progress have been made in the realm of PETs in the past few years. As it is with any sort of new technology, multiple iterations need to be brought into existence in order to improve the reliability of it and this doesn’t undermine the great potential it harbours. As the technology continuous to get developed, it’ll also go down in cost making it easier to integrate the PET into the markets.
Surely the new type of transformer will be put into good use sooner rather than later. And most importantly, it is thought that the applications where size and weight are important will be the first applications to make use of the characteristics of the PET.
Obviously, a lot can still be done to improve upon the simulation of the PET that has been conducted. The hardware built was just a prototype that can be scalable in the future. In addition to that, future work may also include making use of many control techniques such as vector control and zero voltage switching can be adapted into the system to make it even more efficient. Additionally, analysis can be done on the stability of the system while having the PET be integrated into the power system.

## Slide 35
Thank You