## Slide 1: Analysis of Water Distribution Network and design waste water collection network for Al-Zababida
An-Najah National University Faculty Of Engineering Civil Engineering Department Graduation Project 2
Prepared by :
Ahmad Wael “Ali Hussein” Aysar Isbeih Mohammad Jamal Kmail
Supervisor:
Eng. Hamees Tubeileh

## Slide 2: Contents: -
Objective
Methodology
Overview of Al-Zababida
Questionnaire analysis
Modeling & analyzing current WDN now and after 30 year
Result of analyze WDN
Design waste water collection network
Problems that was solved

## Slide 3: Objectives : -
Analyze the exiting water distribution network.
Find the problems in WDN and suggest solution to solve these problems.
Redesign the water network in the town if it needs.
Design WWCN

## Slide 4
Analyze the existing conditions
Methodology : -
Make a questionnaire
Prepare data
Analyze after 30 year
Visiting study area
Design WWCN

## Slide 5: Overview of Al-Zababida : -
Location:
  Al-Zababida town is located 15 kilometers away southeast from Jenin city.
Population:
  The total population of the town was 4261 in addition to 1500 student coming from Arab Americana university in 2017.

## Slide 6: Overview of Al-Zababida : -

## Slide 7: Overview of Al-Zababida : -
Topography:
  Al-Zababida is located at a hill and surrounded by two mountains from south and west and flat from other sides.
Land Use:
  Most people in Al-Zababida mainly works in jobs, commercial side, agricultural work and quarries.
Climate :
  The annual average maximum temperature is 25Co and the annual average minimum is14Co.

## Slide 8: Overview of Al-Zababida : -

## Slide 9: The Questionnaire: -
Chart: level of education
| school degree | univercity certification | not educated
level education | 15 | 28 | 6

## Slide 10: The Questionnaire: -
Chart: source of water
| Municipality | municipality+gathering well | water tank
source of water | 32 | 16 | 1

## Slide 11: The Questionnaire: -
Chart: water quality
| excellent | very good | good | bad | very bad
water quality | 5 | 23 | 15 | 3 | 3

## Slide 12: The Questionnaire: -
Chart: 
Chart: pressure
| high | low | moderate
pressure | 26 | 13 | 10

## Slide 13: The Questionnaire: -
Chart: average consumption(L/C/D)
| garden+yard | garden | yard | nothing
 | 123 | 102 | 143 | 72

## Slide 14: The Questionnaire: -
Chart: consumption variation
| 5 | 1 | 15 | 5 | 12 | 11 | 5 | 4 | 5 | 7 | 8 | 3 | 8 | 3 | 6 | 6 | 3 | 5 | 6 | 5 | 3 | 5 | 8 | 14 | 5 | 9 | 5 | 3 | 7 | 7 | 7 | 1 | 5 | 7 | 5 | 5 | 6 | 2 | 4 | 7 | 2 | 6 | 8 | 5 | 7 | 4 | 7 | 5
 | 126.6667 | 166.6667 | 84.4444 | 66.6667 | 105.5556 | 151.5152 | 333.3333 | 50 | 66.6667 | 76.1905 | 104.1667 | 77.7778 | 125 | 122.2222 | 72.2222 | 83.3333 | 44.4444 | 53.3333 | 44.4444 | 53.3333 | 66.6667 | 66.6667 | 104.1667 | 90.4762 | 66.6667 | 37.037 | 166.6667 | 33.3333 | 119.0476 | 47.619 | 119.0476 | 33.3333 | 120 | 119.0476 | 66.6667 | 126.6667 | 88.8889 | 250 | 158.3333 | 238.0952 | 500 | 138.8889 | 66.6667 | 100 | 90.4762 | 66.6667 | 57.1429 | 66.6667

## Slide 15: The Questionnaire: - for student :
Chart: 
| excellent | very good | good | bad | very bad
water quality | 1 | 9 | 6 | 1 | 3

## Slide 16: The Questionnaire: -
for student :
Chart: 
| high | low | moderate
pressure | 8 | 5 | 2

## Slide 17: The Questionnaire: -
for student :
Chart: consumption variation
| 2 | 1 | 1 | 2 | 2 | 1 | 1 | 2 | 2 | 3 | 1 | 1 | 1 | 2 | 1
 | 66.6667 | 100 | 100 | 66.6667 | 83.3333 | 166.6667 | 100 | 133.3333 | 83.3333 | 122.2222 | 133.3333 | 200 | 166.6667 | 133.3333 | 100

## Slide 18: Analysis of the exiting network

## Slide 19: Modeling & analyzing of network : -
Water resources: -
  water is supplied by bought water from two wells, Al-Kharraz well located in Tubas city and governmental well located between Al-Zababida and Qabatiya city.
Water Tank: -
  The town has a one tank made from reinforced concrete with a capacity 500 lovated at 430m above mean sea level.
Water pumping: -
  The water supplied to the buildings is by the power of ground gravity.

## Slide 20: Collected Data :
Contour shape file from geomolge
Road network shape file
Building from the municipality as Auto CAD
Water consumption for the village from the municipality

## Slide 21: Modeling of network : -
Obtained the network by called the Network AutoCAD shape that was got from the municipality file then draw the network by distribution the junction and drawing the pipes .
1 tank (500 .
219 pipes (2,3,4,6) inches.
194 Junction.

## Slide 22: Demand calculations and distribution :
120119.5
Losses =
Losses =
The losses rate = 24%
.

## Slide 23: Demand calculations and distribution :
By using GIS program we calculated the surface area of the building that serve by each junction.
The total area of buildings from GIS is 155419.0442

## Slide 24: Demand calculations and distribution :
Demand on junction =
One sample calculation for junction 1
Demand = = 462.688 day
Junction Label | buildings area on each junction () | demand on each junction(day)
1 | 165.66 | 462.69
2 | 67.45 | 188.40
3 | 87.36 | 244.01
4 | 0.00 | 0.00
5 | 156.17 | 436.19
Junction Label |  | 
1 | 165.66 | 462.69
2 | 67.45 | 188.40
3 | 87.36 | 244.01
4 | 0.00 | 0.00
5 | 156.17 | 436.19

## Slide 25: analyzing of network : -
Use this pattern which taken from Ammar Kokhon

## Slide 26: Result : -
Velocity at 4:00 am Velocity at 2:00 pm
Chart: Pipe number
Chart: Pipe number

## Slide 27: Result : -
After 30 year
Pressure at 4:00 am Pressure at 2:00 pm
Chart: Junction number
Chart: Junction number

## Slide 28: Modeling & analyzing of network : -
Losses =
Losses =
The losses rate = 24%
.
.

## Slide 29: Future analysis for the existing network

## Slide 30: Data Collection :-
Take
.

## Slide 31: Modeling & analyzing of network after 30 year:-
For the distribution of the future population we assumed that the density of the building in middle areas ( main street area ) of the village will stay the same (fixed density areas)
the expansion in the building will be in the areas which its density is smaller than the middle areas (unfixed density areas)
the increased population will uniformly distribute in the unfixed density area

## Slide 32: Modeling & analyzing of network after 30 year:-

## Slide 33: Demand calculation and distribution after 30 years:-
For population for fixed density area:
𝑃𝑜𝑝𝑢𝑙𝑎𝑡𝑖𝑜𝑛 𝑓𝑜𝑟 𝑒𝑎𝑐ℎ 𝑗𝑜𝑖𝑛𝑡 =
𝑇𝑜𝑡𝑎𝑙 𝑃𝑜𝑝𝑢𝑙𝑎𝑡𝑖𝑜𝑛 = ∑ 𝑝𝑜𝑝𝑢𝑙𝑎𝑡𝑖𝑜𝑛𝑠 𝑠𝑒𝑟𝑣𝑒𝑑 𝑏𝑦 𝑒𝑎𝑐ℎ 𝑗𝑜𝑖𝑛𝑡 = 2744 persons
One sample calculation for junction 69
Population = = 52.55
Junction label | building area | Population (Capita)
59 | 1474.74 | 54.67
63 | 506.35 | 18.77
65 | 1200.26 | 44.49
69 | 1417.72 | 52.55
72 | 688.88 | 25.53
Junction label |  | Population (Capita)
59 | 1474.74 | 54.67
63 | 506.35 | 18.77
65 | 1200.26 | 44.49
69 | 1417.72 | 52.55
72 | 688.88 | 25.53

## Slide 34: Demand calculation and distribution after 30 years:-
For Population for unfixed density area:
In the same way in the fixed density we calculate the population on the junctions that serve these areas
𝑇𝑜𝑡𝑎𝑙 𝑃𝑜𝑝𝑢𝑙𝑎𝑡𝑖𝑜𝑛 = ∑𝑝𝑜𝑝𝑢𝑙𝑎𝑡𝑖𝑜𝑛𝑠 𝑠𝑒𝑟𝑣𝑒𝑑 𝑏𝑦 𝑒𝑎𝑐ℎ 𝑗𝑜𝑖𝑛𝑡 = 3017 persons
We assumed that the increased population will be uniformly distributed in the unfixed density area
𝑇ℎ𝑒 Increased 𝑝𝑜𝑝𝑢𝑙𝑎𝑡𝑖𝑜𝑛 = 𝑇𝑜𝑡𝑙𝑎 𝑝𝑜𝑝𝑢𝑙𝑎𝑡𝑖𝑜𝑛 𝑖𝑛 2048 − 𝑇𝑜𝑡𝑙𝑎 𝑝𝑜𝑝𝑢𝑙𝑎𝑡𝑖𝑜𝑛 𝑖𝑛 2018
𝑇ℎ𝑒 Increased 𝑝𝑜𝑝𝑢𝑙𝑎𝑡𝑖𝑜𝑛 = – 5761 = 3049 persons

## Slide 35: Modeling & analyzing of network after 30 year:-
These people will be served by the junctions that serve the unfixed density area so each of junction will serve extra persons:
= 3049 / 124 = 24.58 capita
One sample calculation for junction 3
Total Population = + 24.58 = 27.08
Junction label | building area | Current population (Capita) | Total population (Capita)
1 | 165.66 | 6.14 | 30.72
2 | 67.45 | 2.50 | 27.08
3 | 87.36 | 3.24 | 27.82
4 | 0.00 | 0.00 | 24.58
5 | 156.17 | 5.79 | 30.37
Junction label |  | Current population (Capita) | Total population (Capita)
1 | 165.66 | 6.14 | 30.72
2 | 67.45 | 2.50 | 27.08
3 | 87.36 | 3.24 | 27.82
4 | 0.00 | 0.00 | 24.58
5 | 156.17 | 5.79 | 30.37

## Slide 36: Modeling & analyzing of network after 30 year:-
After calculate the population served by each junction in future, we can calculate the demand for each junction
One sample calculation for junction 1 Total Demand = = 5.01 /day
Junction label | Population (capita) | Demand
1 | 30.72 | 4.85
2 | 27.08 | 4.28
3 | 27.82 | 4.39
4 | 24.58 | 3.88
5 | 30.37 | 4.79
Junction label | Population (capita) | 
1 | 30.72 | 4.85
2 | 27.08 | 4.28
3 | 27.82 | 4.39
4 | 24.58 | 3.88
5 | 30.37 | 4.79

## Slide 37: Result : -
After 30 year
Pressure at 4:00 am Pressure at 2:00 pm
Chart: Junction number
Chart: Junction number

## Slide 38: Result : -
After 30 year
Velocity at 4:00 am Velocity at 2:00 pm
Chart: Pipe number
Chart: Pipe number

## Slide 39: Design waste water collection network
Al-Zababida town doesn’t have a wastewater network
The terrain of the town allows to use gravity system, to let the wastewater goes downwards
The contour line of the town shows that the lowest point in the town located in north region.
SewerCAD software will be used to design the wastewater networks

## Slide 40: Design waste water collection network
The assumption that will considered in the design is: -
Design period 30years.
Future Population = 8810 capita.
120 L/c.d water consumption
80% of produced waste water from consumed water.
20% infiltration.
The maximum distance between manholes is 30m.
PVC circular pipes.

## Slide 41: Design waste water collection network
The constrains for the design of WWCN are:
Velocity between (0.6 – 3) m/s.
Cover between (1 – 5) m.
Slope between (1 – 4) %

## Slide 42: Design waste water collection network
Calculation:
PF =
m3/d
Total flow for the town 2706.5 m3/day
the load on each manhole = m3/day.

## Slide 43: Design waste water collection network

## Slide 44: Result of Design WWCN
Slope
Chart: conduit number

## Slide 45: Result of Design WWCN
Velocity
Chart: conduit number

## Slide 46
Cover
Cover start cover stop
Chart: conduit number
Chart: conduit number

## Slide 47: Result of Design WWCN
All the diameters in the network are 8 in

## Slide 48: Cost estimate for WWCN
To estimate the total cost of network, 4 main parts should be considered:
Excavation and filling cost
Conduits cost
Manholes cost
Repaving cost

## Slide 49: Cost estimate for WWCN
Conduits cost(8in) = 40 x 22780.9 = 911236 $
excavation of pipes tracks and filling = 30 x 22780.9 = 683427 $
Manholes = 650 x 798 = 518700 $
Total cost = 2113363 $

## Slide 50: Problems that was solved
Problem of the Hard and the quick change in topography and slops.
solution:
Changing the direction of the flow and enlargement the distance between manholes

## Slide 51: Problems that was solved
Adding more than one outfall
One outfall two outfall

## Slide 52: Problems that was solved
three outfall

## Slide 53: Problems that was solved
Problem of minimum velocities and high cover.
After the Trying many cases, the velocities of the flow were very small in general because of the low population
This problem can solve by increase the cover constrain range but that affects to make a huge cover depth

## Slide 54
The cases of the slope rang and its effects on covers:
slope: 1% to 12%

## Slide 55: Problems that was solved
Slope: 1% to 4%