## Slide 1: Water Network Analysis & Design of Ejnesenya
By : Nayef Hani Maqboul
Supervisor: Dr Anan Jayousi

## Slide 2: Content
Review of project 1 (existing network).
The design of the new network.
Housing projects.

## Slide 3: The existing network

## Slide 4: Problems in the existing network
Expansion of the residential areas.
Water pressure problems, 20<P<100 m H2O.
Velocity problems, 0.3<V<3 m/s.
Lack of water.
Lack of data and prober mapping of the network.

## Slide 8: NEW NETWORK DESIGN

## Slide 9: New model

## Slide 10: Design criteria
Velocity in pipes : 0.3 < V < 3 m/s.
Pressure in nodes : 20 < P < 100 m H2O.
Design period of 30 years.

## Slide 11: Population estimates & Demand calculation

## Slide 12: Demand pattern

## Slide 13: Nodes distribution

## Slide 15: Pipe distribution

## Slide 19: Housing Projects
Housing project A (AL-SHUNNAR).
Housing Project B (ISKAAN AL NAQURA).

## Slide 20: Housing Project A

## Slide 21: Population estimates & Demand calculation
Average density = 5 capita per family
Daily Municipal demand = 167.5 liters / capita.day
380 unit
Total demand = 318 m3/day.

## Slide 22: Housing project B

## Slide 23: Population estimates & Demand calculation
Average density = 5 capita per family
Daily Municipal demand = 167.5 liters / capita.day
360
Total demand = 301 m3/day.

## Slide 24
Total future demand of Ejnesenya = 276 m3/day.
Total demand of the housing projects = 619 m3/day.

## Slide 25: ALTERNATIVES

## Slide 26: Alternative 1
Main pipe line from feeding line to a reservoir that feeds the projects.

## Slide 27: Data obtained
pipe length = 910 meters
Elevation difference = 180 meter
Flow = 620 m3/day
Power horse needed = 17 HP

## Slide 28: Relevant costs
4 inch pipe of 910 meter length = 10.000 $
3 pumps = estimated 6000 $
Total cost 16.000 $

## Slide 29: Alternative 2
Connect the projects supply to the new network.

## Slide 30: Data obtained
pipe length = 550m
Elevation difference = 170 meter
Flow = 620 m3/day
Power horse needed = 17 HP

## Slide 31: Effects on the network

## Slide 32: Other scenarios

## Slide 33: Any Questions ?