## Slide 1: An-Najah National University Faculty of Engineering and Information Technology
Analysis and Design of An-Najah Modern Complex for Gravity and Dynamic Forces
Graduation Project Presentation II
Prepared By : Mohammad Iramthat Jadallah
Emran Mohammad Janem
Omar Imad Rajab
Presented to :Dr. Mahmoud M.S. Dwaikat
Dr. Mohammad Samaaneh
Eng. Fawzi Abu-Adas

## Slide 3: Outline
Abstract.
Introduction.
Model Checks.
Analysis Checks
Dynamic analysis.
Design For Gravity and Lateral Forces.

## Slide 4: Abstract

## Slide 5: Introduction
Ultimate Design Method to be used.
For Design will Use ACI 318-11 code
For Seismic Design UBC 97 Code.

## Slide 7: Introduction Stories Properties
Story Number | Story Name | Purpose | Area | Maximum Height *
1 | Basement 2 | Parking | 649.707 | 2.85
2 | Basement 1 | Big Story + Parking | 649.707 | 5.45
3 | Ground Floor | Stores | 514.17 | 5.7
4 | First Floor | Stores | 514.17 | 4.45
5 | Second Floor | Mall | 514.17 | 3.4
6 | Third Floor | Mall | 514.17 | 3.4
7 | Fourth Floor | Restaurant | 514.17 | 3.4
8 | Fifth Floor | Residential | 514.17 | 3.4
9 | Sixth Floor | Residential | 514.17 | 3.4

## Slide 8: Introduction Challenges
The main challenges in the original design of the building are:
The Building has an irregular shape in both horizontal and vertical direction.
Each level in the Building has different uses.
Some floors have variable levels.
In one direction the building has high slenderness ratio.
The Load of stair does not seem to have a safe route to transfer.

## Slide 9: Introduction Significance of the work
The importance of the project, mainly
apply what learned in engineering courses
improve skills in analysis and design by using computer especially SAP2000. Secondly
how communicate with engineering office and with contractor through producing skeleton and drawings.

## Slide 10: Material
Concrete :
Concrete strength for Slabs and Beams is B300 ( f'c=24 MPa).
Concrete strength for Columns and Shear walls is B350 (f'c=28 MPa).
Unit weight is 25 KN/m3.

## Slide 11: Material
Reinforcing Steel :
For steel reinforcement, use Grade A60
Modulus of elasticity : 2×105MPa
Steel yield strength: 420 MPa.

## Slide 12: Material
Other Materials
Density(KN/m3) | Material
12 | Bricks
15 | Filler
27 | Masonry
25 | Tiles
23 | Mortar
23 | plastering
5 | Y-tong Block

## Slide 13: Loads
Live load :
Floor | Live Load (KN/ m2)
Basement 2 | 5
Basement 1 | 5
Ground Floor | 5
First Floor | 5
Second Floor | 5
Third Floor | 5
Fourth Floor | 3
Fifth Floor | 3
Sixth Floor | 2
used ACSE 7-10

## Slide 14: Loads
Dead load
Consist of own weight of structural elements and superimposed loads .
superimposed is coming from four sources as follows:
Internal wall (partition) is 3.1 KN/m2
External wall (masonry wall) is 2.6 KN/m2
Doors and windows is 0.8 KN/m2
Tiles is 2.6 KN/m2

## Slide 15: Loads
Story Name | Snow Load (KN/ m2) | Superimposed Load (KN/ m2) | Live Load (KN/ m2)
Basement 2 | 0 | 0.8 | 5
Basement 1 | 0 | 0.8 | 5
Ground Floor | 0 | 2.8 | 5
First Floor | 0 | 2.8 | 5
Second Floor | 0 | 2.8 | 5
Third Floor | 0 | 2.8 | 5
Fourth Floor | 0 | 2.8 | 5
Fifth Floor | 0 | 2.8 | 3
Sixth Floor | 0 | 2.8 | 3
Roof | 1.5 | 0 | 2

## Slide 16: Loads
Snow Load
Assumed to be 0.5 m thickness snow on the roof so the load will be = 3 KN / m3 * 0.5 = 1.5 KN/m2.
Wind Load
Neglected the effect of wind Load since it’s too much small.

## Slide 17: Load Combinations
As per ACI318-11 code :
U = 1.4D
U = 1.2D + 1.6L + 0.5 (Lr or S or R)
U = 1.2D + 1.6 (Lr or S or R) + (1.0L or 0.5W)
U = 1.2D + 1.0W+1.0L+ 0.5 (Lr or S or R)
U = 1.2D + 1.0E +1.0L+ 0.2S
U = 0.9D+1.0W
U = 0.9D+1.0E

## Slide 18: Project constrains
Architectural constrains.
Shape of land.
Material and tools available.
Expertise in building.

## Slide 19: Structural Systems
Structural System in Basement 1 Floor after modifications.

## Slide 20: Structural Systems
Structural System in Ground Floor after modifications.

## Slide 21: MODELING

## Slide 22: Input Data
Set modifiers for Beam Section

## Slide 23: Input Data
Set modifiers for column Section

## Slide 24: Input Data
Set modifiers for one way Ribbed Slab

## Slide 25: Input Data
Set modifiers for two way Ribbed Slab

## Slide 26: Input Data
Bracing
Type | Wall dimension(m) | H(m) | B
1 | 3.50*3.40 | 1.00 | 0.20
2 | 5.00*3.40 | 1.20 | 0.20
3 | 5.00*5.00 | 1.42 | 0.20
4 | 8.00*3.40 | 1.74 | 0.20
5 | 8.00*5.00 | 1.88 | 0.20

## Slide 27: First mode (Y-direction)

## Slide 28: Second mode (X-direction)

## Slide 30: Dynamic analysis
Parameters of Seismic Force
Base shear Force
Structure irregularity

## Slide 31: Parameters of Seismic Force
Soil profile type = SD
Zone factor for Nablus city from Palestine seismic map = 0.2
Seismic coefficients Ca = 0.28, Cv = 0.40
Importance factor Special occupancy structure: I = 1
Response modification coefficient (R)=5.5 for both directions.
Structure period (Ty) =0.85 sec

## Slide 32: Base shear Force
Equivalent static method
Direction | Vmax (KN) | Vmin (KN) | V (KN)
X | 5499 | 1330 | 3732
Y | 5499 | 1330 | 3930

## Slide 33: Response spectrum analysis RSA
Modal analysis : modal mass participation ratio reaches over 90%
Response spectrum analysis.
Check drift(∆) :
0.7 R ∆Max = 0.16 < =
Direction | Veq (KN) | VResp (KN) | (I*g/R) | Scaled factor (KN)
X | 3732 | 2916 | 1.7836 | 2.2869
Y | 3732 | 3035 | 0.5945 | 2.192

## Slide 34: Design For Gravity and Lateral Forces
Design of :
  Footings
  Tie beams
  Slabs
  Stairs
  Ramp
  Beams
  Shear walls
  Basement wall

## Slide 35: Design of Footings
There are four types of footings:
  wall footing
  isolated footing
  combined
  mat foundation
  Bearing capacity of soil = 300 KN/m2 .

## Slide 37: Single footing design

## Slide 38: Combined footing design

## Slide 39: Wall footing design

## Slide 40: Mat foundation design

## Slide 43: Design of columns

## Slide 44: Column Dimension

## Slide 45: Checks
Stability index :
Q = = 0.0159 < 0.05 Column considered as braced (Non sway)
Slenderness ratio :
= 29.6 < = 40  short column

## Slide 46: Summary of steel reinforcement of Column
Floor | Column Type | reinforcement
B1,B2,G1 | C1 | 2214
 | C2 | 1612
 | C3 | 1614
1,2 | C1 | 2220
 | C2 | 1816
 | C3 | 1818
3,4,5,6 | C1 | 2020
 | C2 | 1425
 | C3 | 1822
Floor | Column Type | reinforcement
B1,B2,G1 | C1 | 
 | C2 | 
 | C3 | 
1,2 | C1 | 
 | C2 | 
 | C3 | 
3,4,5,6 | C1 | 
 | C2 | 
 | C3 | 

## Slide 47: Column C1 in floor B1,B2,GF

## Slide 49: Design of Slabs
Basement 2 floor (slab on grade)

## Slide 50: Design of Slabs
Basement 1 Slab

## Slide 53: Two way ribbed slab property

## Slide 55: One way ribbed slab

## Slide 56: Design of stairs
Stair dimensions
  Going = 30 cm
  Riser = 15 cm
  Floor height = 3.5 m
  No. of goings = 10
  No. of risers = 9
  Length of Flight =3.06 m
  landing thickness = 20 cm
  the thickness of flights = 15 cm

## Slide 58: Design of ramp

## Slide 60: Design of beams

## Slide 61
No. | Beam reinforcement |  |  |  |  |  |  |  |  | stirrups
 | Left |  |  | Mid |  |  | Right |  |  | 
 | L ( -ve) | M(+ve) | R(-ve) | L ( -ve) | M(+ve) | R(-ve) | L ( -ve) | M(+ve) | R(-ve) | 
MB1 | 518 | 418 | 518 | 518 | 318 | 518 | 518 | 218 | 318 | 210/300
MB2 | 718 | 618 | 918 | 918 | 618 | 918 | 918 | 218 | 218 | 210/140
MB3 | 218 | 218 | 418 | 418 | 518 | 418 | 418 | 218 | 218 | 210/300
MB4 | 218 | 218 | 418 |  |  |  | 418 | 618 | 318 | 210/300
MB5 | 218 | 218 | 618 |  |  |  | 618 | 718 | 518 | 210/200
MB6 | 218 | 318 | 718 |  |  |  | 718 | 918 | 718 | 210/200
MB7 | 218 | 218 | 418 |  |  |  | 418 | 518 | 318 | 210/300
No. | Beam reinforcement |  |  |  |  |  |  |  |  | stirrups
 | Left |  |  | Mid |  |  | Right |  |  | 
 | L ( -ve) | M(+ve) | R(-ve) | L ( -ve) | M(+ve) | R(-ve) | L ( -ve) | M(+ve) | R(-ve) | 
MB1 |  |  |  |  |  |  |  |  |  | 
MB2 |  |  |  |  |  |  |  |  |  | 
MB3 |  |  |  |  |  |  |  |  |  | 
MB4 |  |  |  |  |  |  |  |  |  | 
MB5 |  |  |  |  |  |  |  |  |  | 
MB6 |  |  |  |  |  |  |  |  |  | 
MB7 |  |  |  |  |  |  |  |  |  | 
Type | Positive | Negative | stirrups
SB1  SB7 | 512 | 512 | 110/250mm
Type | Positive | Negative | stirrups
SB1  SB7 |  |  | 

## Slide 65: Secondary beam at slab elevation change

## Slide 67: Design of shear wall

## Slide 68: Shear wall reinforcement and dimension

## Slide 69: Design of basement wall

## Slide 70: basement reinforcement and dimension