## Slide 1
Data Center’s Cooling
Prepared by:
Esraa Barahmeh
Hala Kalbouneh
Masa Shaheen
Tala Saffarini
Graduation Project 2

## Slide 2
GOALS
Compare different cooling
methods in data centers
01.
select the most efficient and cost-effective method for Jawwal Company
4
Evaluate the cooling loads
of Jawwal Company's
data center
Compare various cooling system
used in CRAC, then select the
most suitable type for Jawwal
Determine the Break-Even
Point (BEP)
02.
03.
04.
05.

## Slide 3
Notes: As the demands of remote data services keep increasing, both the workload of the data center and its power consumption are rapidly rising. An indispensable part of a data center is the cooling system which provides a suitable operation environment, and accounts for around 50% of the power consumption of the data center. Therefore, optimized energy management of data center’s cooling system is a highly profitable research area.

## Slide 4
Case study
Jawwal company
Cooling method
Rack level cooling
Problem
Mixing hot and cold air
Notes: As the demands of remote data services keep increasing, both the workload of the data center and its power consumption are rapidly rising. An indispensable part of a data center is the cooling system which provides a suitable operation environment, and accounts for around 50% of the power consumption of the data center. Therefore, optimized energy management of data center’s cooling system is a highly profitable research area.

## Slide 5
Types of Cooling Technologies in Data center
Air Cooling
01.
Liquid Cooling
02.
Free Cooling
03.
Aisle
Containment Cooling
04.

## Slide 7
Cold Aisle Containment
Figure 18.1: Layout of CAC
Figure 18.2: CAC

## Slide 8
Hot Aisle Containment
Figure 19.1: Layout of HAC
Figure 19.2: CAC

## Slide 9
Ability to set work environment temperature to 24°C,Acceptable temperature for non-racked equipment
01
Rack power density
02
Effictiveness
03
Cost
04
Ease of deployment with room cooling
05
Comparison between hot and cold aisle containment

## Slide 10
The recommended conditions for data Center

## Slide 11
The Uptime Institute is a leading global organization in the design, construction and operation of data centers.
The Institute provides standards, research and certifications to ensure the highest level of data center performance.
The Uptime Institute classifies data centers into four tiers (Tier I to Tier IV) based on infrastructure, reliability, and availability.
Uptime Institute’s Tier standards

## Slide 12
Uptime Institute’s Tier standards
Uptime is the annual amount of time that a data center is guaranteed to be available and running.
01
Downtime is the annual amount of time that a data center and its availability will be interrupted.
02
Redundancy is a data center component designed to duplicate primary resources and power in the case of failure
03
Fault Tolerant – The ability of a system to continue functioning, even if one or more components fail.
04

## Slide 13
Tier IV
Tier I
Tier III
Tier II
DATA CENTER TIERS
99.671% Uptime
No Redundancy
Small Businesses
29 Hours Downtime /Year
Partial Redundancy
22 Hours Downtime /Year
99.749% Uptime
Medium-Size Businesses
99.995% Uptime
26.3 Minutes Downtime Per Year
Enterprise Corporations
2N+1 Fully Redundant
96 Hour Power Outage Protection
99.982% Uptime
1.6 Hours Downtime /Year
Large Businesses
N+1 Fully Redundant
72 Hour Power Outage Protection

## Slide 14
Air Handel Unit(AHU)
Direct Expantion (DX)
Central chilled water system
DX-Split A/C system -AIR COOLED
DX-Split A/C system -Water COOLED
Chilled water system
glycol cooled
Air cooled chiller
Glycol cooled chiller
Water cooled chiller
Cooling Systems used in CRAC

## Slide 15
Direct Expantion -Air Cooled

## Slide 16
Advantages of Direct Expantion -Air Cooled
Self-contained, Standalone Modules
Maintenance and Reliability
Scalability and low overall cost

## Slide 17
Disadvantages of Direct Expantion -Air Cooled
  Refrigerant Piping Requirements:
Traps: The installation of traps is necessary to prevent liquid refrigerant from returning to the compressor, which can cause damage
Complex Installation: Refrigerant piping must be meticulously designed and installed in the field to ensure proper functioning. This includes careful consideration of the distance and height differences between the IT environment and the outdoor condenser units.
  Limited Connectivity
  Pressure Losses

## Slide 18
Direct Expantion -Water Cooled

## Slide 19
Advantages of Direct Expantion -Water Cooled
  Contained Refrigeration Cycle Components
  Easily Run Piping Loops
  Superior Heat Transfer Properties
  typically servicing multiple CRAC units and other devices from a single cooling tower

## Slide 20
Disadvantages of Direct Expantion -Water Cooled
  High Maintenance Costs
  Water Treatment Requirements
  High Initial Cost

## Slide 21
Chillers
. Both do the same job. This means, it lowers the temperature of the water coming from the AHU and then sends it back to the AHU

## Slide 22
Air cooled chiller

## Slide 23
Air Cooled Chiller

## Slide 24
Air Cooled Chiller

## Slide 25
Air Cooled Chiller

## Slide 26
Air Cooled Chiller

## Slide 27
Advantages Of Air Cooled Chiller
  No cooling towers.
  Low maintenance expenses.
  Better environmental stability—no water waste
  Chemical costs avoided.

## Slide 28
water cooled chiller

## Slide 29
water cooled chiller
AHU&chilled water pupm

## Slide 30
water cooled chiller

## Slide 31
Advantages Of Water Cooled Chiller
  The crac unit houses every component of the refrigeration cycle as a factory-tested, sealed system for greatest reliability.
• Long-distance condenser water piping loops can be easily raised, and they are nearly always used to supply several computer room air conditioners and other devices from one cooling tower.
01
02

## Slide 32
Dis advantages Of Water Cooled Chiller
  High initial cost for cooling tower, pump, and piping systems.
  Very high maintenance costs due to frequent cleaning and water treatment requirements.
01
02

## Slide 33
space
01
02
Energy Cost
03
Compressor failure
04
05
Comparison between Direct expantion &chiller
capital cost
Labor Skills

## Slide 34
Direct expantion or chiller?
The recommendation based in capacity as following:
1. Capacities: < 80 tons use CRAC, DX System.
2. Capacities: > 80 tons and < 200 tons use chilled water systems, screw chillers.
3. Capacities: >200 tons use chilled water systems, centrifugal chillers.

## Slide 35
Why We need humidification
on data center?

## Slide 36
CONDENSATION
LOW
Humidity
Humidification
Dehumidification
ESD
HIGH
Sensors
How much water Vapor needed

## Slide 37
Ideal cooling process at constant humidity ratio.

## Slide 38
Cooling process to apparatus dew point.

## Slide 39
Total cooling process between return air and supply air.

## Slide 40
Calculation: 1. Calculation of sensible cooling load
Heat gain | Old System | New System
Equipment Heat Gains | Design for power rack density= 𝑛𝑢𝑚𝑏𝑒𝑟 𝑜𝑓 𝑟𝑎𝑐𝑘𝑠 × 𝑝𝑜𝑤𝑒𝑟 𝑟𝑎𝑐𝑘 𝑑𝑒𝑛𝑠𝑖𝑡𝑦 30 𝑟𝑎𝑐𝑘 × 4 𝑘𝑤 𝐷𝐶 𝑟𝑎𝑐𝑘 + 27 𝑟𝑎𝑐𝑘 × 5 𝑘𝑤 𝐴𝐶/ 𝑟𝑎𝑐𝑘 = 255 kW | = 38 𝑟𝑎𝑐𝑘 × 3.5 𝑘𝑊/ 𝑟𝑎𝑐𝑘 = 133 kW.
Occupancy | The heat output is approximately 100 watts per person. 300 W=0.3 kW | The heat output is approximately 100 watts per person. 300 W=0.3 kW
Building envelope | heat from the roof, walls and windows - neglected | heat from the roof, walls and windows - neglected
Auxiliary Power | located in a separate room. | located in a separate room.
Lighting | Lighting loads are considered 3 watts per sq-ft. 2466 sq. ft = 229.1 𝑚^2 P-lighting=7.398 kW | Neglected
Total | 262.7 kW | 133.3 kW

## Slide 41
2. Calculation of latent load
  Determine the Dew Point
  Check for Condensation
  Determine the Mass Flow Rate of Air Contacting the Coil (ṁ contact)

## Slide 42
  Calculate the Dehumidification
  Determine the amount of water

## Slide 44
  Calculate the Latent Heat
3.𝑇𝑜𝑡𝑎𝑙 𝑐𝑜𝑜𝑙𝑖𝑛𝑔 load= 𝑠𝑒𝑛𝑠𝑖𝑏𝑙𝑒 ℎ𝑒𝑎𝑡 + 𝑙𝑎𝑡𝑒𝑛𝑡 ℎ𝑒𝑎

## Slide 45
4.CRAC Selection
CRAC Selection Criteria:

## Slide 48
Performance at RAT 30°C / RH 35% - Condensing temperature 45°C - Downflow up air
configuration. CE units - Power supply 400V/3ph/50Hz - High Power EC Fans - Refrigerant
R410A.

## Slide 49
5.Calculate Break Even Point

## Slide 51
HEAVY POWER load | ELECTRICAL FIRE RISK | INFRASTRUCTURE | VENTILATION
Heavy power loads or a defective piece of equipment can very quickly lead to a ﻿short circuit or overheating | Constant ignition source electricity and combustible materials, such as plastics﻿, in printed circuit boards | Extensive cabling, particularly below raised floors | Comprehensive air cooling, resulting in higher air exchange, increases the risk of spreading the fire
The main causes for a high risk of fire in a data center:

## Slide 52
Good data center fire protection consists of
Mitigation
01.
Detection
02.
Suppression
03.
Recovery
04.

## Slide 53
How an air-sampling smoke detector works

## Slide 54
Fire suppression with water
Fire suppression
with gas
01.
Fire suppression systems
1
2
Water Sprinkler
Water Mist
1
2
Clean Agents
Inert Gases

## Slide 55
Fire suppression with water

## Slide 56
Remove One To Stop Fire

## Slide 57
Gas Suppression System

## Slide 58
CONCENTRATION FOR FLOODING
unlimited possible
Max. 10 sec
unlimited possible
Max. 10 sec
temporary possible
60 to 120 sec
not possible
60 sec
STAYING IN THE FLOODED ROOM
TIME FOR EFFUSION
NOVEC 1230
FM-200
CO2
Comparison of fire-extinguishing gases
INERT GASES (ARGON, ARAGONITE, INERGEN, AZOTES)
5.8%
8.4%
45…50.5%
47…57%
RESIDUAL OXYGEN
19.6%
19.1%
10.3 ... 11.4%
CO2 is toxic at >8 vol.-%
FORMATION OF CONDENSATION ON THE PIPES
No
No
Yes
Yes
MULTI AREA SYSTEM
limited possible
limited possible
possible
possible

## Slide 59
NOVEC 1230
FM-200
CO2
Comparison of fire-extinguishing gases
INERT GASES (ARGON, ARAGONITE, INERGEN, AZOTES)
MAXIMUM PIPE LENGTH
around 60m
around 60m
>> 150m
up to 150m
DANGER FOR HUMAN
No
No
Yes
Yes
REQUIRED SPACE FOR SUPPLY
low
low
high
middle
ENVIRONMENTAL IMPACT
very good
bad
good
very good
EVALUATION
1
2
3
4

## Slide 60
  Fast reaction time, can extinguish a fire before it even starts
  Safe to use in occupied areas
  Works on Class A, B and C fires
  Environmentally friendly
  Does not damage sensitive equipment or valuable assets
  No clean-up required
  Minimal downtime after a fire
  Not electrically conducive
Some advantages of using Novec 1230™

## Slide 61
How to make the data center more energy efficient?
Active IT load
Electrical powertrain
Cooling systems
AI in the Data Center
Automation and
monitoring

## Slide 62
ACTIVE IT LOAD
IT load management
Rack management
load balancing
virtualization
COOLING SYSTEM
Aisle containment
Heat recovery
choosing cooling technology
AUTOMATION & MONITORING
Regular maintinance
DCIM
Active monitoring
ELECTRICAL POWER TRAIN
Energy storage solution
valve-regulated lead acid (VRLA) (Li-ion) batteries

## Slide 63
Power Usage Effectiveness (PUE)
PUE values range from 1.0 to infinity. Current research suggests that many data centers have a PUE of 3.0 or higher, but a well-designed center should aim for a PUE of 1.6 or lower.

## Slide 64
Constraints
  Humidity Control: Relative humidity levels must be maintained between 30-60% to prevent damage to sensitive IT equipment.
  Temperature Control: The dry bulb temperature must be maintained between 18-27°C to ensure optimal operatingconditions for the equipment.
  Tier 3 Standards: The system must meet Tier 3 data center standards, including N+1 redundancy for critical components to ensure high availability and reliability.

## Slide 65
Recommendations
  Changing the refrigerant from R410A to R32 will improve environmental sustainability. R32, and energy-saving measures can help the data center lower its carbon footprint.
• Implement tandem compressors in the DX air-cooled system for increased efficiency and reliability. Tandem compressors increase load matching, save energy usage, and extend compressor life.
• Stay up-to-date on new cooling technologies and innovations to enhance data center performance and efficiency

## Slide 66
Conclusion

## Slide 67
Thank You