## Slide 1
AN-NAJAH NATIONAL UNIVERSITY
FACULTY OF ENGINEERING
DEPARTMENT OF MECHANICAL ENGINEERING

## Slide 2
Students name :
Abed Alkareem Alfanni
Ismat Fakhouri
Mohammad Hussein
Saleh Obead
Supervisor:
Ramiz Al Khaldi
24/5/2010
AL BAHRAIN PEDIATRIC HOSPITAL

## Slide 3
24/5/2010
AL BAHRAIN PEDIATRIC HOSPITAL
MECHANICAL SYSTEMS IN BUILDINGS
AL BAHRAIN PEDIATRIC HOSPITAL
Notes: Jyrtftrttdderedrrerwrererererter

## Slide 4
24/5/2010
AL BAHRAIN PEDIATRIC HOSPITAL
The aim of this project is to design the Following Mechanical Systems to AL Bahrain Pediatric Hospital :
Heating Ventilation and air conditioning (HVAC).
Plumping system (Sanitary drainage system& potable water system).
Fire Fighting system.

## Slide 5
24/5/2010
AL BAHRAIN PEDIATRIC HOSPITAL
HVAC System
This abbreviating stands for Heating Ventilation and Air Conditioning System
The main objective of air conditioning is to maintain the environment in enclosed space at conditions that induce the feeling of comfort to human.

## Slide 6
24/5/2010
AL BAHRAIN PEDIATRIC HOSPITAL
WINTER INSIDE AND OUTSIDE DESIGN CONDITIONS
Outside temperature To=4.7 ˚C.
Inside temperature Ti=21 ˚C.
Outside Relative humidity Фo=71.7% .
Inside Relative humidity Фi=30%.
Outside Moisture content Wo =3.9g of water/ Kg of dry air.
Inside Moisture content Wi =4.7g of water/ Kg of dry air.

## Slide 7
24/5/2010
AL BAHRAIN PEDIATRIC HOSPITAL
HEATING LOAD EQUATIONS
The following equations were used to calculated the heating load:
Qs,cond = U A (Tin – To) .
Q s,vent = 1.2 Vvent (Tin – To).
Q l,vent = 3 Vvent (Wi- W o).
Qtotal = Qs,cond + Qs,vent +Ql,vent
Notes: HEATING LOAD EQUATIONS

## Slide 8
24/5/2010
AL BAHRAIN PEDIATRIC HOSPITAL
HEATING LOAD RESULTS
Floor | Qs)cond. (w) | Qs) vent. (w) | Ql) vent. (w) | Q)total .(w)
Basement Floor | 3464.9072 | 19090.8 | 2232 | 23887.7072
Ground Floor | 21450.745 | 53389.02 | 6550.8 | 81390.57
First Floor | 50234.88477 | 30240.24 | 5712 | 86187.12
Second Floor | 27533.056 | 55491.72 | 6808.8 | 89833.58
Total | 102683.6 | 158211.8 | 21303.6 | 281299
Notes: HEATING LOAD RESULTS

## Slide 9
24/5/2010
AL BAHRAIN PEDIATRIC HOSPITAL
The boiler is the main source of heating process, selection of boiler depends on its capacity. selection of boilers from FERROLI COMPANY.
The total amount of heat in our project equal to 291.388 KW. Use catalog of boilers B.1 then the suitable boiler is that of type GN4 N 09
The GN4 N 09 has the following specifications:
Max. Heat input = 300 KW
Min. Heat input = 180KW
Combustion Chamber (Length = 1140mm, Diameter = 500 mm)
Working pressure = 4 bar
Width of boiler = 1300mm
Boiler gross weight = 1170 Kg

## Slide 10
24/5/2010
AL BAHRAIN PEDIATRIC HOSPITAL
SUMMER INSIDE AND OUTSIDE DESIGN CONDITIONS
Outside temperature (To) be 30˚C.
Inside temperature (Ti) be 25 ˚C.
Outside Relative humidity (Фo) is 49.7%.
Inside Relative humidity (Фi) is 50%.
Outside Moisture content (Wo) is 13.5 g of water/ Kg of dry air.
Inside Moisture content (Wi) is 10 g of water/ Kg of dry air

## Slide 11
AL BAHRAIN PEDIATRIC HOSPITAL
24/5/2010
COOLING LOAD EQUATIONS
Qs = U * A * CLTD corc. For Wall And Ceiling. CLTD coro = ( CLTD + LM ) K +( Tin -25.5 ) + ( To – 29.4 ). Qs) transmitted = A * SHG * SC * CLF . From glass Qs) convection = U * A * ( CLTD ) correction. From glass Qs) vent = 1.2 *A * ( To – T in ) . Q latent = 3 * A ( W o –W in ) Qs) people = qs * n * CLF Ql) people = ql * n Qs) lighting = W * CLF Qs) equipment = qs * CLF Ql) equipment = ql

## Slide 12
AL BAHRAIN PEDIATRIC HOSPITAL
24/5/2010
Floor. No | Q(Total) (Kw) | Q(Total) (Ton) | Q(Total) (CFM)
Basement floor | 33.1818 | 9.480515 | 3287.122
Ground floor | 110.9769 | 31.7077 | 13266.677
First Floor | 109.940 | 31.41143 | 14988.76
Second floor | 106.745 | 30.49857 | 13073.59
COOLING LOAD RESULTS

## Slide 13
AL BAHRAIN PEDIATRIC HOSPITAL
24/5/2010
The chiller is the main source of cooling process, our selection depends on PETRA COMPANY.
The cooling load in our project is 102.43 Ton. . So we select 110 ton R 134-a chiller it's manufactured with Two compressors and with the same compressors type.
The Chiller Code is: WPS a 110 2 S

## Slide 14
AL BAHRAIN PEDIATRIC HOSPITAL
24/5/2010
DUCT DESIGN
There are two methods for duct design :
Equal pressure drop method.
Velocity method.
All the results of duct design based on equal pressure drop method
Notes: All the results of duct design based on equal pressure drop method

## Slide 15
AL BAHRAIN PEDIATRIC HOSPITAL
24/5/2010
PIPES DESIGN
The total cooling load was calculated for the floor.
The mass flow rate for the water calculated (m).
The pressure head was estimated in (Kpa) .
The longest loop from the boiler to the farthest fan coil unit and return to the boiler was calculated multiplying by (1.5) due to fittings.
The pressure head per unit length is calculated and it should be between range from (200< ∆p/L<550).
Then the diameter of pipe entering to the floor is estimated .

## Slide 16
AL BAHRAIN PEDIATRIC HOSPITAL
24/5/2010
The Air Handling Units were selected from PETRA COMPANY using PETRA catalogue:
AIR HANDLING UNIT SELECTION
Notes: AIR HANDLING UNIT SELECTION

## Slide 17
AL BAHRAIN PEDIATRIC HOSPITAL
24/5/2010
The suitable A.H.U (AHU#2) for ground floor (4724.164 CFM) is:
PAH H C 50 C6 H3 X2
The suitable A.H.U(AHU#1) for (ground & second floor) (7301.165 CFM) is:
PAH H C 80 C6 H3 X2
The suitable A.H.U for first floor:
AHU# 1: Operation rooms (1407.188 CFM) PAH H C 16 C6 H3 X2
AHU #2: I.C.U room (555.745 CFM) PAH H C 8 C6 H3 X2
AHU #3: N.I.C.U room (1037.010 CFM) PAH H C 12 C6 H3 X2

## Slide 18
AL BAHRAIN PEDIATRIC HOSPITAL
24/5/2010
FAN COIL UNIT SELECTION
In Our project we need Ducted FCU and to ensure the high level of comfort we need the filtered FCU our selection from Petra catalogs is CBP type.

## Slide 19
AL BAHRAIN PEDIATRIC HOSPITAL
24/5/2010
PLUMMPING SYSTEM IN BUILDINGS
The drainage fixture unit in building
Size of pipes (in) | No .of fixture | Type of fixture
4 | 6 | Water closet
1 1/2 | 3 | Kitchen sink
2 | 2 | Shower head
1 1/2 | 1 | Lavatory
2 | 3 | Floor drain
    Total No. of Fixture = (478) F.U
    The Main Building Drain = 5 in. 6in practical

## Slide 20
AL BAHRAIN PEDIATRIC HOSPITAL
24/5/2010
Potable water fixture unit in building
Size of pipes (in) | No .of fixture | Type of fixture
1 | 10 | Water closet
1/2 | 4 | Kitchen sink
1/2 | 4 | Shower head
3/8,1/2 | 2 | Lavatory
1/2 | 3 | Service sink
    Total No. of Fixture = (633) F.U from table (appendix **)
    The total demand is 178 GPM
    Total cold water demand = 178 x 0.75 =133.5 GPM
    Total hot water demand = 178 x 0.25 = 44.5 GPM
Notes:     Total No. of Fixture = (633) F.U from table (appendix **)
    the total demand is 178 GPM
    Total cold water demand = 178 x 0.75 =133.5 GPM
    Total hot water demand = 178 x 0.25 = 44.5 GPM