## Slide 1
An-Najah National University
Faculty of Engineering
Civil Engineering Department
Graduation Project ||
Structural analysis and design for static and seismic loads of Nihad AL-Bezreh building in Nablus city
Prepared by:
Ahmad Halaweh
Asem Al-Nouri
Muslem Al-jubeh
Tariq Alwaneh
supervisor
Dr. Mahmoud Dweikat

## Slide 2: Outline
Project description
Analysis & Design Principles
ETABS modeling
Dimensional Analysis
Design

## Slide 4
Notes: This project is commercial and residential building located near AL Bizreh Complex, Nablus Tulkarm Main Street, Nablus, Palestine. The proposed building will have 1300m2 plan area and will consist most of 12 stories (4 basements) and have a total area of 14,476 m2

## Slide 6
Floor | Function | Area of block 1 (m2) | Area of block 2 (m2) | Total area (m2)
B4 | Garage | 731 | 322 | 1053
B3 | Storage | 731 | 738 | 1469
B2 | Warehouse | 615 | 738 | 1353
B1 | Warehouse | 615 | 738 | 1353
G | Commercial | 615 | 662 | 1277
Shed | Commercial | 460 | 550 | 1010
F1 | Commercial | 615 | 662 | 1277
F2 | Residential | 454 | 707 | 1161
F3 | Residential | 454 | 707 | 1161
F4 | Residential | 454 | 707 | 1161
F5 | Residential | 454 | 707 | 1161
F6 | Residential | 389 | 592 | 981
The function and area for each floor:

## Slide 7
Architectural Drawings

## Slide 8
Site plan

## Slide 9
Notes: الطوابق المختلفه والارتفاعات

## Slide 11: Basement B4

## Slide 12: Ground Floor G

## Slide 13: Floor 2-5

## Slide 14: Soil properties:
The site from geotechnical point of view can be described as follows:
The allowable bearing is 250 kN/m2
Mat foundation is recommended to be used for this site.
Layer No. | Location | Description | Shear Wave Velocity (Vs) m/sec | (P-wave) m/sec | Soil Profile Type
1 | Northern part of the site BLOCK 1 | Soft chalky Marlstone formation | 700 | 1400 | SD
2 | Southern Part of the site BLOCK 2 | Silty clay mixed with boulders | 300 | 600 | SC

## Slide 15: Analysis and Design Principles
  Three dimensional model is used to model the building using ETABS V16.0.0 program.
  The footings are considered as fixed supports (MAT Foundation) .
  Codes and Standards:
    ACI 318-11 : American Concrete Institutes Building Code Requirements for design of concrete elements.
    UBC-97 : Uniform Building Code.
    ASCE : American Society of Civil Engineers.

## Slide 16
Concrete
Structural element | Compressive strength(fc’) (Mpa)
Slab, beam | 24
Column, footing, shear wall, Stair | 28
Material
Reinforcement steel:
Yielding strength (Fy) = 420MPa
Modulus of elasticity (Es) = 200GP

## Slide 17
Material | Unit weight, γ (KN/m3)
Plain concrete | 23
Reinforced concrete | 25
Tiles | 26
Filling material | 23
Materials unit weight
Material

## Slide 18
Loads
Gravity
Dead
Live
Lateral
Wind
Seismic

## Slide 19
Dead load
  Slab own weight for solid= 5 KN/m2
  Superimposed dead load= 3.9 KN/m2
  Wall load= 6.30 KN /m2
Floor | Function | uniform live load (KN/m2)
B4 | Garage | 1.92
B3 | Storage | 4
B1-B2 | warehouse | 6
G-F1 | Commercial | 4
F2-F6 | Residential | 4
Live load “according to ASCE code”
Gravity Loads

## Slide 20
Seismic Load
  For Nablus City, seismic zone is 2B.
  Seismic zone factor, Z = 0.2
  Importance factor, I = 1
  Over strength factor, R = 5.5
  Acceleration & Velocity seismic coefficient:
Lateral Loads
 | Block 1 | Block 1
Soil type | SD | SC
Ca | 0.28 | 0.24
Cv | 0.4 | 0.32

## Slide 21
Load Combinations
The Ultimate load combinations used in design are:
  1.4D
  1.2D + 1.6L
  1.2D + 1.6L + 0.5(Lr or S or R)
  1.2D + 1.6(Lr or S or R) + (1.0L or 0.5W)
  1.2D + 1.0W + 1.0L + 0.5(Lr or S or R)
  1.2D + 1.0E + 1.0L + 0.2S
  0.9D + 1.0W
  0.9D + 1.0E
Notes: According to ACI 318-11

## Slide 22
Load Combinations
The service load combinations used in checks are:
  D
  D +L
  D +0.75L
  D +0.7E
  D +0.75L +0.75(0.7E)
  0.6D+0.7E
Notes: According to ACI 318-11

## Slide 23
Computer programs
ETABS
Word and Excel
AutoCAD
SAFE
SAP2000

## Slide 24: PRELIMINARY DESIGN
Notes: Preliminary Design is the first phase of the design process. In this stage of the project a preliminary dimensions was selected in order to build the 3-D model. To check the validity of 3D model, three verification checks will be made which are compatibility, equilibrium and stress-strain relationships. After studying the 3D model and results, a change of these dimensions could be occurred to get the most suitable dimension that will achieve the strength needs.

## Slide 25: Slab
The structural system used is two way solid slab
BLOCK
1
Notes: Determine the slab structural system and slab thickness

## Slide 26
The Critical Panel
(4.70m x 6.65m) as shown in the figure
According to Direct Design Method Slab thickness =200mm
Wide beam shear check:
=
ΦVc ˃Vu ( OK )
Slab thickness
BLOCK
1
Notes: Slab thickn
=
Since ΦVc ˃Vu, Slab thickness is adequate for resisting shear (OK). So use h= 200 mm and there is no need for shear reinforcement.
Slab thicknOwn weight=0.2∗25=5 KN/m2
Superimposed dead load =3.2 KN/m2
Live load =4.00 KN/m2
Ultimate load(Wu) =1.2(5+3.2)+1.6(4.00)=16.24 KN/m2
∅Vc=∅1/6 √(fc ) bw∗d =(0.75) 1/6 √(24 ) 1000/1000∗(200−40)=98.00KN
Vu=Wu(l/2−B/2−d)=16.24(6.65/2−0.4/2−0.16)=48.15KN
Since ΦVc ˃Vu, Slab thickness is adequate for resisting shear (OK). So use h= 200 mm and there is no need for shear reinforcement.

## Slide 27: Beams
The distribution of beams for F1 and F6 shown below:
BLOCK
1

## Slide 28
According to ACI 318-11, Table 9.5(a), the thickness of beams can be obtained based on the deflection limit:
The preliminary sections of beams
Member | Simply supported | One end continuous | Two end continuous | Cantilever
Beams | L/16 | L/18.5 | L/21 | L/8

## Slide 29: Beams
Beam | Dimensions (mm)
B1 | 400*400
B2 | 400*400
B3 | 300*400
B4 | 300*600
B5 | 600*600
B6 | 200*400
B7 | T
B8 | L
The preliminary sections of beams:
BLOCK
1

## Slide 30
Beams
The distribution of beams for F1 shown below:
BLOCK
2

## Slide 31
Beams
The preliminary sections of beams:
Beam | Dimensions (mm)
B1 | 200*600
B2 | 300*600
B3 | 500*600
B4 | 800*500
B5 | T
B6 | L
BLOCK
2

## Slide 32: Columns
By using tributary area method, we found the ultimate load and determine the dimensions of columns
BLOCK
1
Notes: 8351∗E3=0.75∗0.85(0.85∗28(Ag−0.01Ag)+420∗0.01Ag)

## Slide 33: Columns layout
BLOCK
1

## Slide 34
 | original dimensions (mm) | preliminary design dimensions (mm)
C1 | D700 | D800
C2 | 400*400 | 400*400
C3 | 400*700 | 400*700
C4 | 700*300 | 700*300
C5 | 300*1000 | 300*1000
Columns dimensions are shown in table:
BLOCK
1

## Slide 35: Columns
By using tributary area method, we found the ultimate load and determine the dimensions of columns
BLOCK
2

## Slide 36: Columns layout
BLOCK
2

## Slide 37
 | Original dimensions (mm) | Preliminary design dimensions (mm)
C1 | D 700 | D 850
C2 | 300*700 | 500*700
C3 | 300*800 | 400*800
C4 | 300*1000 | 300*1000
C5 | 300*1000 | 650*1000
Columns dimensions are shown in table:
BLOCK
2

## Slide 38: Shear Wall
Wall | Thickness (mm)
Wall 1 | 250
Wall 2 | 300

## Slide 39: Bracing
Objective
  Bracing in the model expresses the effect of masonry walls, they may increase stiffness In the building and reduce the period.
Section
  Bracing dimensions were calculated as following:
  Depth=200mm.
  Width=diagonal length/5
Material:
  Using a modulus of Elasticity = 0.1 of concrete modulus of Elasticity to represent the average value of concrete, masonry and blocks.

## Slide 40: Bracing
Bracing number | L (m) | Dimensions (mm)
b1 | 6.00 | 1200*200
b2 | 7.40 | 1500*200
b3 | 4.50 | 900*200
Bracing dimensions in BLOCK 1
Bracing dimensions in BLOCK 2
Bracing number | L (m) | Dimensions (mm)
b1 | 5.6 | 1200*200
b2 | 7.40 | 1500*200
b3 | 8.50 | 1700*200

## Slide 41: Structural Modeling

## Slide 42: 3D model for block 1

## Slide 43: 3D model for block 2

## Slide 44: Modifiers for area structural element
Modifiers/Section | Slab | Shear walls
Membrane f11 Direction | 1 | 1
Membrane f22 Direction | 1 | 1
Membrane f12 Direction | 1 | 1
Bending m11 Direction | 0.25 | 0.35
Bending m22 Direction | 0.25 | 0.35
Bending m12 Direction | 0.25 | 0.35
Shear v13 Direction | 1 | 1
Shear v23 Direction | 1 | 1
Mass | 1 | 1
Weight | 1 | 1

## Slide 45: Modifiers for frame structural element
Modifiers/Section | beams | Columns | Bracing
Cross Section(axial) Area | 1 | 1 | 1
Sheer Area in 2 direction | 1 | 1 | 0
Sheer Area in 3 direction | 1 | 1 | 0
Torsional Constant | 0.35 | 0.7 | 0
Moment of Inertia about 2 axis | 0.35 | 0.7 | 0
Moment of Inertia about 3 axis | 0.35 | 0.7 | 0
Mass | (Depth-200)/200 | 1 | 0
Weight | (Depth-200)/200 | 1 | 0

## Slide 46
seismic Loads
V = CsW = 0.0945*98569.14 = 9314.8 kN
  Vmax= 2.5CaIW/R = 12545.16KN
  Vmin= 0.11CaIW = 3035.90kN
Equivalent static:
Where:
Cs = the seismic response coefﬁcient = = 0.0945
W = the effective seismic weight.
I=importance factor.
R=over strength factor.
Ca: Acceleration seismic coefficient
Cv: velocity seismic coefficient
W (kN) | Cv | Ca | I | R | Ta
98569.14 | 0.4 | 0.28 | 1 | 5.5 | 0.77
BLOCK
1

## Slide 47: Loads assignments:
Earthquake Assignment in X-Direction with Positive Eccentricity
BLOCK
1

## Slide 48
  Functions:
  Response Spectrum Function Definition:
BLOCK
1

## Slide 49
Response spectrum curve:
Ts== 0.57
T0 = 0.2 Ts = 0.114
Sa= = 0.519
BLOCK
1

## Slide 50
seismic Loads
V = CsW = 0.0756*110962.3 = 8384.4 kN
  Vmax= 2.5CaIW/R = 12104.98 KN
  Vmin= 0.11CaIW = 2929.4 kN
Equivalent static:
Where:
Cs = the seismic response coefﬁcient = = 0.0756
W = the effective seismic weight.
I=importance factor.
R=over strength factor.
Ca: Acceleration seismic coefficient
Cv: velocity seismic coefficient
W (kN) | Cv | Ca | I | R | Ta
110962.3 | 0.32 | 0.24 | 1 | 5.5 | 0.77
BLOCK
2

## Slide 51
Checks
Model
Deflection
Structural period T
Drift
Structural Irregularity
Equilibrium
Stress strain
Participating mass ratio
Base Shear

## Slide 52: Model check
BLOCK
1

## Slide 53: Equilibrium check
Type | ETABS results (KN) | Hand calculation (KN) | Error%
Live | 26876.06 | 26898.40 | 0.08
Superimposed | 20396.27 | 20414.05 | 0.09
External wall | 8729.02 | 8497.64 | 2.72
Dead | 74375.12 | 74259.53 | 0.16
BLOCK
1

## Slide 54: Equilibrium check
Type | ETABS results (KN) | Hand calculation (KN) | Error%
Live | 33712.22 | 34574.48 | 2.49
Superimposed | 24647.70 | 25244.80 | 2.37
External wall | 7163.91 | 7099.26 | 0.91
Dead | 70369.88 | 70573.05 | 0.29
BLOCK
2

## Slide 55
M Hand =62.357 KN.m
% Difference =15.6% < 25 %
so it is OK.
We made the internal force check from live load for this beam as following in the figure:
Stress strain check
BLOCK
1

## Slide 56
M Hand =40.74 KN.m
= + 18.95 = 34.45
% Difference =15.4% < 25%
so it is OK.
Stress strain check
BLOCK
2
We made the internal force check from live load for this beam as following in the figure:

## Slide 57
ACI code limitations on immediate and long term deflections
Long term deflection
Deflection check

## Slide 58
Immediate deflection due to live load:
Deflection check
BLOCK
1

## Slide 59
Long term deflection
L=8.00m | Relative deflection (mm) | Allowable deflection mm) | 
Live | 3.40 | 22.20 | OK
Long term | 31.40 | 33.33 | OK
BLOCK
1
Deflection check
Results:

## Slide 60
Deflection check
Immediate deflection due to live load:
BLOCK
2

## Slide 61
L=4.85 m | Relative deflection (mm) | Allowable deflection (mm) | 
Live | 4.94 | 13.47 | OK
Long term | 19.26 | 20.21 | OK
BLOCK
2
Deflection check
Immediate deflection due to live load:
Results:

## Slide 62
Modifiers/Section | Slab | Shear walls
Membrane f11 Direction | 1 | 1
Membrane f22 Direction | 1 | 1
Membrane f12 Direction | 1 | 1
Bending m11 Direction | 1 | 1
Bending m22 Direction | 1 | 1
Bending m12 Direction | 1 | 1
Shear v13 Direction | 1 | 1
Shear v23 Direction | 1 | 1
Mass | 1 | 1
Weight | 1 | 1
Modifiers for area structural element
Structural period T check

## Slide 63
Modifiers/Section | beams | Columns | Bracing
Cross Section(axial) Area | 1 | 1 | 1
Sheer Area in 2 direction | 1 | 1 | 0
Sheer Area in 3 direction | 1 | 1 | 0
Torsional Constant | 1 | 1 | 0
Moment of Inertia about 2 axis | 1 | 1 | 0
Moment of Inertia about 3 axis | 1 | 1 | 0
Mass | (Depth-200)/200 | 1 | 0
Weight | (Depth-200)/200 | 1 | 0
Structural period T check
Modifiers for frame structural element

## Slide 64
Structural period T check
The structure period shall be determined from one of the following methods
(UBC_97 section 1630.2.2):
Method A:
The period, T is given by:
Hn= height of structure in meters=39.70m
Take Ct=0.0488
So, T=
Method B:
The period (T) is given by

## Slide 65
Structural period Method B
We defined a Mass source as shown below to convert all additional mass into load
wi=0.25 WLi + W Deadi + WSDi + W Eternal walli
+ 0.5 (W columns + W shear wall) above and below the floor

## Slide 66
Structural period
No Torsion
Before starting, it’s important to insure that there is no torsion in mode 1 in the structure, so
one of the mass displacements in X direction or in Y direction must be larger than 50% of the total mass displacement
the rotation about Z direction must be smaller than (20-30)%.

## Slide 67
Structural period
BLOCK
1
ETABS results:
the period from ETABS T=1.183 sec
From the figure we can see most of mass displacement in Y direction with 67% and Rz is <<30%. So there is no torsion in this block

## Slide 68
Structural period Method B

## Slide 69
Structural period Method B
 | fi (KN) | 𝛅i (mm) | fi* 𝛅i | Wi (KN) | Wi* 𝛅i2
F6 | 391.36 | 19.70 | 7709.79 | 6328.57 | 2456053.04
F5 | 432.48 | 18.90 | 8173.89 | 8024.23 | 2866334.82
F4 | 407.22 | 17.80 | 7248.49 | 8118.27 | 2572193.23
F3 | 374.27 | 16.40 | 6137.99 | 8118.27 | 2183490.37
F2 | 334.35 | 14.70 | 4920.48 | 8118.27 | 1754277.35
F1 | 395.46 | 13.10 | 5180.55 | 10086.85 | 1731004.83
G0S | 320.06 | 11.20 | 3584.62 | 7959.61 | 998452.98
G0 | 263.60 | 9.20 | 2425.15 | 8955.48 | 757992.24
B1 | 183.54 | 6.40 | 1174.68 | 8649.27 | 354273.99
B2 | 120.95 | 4.20 | 507.98 | 10182.15 | 179613.10
B3 | 73.01 | 2.20 | 160.62 | 12069.28 | 58415.34
B4 | 19.52 | 0.60 | 11.71 | 10050.01 | 3618.01
Total |  |  | 47235.96 |  | 15915719.29

## Slide 70
 | T ETABS=1.183 Sec | 
Method | Method A | Method B
T (Sec) | 0.770 | 1.164
Error% | 34.91 | 1.61
 | less than 40 % | less than 10 %
Structural period Method B
Final results :
BLOCK
1

## Slide 71
Structural period Method B
BLOCK
2

## Slide 72
Structural period Method B
BLOCK
2

## Slide 73
 | T ETABS=0.708 Sec | 
Method | Method A | Method B
T (Sec) | 0.770 | 0.653
Error% | 8.757 | 7.768
 | less than 40 % | less than 10 %
BLOCK
2
Structural period Method B
ETABS results:
the period from ETABS T=0.708 sec
Final results :

## Slide 74
Participating mass ratio check
“Modal Analysis”
BLOCK
1
Modal analysis was done and the modal mass participating ratio for a mode provides a relative measure of how important the mode is for computing the response to the Acceleration loads in each of the three global directions. Thus it is useful for determining the accuracy of response-spectrum analyses. Ritz method is used for the modal analysis.

## Slide 75
Base Shear check
“Equivalent Static”
BLOCK
1
V = 9314.8 kN
OK

## Slide 76
Base Shear check
“Response Spectrum”
BLOCK
1
TABLE: Base Reactions |  |  |  |  |  | 
Load Case/Combo | FX | FY | FZ | MX | MY | MZ
Unit | kN | kN | kN | kN-m | kN-m | kN-m
EQ x Max | 9811.4 | 2980.2 | 3079.4 | 51365.9 | 220549.0 | 74680.1
EQ y Max | 3226.3 | 9926.7 | 3796.3 | 239332.6 | 48945.5 | 73167.4
 | ETABS | manual | 
V Eq x | 9811 | 9812 | OK
V Eq y | 9927 | 9812 | OK
V Eq x in Y | 2980 | 2943.6 | OK
V Eq Y in x | 3226 | 2943.6 | OK

## Slide 77
Drift check
BLOCK
1
The design story drift (Δ) shall not exceed the allowable story drift (Δall) as obtained from Table 12.12-1 in ASCE 7-10 for any story which is ≤0.02hx.
X - Direction |  |  |  |  |  | 
floor# | story height (m) | Horizontal deflection for each floor (ETABS) (mm) | Inter story drift (mm) | max Inelastic deflection (0.7×R×∆)(mm) | Allowable deflection (mm) | result
GF | 3.5 | 11.33 | 4.13 | 15.9 | 70 | OK
B1 | 3 | 7.2 | 3.034 | 11.7 | 60 | OK
B2 | 3.2 | 4.166 | 2.636 | 10.1 | 64 | OK
B3 | 3.8 | 1.53 | 1.23 | 4.7 | 76 | OK
B4 | 3.25 | 0.3 | 0.3 | 1.2 | 74 | OK
… | … | … | … | … | … | …
All values of drift are less than 0.02hx, so it is OK.

## Slide 78
Structural Irregularity check
BLOCK
1

## Slide 80
Members
Slabs
Shear walls
Beams
Columns
Staircase
Footing

## Slide 81
Design of Slab

## Slide 82
Design of Slab
= × × λ××bw × d= 98 kN
From ETABS, the result of V13 and V23 within the range of(-98)and(98).
< Vu
BLOCK
1
Check wide beam shear:

## Slide 83
Asmin = ρ b h= 0.0018 X 1000 X 200 = 360 mm2 (use 1 12/250mm)
ΦMn=26.6 kN.m /m
Design the slab for flexure:

## Slide 84
      Design the slab for Tension and compression:
T= Φ× As ×fy
For floor F1, the value of Tension and compression was 450kN in both directions.
So, the area of steel required to resist this force equal:
As =
Use (6 Φ 16/m)

## Slide 85
 | Steel requirement/m |  |  |  |  |  |  | 
 | Due to moment |  |  |  | Due to tension & compression |  |  | 
 | X-direction |  | Y-direction |  | X-direction |  | Y-direction | 
Floor | Top | Bottom | Top | Bottom | Top(C) | Bottom(T) | Top(C) | Bottom(T)
F6 | 4 Φ 12 | 4 Φ 12 | 4 Φ 12 | 4 Φ 12 | No need | No need | No need | No need
F2-F5 | 4 Φ 12 | 4 Φ 12 | 4 Φ 12 | 4 Φ 12 | No need | No need | No need | No need
F1 | 4 Φ 12 | 4 Φ 12 | 4 Φ 12 | 4 Φ 12 | 6 Φ 16 | 4 Φ 16 | 6 Φ 16 | 7 Φ 16
Shed | 4 Φ 12 | 4 Φ 12 | 4 Φ 12 | 4 Φ 12 | No need | No need | No need | No need
GF | 4 Φ 12 | 4 Φ 12 | 4 Φ 12 | 4 Φ 12 | 6 Φ 16 | 6 Φ 16 | 4 Φ 16 | 4 Φ 16
B1 | 4 Φ 12 | 4 Φ 12 | 4 Φ 12 | 4 Φ 12 | No need | No need | No need | No need
B2 | 4 Φ 12 | 4 Φ 12 | 4 Φ 12 | 4 Φ 12 | No need | No need | No need | No need
B3 | 4 Φ 12 | 4 Φ 12 | 4 Φ 12 | 4 Φ 12 | 4 Φ 16 | 4 Φ 16 | 6 Φ 16 | 6 Φ 16
B4 | 4 Φ 12 | 4 Φ 12 | 4 Φ 12 | 4 Φ 12 | 5 Φ 16 | 6 Φ 16 | 5 Φ 16 | 5 Φ 16
BLOCK 1

## Slide 86
 | Steel requirement/m |  |  |  |  |  |  | 
 | Due to moment |  |  |  | Due to tension & compression |  |  | 
 | X-direction |  | Y-direction |  | X-direction |  | Y-direction | 
Floor | Top | Bottom | Top | Bottom | Top(C) | Bottom(T) | Top(C) | Bottom(T)
F6 | 4 Φ 12 | 4 Φ 12 | 4 Φ 12 | 4 Φ 12 | No need | No need | No need | No need
F2-F5 | 4 Φ 12 | 4 Φ 12 | 4 Φ 12 | 4 Φ 12 | No need | No need | No need | No need
F1 | 4 Φ 12 | 4 Φ 12 | 4 Φ 12 | 4 Φ 12 | No need | No need | No need | No need
Shed | 4 Φ 12 | 4 Φ 12 | 4 Φ 12 | 4 Φ 12 | No need | No need | No need | No need
GF | 4 Φ 12 | 4 Φ 12 | 4 Φ 12 | 4 Φ 12 | No need | No need | No need | No need
B1 | 4 Φ 12 | 4 Φ 12 | 4 Φ 12 | 4 Φ 12 | No need | No need | 6 Φ 14 | 6 Φ 14
B2 | 4 Φ 12 | 4 Φ 12 | 4 Φ 12 | 4 Φ 12 | No need | No need | No need | No need
B3 | 4 Φ 12 | 4 Φ 12 | 4 Φ 12 | 4 Φ 12 | No need | No need | No need | No need
B4 | 4 Φ 12 | 4 Φ 12 | 4 Φ 12 | 4 Φ 12 | No need | No need | No need | No need
BLOCK 2

## Slide 87
where:
  cc=clear cover to bars=40 mm.
  =stress in steel at service load
=×fy =280 MPa
According to ACI315-04code, the spacing between bars:
      Notes For Reinforcement of slabs:
So using S =250 mm is OK.

## Slide 88
Beams distribution and Slab Reinforcement of Floor 1 :
BLOCK
1

## Slide 89
Design of Beams

## Slide 90
BLOCK
1
      Reinforcement of Beams:

## Slide 91
S1=
s2 = min
      Notes For Reinforcement of Beams:
Notes: Bottom steel at face of joint ≥ 1/3 top steel at face of joint
Bottom or top steel at any section ≥ 1/5 top steel at face of joint

## Slide 92
Design of columns

## Slide 93
      Column axis Layout:

## Slide 94
      Reinforcement of Columns:

## Slide 95
S0=
S1=
l0=
      Notes For Reinforcement of Beams:

## Slide 96
Design of Shear Walls

## Slide 97
 | Vertical reinforcement/m | As/2 | Reinforcement | Horizontal reinforcement/m | Reinforcement
SW1, SW2, SW4 | 750 | 375 | 1φ12/200mm | 750 | 1φ12/200mm
SW3 | 750 | 375 | 1φ12/200mm | 1070 | 1φ14/200mm
SW5 | 2025 | 1013 | 1φ18/200mm | 1300 | 1φ16/200mm
      Distribution and Reinforcement of Shear Wall:

## Slide 98
 | Vertical reinforcement/m | As/2 | Reinforcement/m | Horizontal reinforcement/m | Reinforcement
SW6 | 3144 | 1572 | 1φ20/200mm | 625 | 1φ10/200mm
SW7 | 1731 | 866 | 1φ16/200mm | 625 | 1φ10/200mm
SW8 | 1179 | 590 | 1φ12/200mm | 625 | 1φ10/200mm
SW9 | 750 | 375 | 1φ10/200mm | 625 | 1φ10/200mm

## Slide 99
Design of Foundation

## Slide 100
Type of Foundation
BLOCK
1
The area of footing =
= = 470 m2
The ratio of area of footing to area of basement = *100% = 63.6 %
The ratio is larger than 50%.
So, the type of footing will be Mat foundation.

## Slide 101
BLOCK
1
      Plan of Mat Foundation:

## Slide 102
      Material, Mat Section and Soil property Definition:

## Slide 103
Checks
Bearing capacity
Shear capacity
Deflection

## Slide 104
The maximum soil pressure is less than 250 kN/m2
      Bearing capacity of soil
So it is OK

## Slide 105
From SAFE the largest displacement (U3) = 8.2 mm which is less than 10 mm.
      Deflection check
So it is OK

## Slide 106
When the ratio of punching shear < 1, it means that there is no punching shear occurs.
We noticed that all values are less than 1.
      Shear capacity check
      (punching)
So the thickness of mat is OK.

## Slide 107
Asmin = ρ b h = 1800 mm2 Use 4 Ø25/m
Design of mat foundation
Asmin = ρ b h
= 0.0018 × 1000 × 1000 = 1800 mm2 (use 12 14mm )
So, As = 12×153.86= 1846.3 mm2
ΦMn= 0.9×As×fy× (d-d’)
= 0.9×1846×420× (920-(32.58/2)) ×10-6 = 630.6 kN.m /m
By making range between (-630.6 to 630.6) kN.m/m in M11 and M22 as shown in the following Figures:

## Slide 108
M11 and M22 of the mat foundation from ETABS
For regions those need a min steel, Use
4 Ø25/m as a top and bottom steel in both Direction.
For all other areas that do not meet minimum area of steel (dark purple and dark blue) have a reinforcement of column strip as follows:

## Slide 109
Distribution of column strip

## Slide 110
Frames in X directions:
Frames in X-direction |  | 
Frame | Top steel (mm2) | Bottom steel (mm2)
Frame A | 4 Ø25/m | 4 Ø32/m
Frame B | 4 Ø25/m | 7 Ø32/m
Frame C | 7 Ø25/m | 7 Ø32/m
Frame D | 9 Ø25/m | 7 Ø32/m
Frame E | 5 Ø25/m | 6 Ø32/m
Frame F | 5 Ø25/m | 5 Ø32/m

## Slide 111
Frames in Y-direction |  | 
Frame | Top steel (mm2) | Bottom steel (mm2)
Frame 1 | 5 Ø25/m | 4 Ø25/m
Frame 2 | 6 Ø25/m | 7 Ø32/m
Frame 3 | 7 Ø25/m | 8 Ø32/m
Frame 4 | 7 Ø25/m | 7 Ø32/m
Frame 5 | 10 Ø25/m | 8 Ø32/m
Frame 6 | 7 Ø25/m | 7 Ø32/m
Frame 7 | 7 Ø25/m | 6 Ø32/m
Frame 8 | 8 Ø25/m | 6 Ø32/m
Frame 9 | 7 Ø25/m | 7 Ø32/m
Frame 10 | 8 Ø25/m | 6 Ø32/m
Frames in Y directions:

## Slide 112
Design of Stairs

## Slide 113
The thickness of stair slab is assumed based on ACI 318-11 ,which equal 150 mm (landing and flight)
Loads:
  The own weight of stairs = 3.75 kN/m2
  Live load (LL) = 5 kN/m2
  Superimposed dead live () =~ 4.2 kN/m2
Design of Stairs

## Slide 114
A𝑙𝑙𝑎𝑤𝑎𝑏𝑙𝑒 𝐿𝑜𝑛𝑔 𝑡𝑒𝑟𝑚 deflection, ∆𝐿 ≤ 11.25 mm
The long term deflection from SAP found approximately = 2.00 mm
which means that is smaller than the allowable deflection
Deflection Checks:
So, Its OK

## Slide 115
VC= 72.8 kN
Vu13 and Vu23= 56.20 & 67.00 kN respectively.
Check for shear:
So, The slab thickness is OK

## Slide 116
For landing:
Use As= 270 (4ɸ10/m in two direction)
For Flight:
Design for flexural:
Mu max =8 kN.m
As= 0.00236 × 1000×110 =260
=0.0018×1000×150=270 (Consider it as slab)
As >
Mu22 max =8.6 kN.m
As=0.00191× 1000×110 =210
=0.0018×1000×150=270
As <
Use As= 270 (4ɸ10/m in two direction)
)

## Slide 117
For Beam:
Use As= 660 (6ɸ12/m)
Design for flexural:
Depth= 200 mm
Width= 200 mm
Effective depth= 160 mm
Mu = 1.5 kN.m
ρ>>> 0.0033
As min= 0.0033 ×1000×200 = 660 mm <<< 6ɸ12/m

## Slide 118
Stair Reinforcement:

## Slide 119
References
Nilson, Arther H., David Darwin, Charles W. Dolan.” Design of Concrete Structure. Fourteenth edition”. New York: McGraw-Hills Companies, Inc., 2010.
ASCE Committee, “American society of Civil Engineers, Minimum Design loads for Buildings and other Structures” American Society of Civil Engineers, Virginia 20191, 2010.
ACI Committee 318 “Building Code Requirements for Structural Concrete
(ACI 318M-11)” American Concrete Institute, Michigan, 2011.
Reinforced concrete () notes.