## Slide 1: Graduation Project II
Design and cost estimation of the wastewater collection network for Bidya Village and a study of the water consumption at schools
Prepared by :
Mohamad Mousa
Mohammad Al sadi
Sanad Qashoa
Under the supervision of Dr. Mohammad N. Almasri

## Slide 2: Introduction:
Bidya Village lies in the north west of Salfit City in Palestine, Bidya has a total area of about 13,428 donums .
Elevations in the village vary significantly from one place to another with maximum and minimum values of 390 m and 215 m AMSL.

## Slide 3
Bidya has an overall area of 13,428 dounms.
1,633 donums is residential areas have a blue color.

## Slide 4: STUDY AREA

## Slide 5: LOCATION

## Slide 6: OBJECTIVES
To design the wastewater collection network for Bidya using SewerCAD.
To estimate the cost of the network.
To compare the consumption of water at schools between Jenin and Qalqilya.

## Slide 7: METHODOLOGY OF DESIGN THE NETWORK

## Slide 8: LIMITATION
Hard terrain is big challenge.
The network must be in street because it public ownership.
We need 1m contour map to know more details about elevations.

## Slide 9: DATA COLLECTION
Road network.
Contour map.
Boundary of study area.
Population number.
House distribution.

## Slide 10: TOPOGRAPHIC NATURE
Due to the topography nature in Bidya we divided the network into three parts north, middle and south in terms of the location of each part in the town, the outfall direction in each part is north, west and south respectively

## Slide 11: North part

## Slide 12: Middle part

## Slide 13: South part

## Slide 14: Standards and specifications
Water consumption is 120 l/c. d.
Return flow of 80% of the consumption.
Infiltration rate of 5% of the flow.
Length of conduit: 30-50 m.
Material: PVC pipes.
Pipe sizes: minimum 8 inches (200 mm).
Full flow: 75% of the cross section.
(MHF): The peak factor used is 4.
Velocity: 0.6 - 3 m/s.
Cover: 1 - 4 m.
Slope: 1-12%.

## Slide 15: Design
After drawing the manholes on ArcMap, the final model for three parts has 1316 manholes.

## Slide 18: Population Prediction
Year | 2007 | 2017
Population | 7,978 | 10,451
=×→10,451=7,978×→r= 2.73%
=×→=10451×→ = 23,442 persons

## Slide 19: Load on manhole
Total peak wastewater generationpopulation in 30 yearPer capita water demandWW to W ratioMHF (1+infiltration)

## Slide 20: First attempt in SewerCAD
When put the manhole and conduits shapefiles for three zones in SewerCAD some results of velocity and cover depth was out of criteria range.

## Slide 21: Velocity and cover depth in north part

## Slide 22: Velocity and cover depth in middle part

## Slide 23: Velocity and cover depth in south part

## Slide 24: Second attempt in SewerCAD
The range of design criteria for the minimum velocity form 0.6 m/s to 0.45 m/s
Network connectivity.
We did edit in

## Slide 25: Velocity values in north part

## Slide 26: Cover values in north part

## Slide 27: Velocity values in middle part

## Slide 28: Cover values in middle part

## Slide 29: Velocity values in south part

## Slide 30: Cover values in south part

## Slide 31: Profiles:

## Slide 33: Discussion
Prioritizing velocity constrains in SewerCAD rather than the cover constrains.
Is the small flow at the beginnings of the networks.
Existence of quite level ground elevation that conduits go along below it.
Problems in cover on many conduits appeared,
this is due to three reasons:

## Slide 34: Conclusions
There are three outfalls of the study area.
The final model for three zones has conduits 1372 and 1316 manholes.
The Network has an 8,10 inch pipe diameter.
All slopes for conduits lie between (1% -12%)
Some conduits have a velocity greater than 3 m/s because they have big slopes.

## Slide 35: Recommendations
The wastewater should be treated to avoid pollution, illness and other problems of wastewater gathering so wastewater treatment plant must be constructed.
The Joint Service Council must implement the same project for all the neighbour villages to collected wastewater from all to reach one outfall somewhere in the west.

## Slide 36: Cost estimation of the network
The main cost drivers for wastewater collection network:
Conduits.
Manholes.
Excavation depth.

## Slide 37: Result of the cost estimation
cost ($) | Description | #
1,203,334 | South part | 1
885,944 | North part | 2
2,193,115 | Middle part | 3
15,625 | Mobilization | 4
4,688 | Testing | 5
4,302,705 | Total cost ($) | 
164 | Total cost/m ($) | 
369 | Total cost per capita ($) | 
we compared our result with the costs of a new project similar in Bidya approved on 10/2021 has a cost equal to 159$/m but in our project the cost equal to 164$/m.

## Slide 38: Water consumption at schools
The student's water consumption (L/d) for year 2017 at Al khansaa school
Student's daily water consumption rate (L/d) | Number of students | The sum | The consumption | The mounth
3.88 | 481 | 681 | 101 | 1
 |  |  | 30 | 2
 |  |  | 20 | 3
 |  |  | 81 | 4
 |  |  | 13 | 5
 |  |  | 192 | 6
 |  |  | 23 | 7
 |  |  | 87 | 8
 |  |  | 13 | 9
 |  |  | 25 | 10
 |  |  | 27 | 11
 |  |  | 69 | 12

## Slide 39: Results of consumption rates in Jenin villages
Chart: 2017 2018 2019
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | 70 | 71 | 72 | 73 | 74 | 75 | 76 | 77 | 78 | 79 | 80 | 81 | 82 | 83
2017 | 3.8789 | 1.686 | 4.9729 | 7.6495 | 3.0474 | 3.6862 | 1.8826 | 1.8121 | 2.8839 | 4.7818 | 1.8895 | 3.2266 | 6.7248 | 2.2533 | 13.037 | 4.1014 | 2.6027 | 1.6809 | 2.6075 | 8.7852 | 2.0599 | 1.9191 | 2.3992 | 16.0058 | 9.2985 | 2.5615 | 8.8136 | 10.6234 | 3.5472 | 1.9389 | 4.5984 | 5.8992 | 3.306 | 1.6751 | 1.3133 | 0.74586
2018 | 1.711 | 1.1817 | 16.7908 | 1.4773 | 3.4314 | 1.9704 | 1.6116 | 1.8349 | 2.3256 | 5.2319 | 3.2327 | 5.1388 | 5.7361 | 1.7203 | 2.6093 | 1.2856 | 2.0629 | 2.544 | 1.446 | 1.2765 | 14.3296 | 2.2633 | 2.0025 | 6.9036 | 3.8371 | 3.3249 | 18.6112 | 1.4247 | 18.287 | 8.6575 | 3.7368 | 0.76178 | 4.0468 | 2.5786 | 3.6441 | 1.8166 | 2.0445 | 0.85659
2019 | 5.6847 | 2.0832 | 3.8356 | 6.8004 | 1.9256 | 4.4631 | 2.0032 | 2.1044 | 2.2852 | 2.5463 | 2.017 | 0.31566 | 7.9524 | 8.8093 | 2.4695 | 2.4849 | 2.0908 | 2.1075 | 5.1995 | 1.2938 | 3.3251 | 9.2629 | 2.4473 | 3.1816 | 4.1553 | 4.4579 | 3.1152 | 7.5405 | 22.151 | 3.1139 | 7.1122 | 5.2617 | 1.8211 | 5.9379 | 4.3108 | 1.8838 | 0.95115 | 2.8493 | 0.8505

## Slide 40: Results of consumption rates in Jenin city
Chart: 2017 2018 2019
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23
2017 | 1.9394 | 0.67714 | 6.4004 | 0.91505 | 2.9345 | 1.1877 | 2.3695 | 2.5472 | 0.29966 | 2.5186 | 1.7051 | 3.8678 | 4.365 | 2.2701 | 1.4912 | 3.29 | 7.7688 | 1.4171 | 6.6868 | 1.9857 | 1.0415 | 2.1689 | 0.63166
2018 | 1.1827 | 0.24809 | 4.0277 | 0.83753 | 1.8756 | 1.7489 | 2.2847 | 1.4547 | 1.6468 | 2.0091 | 2.8493 | 2.1689 | 2.2095 | 1.1367 | 2.2297 | 1.1627 | 5.6339 | 1.4854 | 2.7636 | 1.7595 | 0.60093 | 1.925 | 0.47264
2019 | 1.865 | 1.2671 | 3.3193 | 1.2032 | 3.1174 | 1.9277 | 4.1096 | 2.7256 | 1.6529 | 8.9254 | 1.8967 | 2.8932 | 1.9313 | 1.9524 | 6.1196 | 6.071 | 4.7681 | 1.4415 | 2.2551 | 3.1705 | 1.0421 | 2.2863 | 0.60606

## Slide 41: Results of consumption rates in Qalqilya city
Chart: 2017 2018 2019
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27
2017 | 8.0007 | 9.1058 | 9.8935 | 8.8544 | 4.6336 | 3.0437 | 8.4853 | 6.671 | 7.6135 | 9.2057 | 6.4852 | 1.3969 | 14.2491 | 5.2727 | 2.881 | 2.9255 | 4.3674 | 2.3483 | 7.7277 | 4.5561 | 7.7191 | 3.5385 | 1.6084 | 7.3294 | 3.2949 | 4.7047 | 17.5313
2018 | 3.3988 | 4.693 | 10.6362 | 4.9715 | 3.6687 | 2.4796 | 6.0784 | 1.7205 | 8.0406 | 6.5199 | 9.5449 | 1.7717 | 3.4376 | 2.3814 | 3.6892 | 29.5775 | 2.9492 | 2.2394 | 8.7716 | 7.9457 | 7.0357 | 4.2275 | 1.7822 | 6.7992 | 4.2242 | 5.0574 | 7.8829
2019 | 3.1562 | 5.3751 | 7.0272 | 6.1428 | 9.7931 | 3.4811 | 14.0667 | 2.9693 | 5.7061 | 7.1376 | 10.1275 | 21.9839 | 3.7009 | 3.2832 | 2.7808 | 2.3051 | 2.9609 | 2.8936 | 20.3458 | 5.4841 | 5.4928 | 9.8338 | 3.6371 | 11.2438 | 3.9041 | 3.0018 | 15.1687

## Slide 42: Results of consumption rates
The consumption rate in Jenin villages (L/d) |  |  | 
min | max | avg | 
0.75 | 16.01 | 4.44 | 2017
0.76 | 18.61 | 4.31 | 2018
0.32 | 22.15 | 4.16 | 2019
The consumption rate in Jenin city (L/d) |  |  | 
min | max | avg | 
0.30 | 7.77 | 2.63 | 2017
0.25 | 5.63 | 1.90 | 2018
0.60 | 8.93 | 2.89 | 2019
The consumption rate in Qalqilya city (L/d) |  |  | 
min | max | avg | 
1.40 | 17.53 | 6.42 | 2017
1.72 | 29.58 | 5.98 | 2018
2.31 | 21.98 | 7.15 | 2019

## Slide 43: Comparison between schools’ categories in Jenin and Qalqilya Cities
(Females > males) in elementary and secondary schools.
Secondary schools > elementary schools.

## Slide 44: References
Bidya Municipality.
Palestinian Central Bureau of Statistics.
Dr. Mohammad N. Almasri website(https ://sites.google.com/site/mohammadnablus/Home).
https ://geomolg.ps/ .

## Slide 45
THANK YOU