## Slide 1: An-Najah National University Faculty Of Engineering Civil Engineering Department Graduation Project II
Analysis and Redesign of Water network & Design of Wastewater network for Kaferdan village
Prepared By :
Abdallah Bzoor
Kefah Ali
Mohammed Abo Abed
Supervision of Dr. Anan Jayyousi

## Slide 2: Outline:
Objectives of the project.
Significance of the work
Study area
Questionnaire analysis
Existing water network
Redesign of water network
Design of wastewater network

## Slide 3: Objectives
Analyze the existing water network.
Redesign the water network in the village.
Design a wastewater network.

## Slide 4: Significance of the work
To supply water at an adequate pressure and flow.
To transport sewage through KAFERDAN VILLAGE to sewage treatment plants.
To have an economic design as possible for both networks.

## Slide 5
Study area

## Slide 6
Area and land use:
The present population is 6400 persons.
The area is approximately 7330 donum
Kaferdan village is a flat land, The ground surface in the village varies from 100 m to 190 m (A.M.S.L).

## Slide 7
Data Collection:
Contour, Houses, roads, Boundary, aerial photo and amount of consumption water for each consumer,… etc. manhole, conduits, road contour and outfall for the village.

## Slide 8: Questionnaire analysis
avaerage consumption water
Average family size = 5.9 capita
Average consumption = 11.9 m³
So the water consumption = (11.9*1000)/(30*5.9)= 67.2 L/C/day

## Slide 11: Modeling of WDN
Present population (2016) = 6399 capita
Water consumption = 67.2 Little /capita/day
Total consumption (Demand) = (6399 capita *67.2 Litter/capita/day) / (1000 litter/m³)
Demand = 470.4 m³/day
Supply =
Supply = = 670 m³/day

## Slide 12: Modeling of WDN

## Slide 13: WDN

## Slide 14: WDN
Design constraints:
Pressure at junction between (20-100) m.H2O.
Velocity in pipe (0.3-3.0) m/s.

## Slide 15: Result of analysis of WDN
Preesure at minimum demand (2:00am) and maximum demand (6:00am)

## Slide 16: Result of analysis of WDN
Velocities at minimum demand (2:00am) and maximum demand(6:00am)

## Slide 17: Redesign of WDN

## Slide 18: Data of future population
Where:
P(t) : number of population for (t) of times.
Po : number of population now .
K : proportionality constant.
t : number of years .
In Koferdan town :
Po = P2016 = 6399 capita
t = 30 years

## Slide 20: Data of future population
To calculate the constant K . It will take the years 1997 and 2007 , and the population for these years are 3816 and 5087 respectivilly .
K = 0.0287
Thus;
P2046 = 15159 capita.

## Slide 21: Data of the supply
the average municipal consumption is 120 L/C/Day.
Avaerage Supply =
Avaerage Supply = = 141 L/C/Day
Total supply that should be design of Koferdan water network on it = 141*15159 = 2140451 L/Day = 2140.45 m³/day

## Slide 22: Model of WDN

## Slide 23: WDN

## Slide 24: Design Critera
Type of pipes / Criterea | Pressure(mH2O) | Velocity(m/sec)
Ductile iron | 20-100 | 0.1- 3

## Slide 25: Methodology of Design

## Slide 27: Result of Design
1- Pumps

## Slide 28: Result of Design
Pw = ɤQH
Where :
ɤ : Specific weight for water(N/ m³).
Q : Total flow rate that input to pump (m³/sec).
H : Total head that was added by pump (m).
Pw = (9810 N/ m³)*(3852/24*60*60 m³/sec)*(20m) =8747.25 watt.
Pw = 8.74725 Kelowatt = Poutput .
Pinput = Poutput/µ
Where :
µ : The efficiency of the pump (-)
Pinput = 8.74725/0.85 = 10.29 kelowatt.
The power of pump (hp) = 10.29/0.75 = 14 hp

## Slide 29: Result of Design
The below drown illustration the method of installation the two pump in series:

## Slide 30: Result of Design
2- Preesures
Pressure at maximum demand (6:00am) by using of two pumps
Chart: 

## Slide 31: Result of Design
Pressure at minimum demand (2:00am) by using of one pump
Chart: 

## Slide 32: Result of Design
3- Velovities
Velocity at maximum demand (6:00am) by using of two pumps
Chart: 

## Slide 33: Cost of The design
Total cost = (Ʃ Ci*Li) + Cost of two pumps.
Where :
Total cost ($).
Ci : The cost of diameter i (inch) per meter ($/m).
Li : The length of diameter i (m).
In this network was the estimated total cost was 303262 $ .
Cost of one pump (15hp) = 14000$
The total cost = 303626+28000 = 331626 $

## Slide 34: Design of the wastewater network

## Slide 36: Wastewater generation
Each person in the town will generate about 80% of water consumption(120L/c/day).
Thus , Avaerage wastewater generation = 0.8 * 120 * 15159/ 1000 = 1455.26 m³/day
Peak wastewater generation = Pf * Avaearage wastewater generation
Where :
Pf : Peak factor = 16* {(Population in thousands)^(-1/6)} = 16 * (15159)^(-1/6) = 3.2
Then , Peak wastewater generation for koferdan town = 3 * 1455.26 = 4365.75 m³/day

## Slide 37: Design criteria
The velocity : (0.6 – 3 m/sec)
The cover : (1-5m)
The slope : (1-15%)
The distance between manholes are (30-50 m)

## Slide 38: Design constrain

## Slide 39
MODELING AND DESIGN

## Slide 40: Methodology

## Slide 41: Methodology
Location & Connecting Manhole
Before starting the design we should consider that the manholes must be located at the roads networks wherever there is:
1- An intersection.
2- Change in slop.
3- Change in direction.
4- Maximum distance of (30-50) m.

## Slide 42: Choosing the PVC conduits

## Slide 43: Model of the wastewater network

## Slide 44
Loads on manholes
By finding the area of catchment of each manhole using ArcHydro Tool in GIS we can find the load for each manhole as follows:
15159 capita/7328000 m² = 0.002 capita/ m²
0.002* area of each part = number of persons in each part(q˳)
Load was produced from each part = (120L/c/d * q˳* 3 * 0.8) + (120* q˳* 0.8 * 0.2)

## Slide 45
Results And Discussion

## Slide 46
Velocity (m/s)

## Slide 47
Slope (%)

## Slide 48
Cover (m)

## Slide 49
Profile

## Slide 50: The proposed location for Wastewater Treatment Plant
Location of WWTP

## Slide 51
After the end of design process we got the following conclusions:
The majority diameter of water pipes are 1.3, 2,3,4,6 and 8 inch.
The water pipe material is ductile iron.
The sewer conduit material is PVC because it's easy to site.
Most sewer network conduits diameters are 8,10,12 inch.
ArcHydro tools save a lot of time in calculates loads.
Conclusions

## Slide 52
Recommendations
A periodic maintenance should be done and the damaged parts should be replaced.
If possible treatment plant is considered as a feasible project.
Suitable space between water pipes and wastewater pipes must be achieved (water pipes must be above wastewater pipes).