## Slide 1: An-Najah National University Building Engineering Department
Integrated redesign of a faculty of architecture in Nablus city
Prepared By:
Marwan Akhras
Musab Seddeh
Jameel Sabbah
Supervisor:
Eng. Haitham Sawalha

## Slide 2: Contents
Architectural
Site and location
Environmental design
Passive design
Structural Design
Electro- Mechanical Design
BOQ
Fire and safety

## Slide 3
Site and location

## Slide 4
This faculty is located in Nablus city, which lies in the north of west bank, approximately 30 mile north of Jerusalem; Nablus is about 565 m above sea level. The site is located in Al-Najah University on latitude 32.2N and longitude 35.2 E.
Site location

## Slide 5
Architectural Plans

## Slide 6
The 3rd model for the existed architectural plan.

## Slide 7
Basement floor with the site

## Slide 8
Ground floor with the site
Before
After

## Slide 9
Fist floor

## Slide 10
Second floor

## Slide 11
Third floor
Before
After

## Slide 12
Fourth floor

## Slide 13
East elevation

## Slide 14
West elevation

## Slide 15
Section B-B

## Slide 16
Environmental Design

## Slide 17
The model of the faculty from Design Builder before and after modification
Day lighting
Before
After
Main modification for day lighting:
Adding Louvers.
Using low transmission glass.

## Slide 18
Daylight analysis for the model for the third and fourth floors before and after modification
Before
After

## Slide 19
Thermal Design

## Slide 20
Summary for the materials that were used in the walls and slabs in the faculty

## Slide 21
The comfort graph for the faculty from Design Builder

## Slide 22
The site and source energy for the faculty from Design Builder
The site energy for the faculty = 111.3 kWh/m2, and the standard required 411.7 kWh/m2 ,for the college (“Portfolio Manager,” n.d.),so it is ok for the faculty.
Temperature and heat gain
Temperature and heat loss

## Slide 23
HVAC system
The system that was used is VRF system and the maximum cooling load equal 374.8 KW.
The components of this system is from TROX and Samsung company.
Four unit with a capacity of 73.6 kw for each unit.
From TROX TECHNIK Company with flow rate of 0.63 m3/s .
From Samsung Company with flow rate of 0.28 m3/s
From Samsung Company with flow rate 0.275 m3/s. and one with flow rate of 0.16 m3/s .
From Samsung Company with flow rate of 0.10 m3/s

## Slide 24
The number of fan coils and indoor unit that are needed in the ground floor
The distribution of the ducts and diffusers in the ground floor.

## Slide 25
The number of fan coils and indoor unit that are needed in the first floor.
The distribution of the ducts and diffusers in the first floor.

## Slide 26
Structural Design

## Slide 27
Concrete with compressive strength of 28 MPa (B350) and 32 MPa(B400)
Steel rebar with yielding strength of 420 MPa
Steel with minimum yield stress of 248.1 MPa.
ACI 318-14
Seismic design UBC 97
ASCE for load design
AISC360-10 for steel analysis,
Codes
Materials
Live load = 5 kN/m2
SID load = 4 kN/m2
1
Mass source: 100% for dead laods and SID , 25% for live laods.
2
Seismic zone : The faculty is located in Nablus city Therefore, the seismic zone is 2B and the Z value is equal to 0.20.
3
Soil profile: The soil type is rock so the soil profile is SB .
4
5
6
Force Reduction Factor R = 5.5 (Building Frame System - shear wall)
Importance Factor I = 1.25
Acceleration-Dependent Seismic Coefficient Ca = 0.2
7
Velocity-Dependent Seismic Coefficient Cv = 0.2
8
Response spectrum scale factor = = = 2230
Response spectrum scale factor = (𝐼×𝑔)/𝑅 = (1.25 ∗9810)/5.5 = 2230
1
Mass source: 100% for dead laods and SID , 25% for live laods.
2
Seismic zone : The faculty is located in Nablus city Therefore, the seismic zone is 2B and the Z value is equal to 0.20.
3
Soil profile: The soil type is rock so the soil profile is SB .
4
5
6
Force Reduction Factor R = 5.5 (Building Frame System - shear wall)
Importance Factor I = 1.25
Acceleration-Dependent Seismic Coefficient Ca = 0.2
7
Velocity-Dependent Seismic Coefficient Cv = 0.2
8
Loads
The parameters for seismic analysis

## Slide 28
Block 2
Block 1
Block 1
Block 2
Ground floor
First floor
Ground and first floors

## Slide 29
ETABS model of block 1
ETABS model of block 2
Safe model
ETABS model of block 1

## Slide 30
Seismic design checks
1. Period and base shear checks for block 1
2. Period and base shear checks for block 2
3. Drift check for block 1
4. Drift check for block 2
Time period from mode 1 (Tx) = 0.469 sec < 0.74 sec, the check is ok.
Time period from mode 2 (Ty) = 0.414 sec < 0.74 sec, the check is ok.
shear results from ETABS are greater than manual calculations, so base shear check is ok
Time period from mode 1 (Tx) = 0.633 sec < 0.742 sec, the check is ok.
Time period from mode 2 (Ty) = 0.453 sec < 0.742 sec, the check is ok.
shear results from ETABS are greater than manual calculations, so base shear check is ok
All drifts in floors < 100 mm, so the check is ok
All drifts in floors < 100 mm, so the check is ok

## Slide 31
Slabs
U-BOOT slab
Solid slab

## Slide 32
Footings layout

## Slide 33
C1
C2
C3
C4
Columns sections
Beams sections

## Slide 34
Steel
For steel design
TUBO
HEE

## Slide 35
Third floor

## Slide 36
Truss 1
C5
C6

## Slide 37
C1

## Slide 38
SPC2

## Slide 39
C12-B

## Slide 40
C12-A

## Slide 41
Retaining wall design

## Slide 42
Electro-Mechanical Design

## Slide 43
The selected Luminaires
Artificial lighting
Lighting with switches

## Slide 44
Illuminance result from DIALux evo for the classroom .

## Slide 45
Auditorium
Lap
Gallery
Jury
Cafeteria
Gallery
Result from DIALux evo for the ground floor.

## Slide 46
Sockets plan for the cafeteria
The electrical load of power, lighting and loud speaker system in the ground floor
Distribution of circuit breaker in distribution board 1
Main distribution board of circuit breaker in the ground floor

## Slide 47
The electrical load of power, lighting and loud speaker system in the main distribution board 1
The electrical load of elevators and HVAC system in the main distribution board 2

## Slide 48
Water consumption
Water tanks
Mechanical system

## Slide 49
Total Fu & water demand
Diameter of the pipes in the faculty
Water collector

## Slide 50
Summary for diameter & pipe slope

## Slide 51
Drainage pipes and manhole on the site

## Slide 52
Elevators assessment
The assessment on the number of elevators will depend on the distribution of the elevators and if the number is enough or not by engineering sense. The distribution of the elevators is good and the number is enough for all the student and stuff.

## Slide 53
Acoustical Design

## Slide 54
The spaces that were designed acoustically in the faculty
The absorption coefficient for the finished material

## Slide 55
Reverberation time(RT60):
The reverberation time for the classroom according to Sabine
The reverberation time for the cafeteria according to Sabine

## Slide 56
Sound Transmission Loss (STC)
The sound transmission loss (STC) for the internal walls between different spaces
The sound transmission loss (STC) for the internal walls between different spaces in the faculty is more than the limit = 49 dB
The OITC for the external walls = 46dB more than the standard = 42 dB (Egan, n.d.), so it is ok for the external walls

## Slide 57
The layers for the ceiling
Impact Insulation Class (IIC)
The Impact insulation class for the ceiling = 52 dB between two classrooms and the calculated IIC for the ceiling should be more than 50 dB, so it is ok.

## Slide 58
Loud speaker
Cafeteria
The direct SPL distribution in the cafeteria at 500 HZ

## Slide 59
Fire and Safety

## Slide 60
The symbols of the suppression system in the plans
The emergency lights and signs
The symbols for the detection and notification system.
Part of firefighting plan for the ground floor

## Slide 61
The different types of sprinkler in the faculty
The different types of the extinguisher

## Slide 62
Flood sprinkler
Wet chemical sprinkler
FM 200 system

## Slide 63
The evacuation plan for the second floor

## Slide 64
Reflected false ceiling for ground floor

## Slide 65
Quantity Surveying and Cost Estimation

## Slide 66
The total cost of the faculty is 22548939 NIS and the total area of the faculty building is 8141 m2 which means that the total unit cost per m2 is 2770 NIS/ m2.
Quantity Surveying
Earth work = 459000 NIS
Foundation Work = 589386 NIS
Sub Structure Work = 308506 NIS
Super Structure = 6804333 NIS
Finishes Work = 8580320 NIS
Electrical work = 449360 NIS
Safety work = 128300 NIS
Mechanical work = 2990850 NIS
Site Work = 2238884 NIS

## Slide 67
Chart: 
| Earth work (5%) | Structural Work (31%) | Finishes Work (38%) | Eelctrical work (2%) | Mechanical work (14%) | Site Work (10%)
 | 1048386.05 | 7112838.74 | 8580320 | 449360 | 3119150 | 2238884
Percentage for each work from total cost of the faculty