## Slide 1
An-Najah National University
Faculty of Engineering & Information Technology
Department of Building Engineering
Integrated redesign of Al-Istiqlal University Library.
By
Zeina Mahamdah
Hanan Abdo
Tasneem Riyad
Under the supervision of Eng. Fadi fatayer

## Slide 2: Contents of the project
01
Introduction
02
Architectural Aspect
03
Environmental Aspect
04
Structural Aspect
05
Electro-mechanical Aspects
06
Quantity surveying & cost estimate

## Slide 3
Introduction
The location of the building
In Jericho – Al-Istiqlal University.
It contains 3 floors.
It has a total area of 5900 SM.

## Slide 4: Architectural Aspects

## Slide 5: Site analysis

## Slide 6: Basement

## Slide 7: Ground floor
Before
After

## Slide 8: First floor
Before
After

## Slide 9: Elevations
South Elevations
North Elevations

## Slide 10: Elevations
East Elevations
West Elevations

## Slide 11: Sections
Section A-A

## Slide 12: Sections
Section B-B

## Slide 13: Sections
Section 1-1

## Slide 14: Sections
Section 2-2

## Slide 15: 3 D Modeling

## Slide 16: 3 D Modeling

## Slide 17: Environmental Aspects

## Slide 18
Shading analysis
At 8 am
Summer 21 June
At 2 pm
At 12 pm

## Slide 19
Shading analysis
At 8 am
Winter 21 December
At 12 pm

## Slide 20
Daylight analysis
Before
For ground floor
After

## Slide 21
Daylight analysis
For first floor

## Slide 22
Heating and cooling load
Heat transfer coefficient (U value) before treatment for the element in the building :
Element type | U value (W/
Exterior wall | 1.893
Floor | 1.753
Roof | 1.413
glass | 3.835
Element type | 
Exterior wall | 1.893
Floor | 1.753
Roof | 1.413
glass | 3.835

## Slide 23
Heating and cooling capacity (before all treatments )
Zone | Design Capacity (kW) | Design Capacity (W/m2)
first-floor design heating capacity=62.4 W |  | 
office 1 | 7.89 | 61.0367
secretary | 1.25 | 79.1594
Main office | 2.86 | 69.7134
documentation | 1.3 | 57.834
meeting room | 5.7 | 56.677
Reading room 2 | 7.47 | 53.3253
study room | 5.46 | 62.9904
server | 0.27 | 32.1282
M.W.C | 0.22 | 38.7563
reading room | 14.08 | 55.815
references hall | 6.16 | 35.3289
F.W.C | 0.37 | 33.4694
lobby | 9.37 | 40.8875
ground floor design heating capacity =59.880 W |  | 
office | 0.67 | 38.3422
computer lap | 11.62 | 62.1027
entrance 1 | 0.77 | 28.7915
police room | 1.34 | 45.4227
multipurpose hall | 10.93 | 57.3048
M.W.C | 0.17 | 29.365
server | 0.24 | 27.8159
F.W.C | 0.3 | 26.7732
entrance hall | 2.12 | 24.1311
LOBBY | 5.03 | 35.4753
info desk | 1.68 | 87.7609
book repair | 1.62 | 63.8066
lobby | 1.36 | 60.6369
bookkeeper | 1.2 | 53.0729
receptions | 3.67 | 29.7169
references hall | 6.21 | 32.5175
reading room | 10.95 | 43.8662
total heating design capacity =112.280 W |  | 
Zone | Design Capacity (kW) | Design Flow Rate (m3/s) | Total Cooling Load (kW) | Design Cooling Load Per Floor Area(W/m2) | Glazing Gains (kW) | Wall Gains (kW) | Floor Gains (kW) | Roof and Ceiling Gains (kW)
office 1 | 14.04 | 0.9669 | 12.2 | 108.6 | 1.215 | 1.265 | -1.516 | 1.185
secretary | 2.1 | 0.1447 | 1.83 | 132.7 | 0.3 | -0.171 | -0.428 | 0.144
Main office | 4.25 | 0.2931 | 3.7 | 103.9 | 0.185 | 0.921 | 0.162 | 0.566
documentation | 2.37 | 0.1633 | 2.06 | 105.7 | 0.193 | 0.23 | 0.121 | 0.331
meeting room | 10.73 | 0.7391 | 9.33 | 106.6 | 0.385 | 0.473 | 0.378 | 1.299
Reading room 2 | 16.18 | 1.1149 | 14.07 | 115.5 | 0 | 0.568 | -0.152 | 1.901
study room | 11.41 | 0.7864 | 9.93 | 131.7 | 0.565 | 1.589 | 0.168 | 1.262
server | 0.53 | 0.0363 | 0.46 | 61.7 | 0 | 0.15 | 0.009 | 0.137
M.W.C | 0.6 | 0.0383 | 0.53 | 105.3 | 0 | 0.067 | -0.004 | 0.091
reading room | 30.95 | 2.1321 | 26.91 | 122.6 | 1.393 | 2.188 | 3.766 | 3.266
references hall | 15.08 | 1.0386 | 13.11 | 86.5 | 0.616 | 0.538 | -0.023 | 2.544
F.W.C | 0.91 | 0.0581 | 0.79 | 83.4 | 0 | -0.002 | -0.017 | 0.162
lobby | 24.84 | 1.5375 | 21.6 | 108.4 | 0.42 | 0.571 | -0.323 | 3.081
office | 1.55 | 0.1068 | 1.35 | 88.7 | 0 | 0.391 | 0.034 | 0
computer lap | 23.85 | 1.6431 | 20.74 | 127.5 | 1.975 | 0.834 | -1.42 | 0.01
entrance 1 | 1.9 | 0.1264 | 1.65 | 70.8 | 0.125 | 0.141 | 0.023 | 0
police room | 2.62 | 0.1802 | 2.27 | 88.5 | 0.26 | 0.204 | -0.047 | 0.006
multipurpose hall | 20.24 | 1.3942 | 17.6 | 106.1 | 1.363 | 1.425 | 0.567 | 0.035
M.W.C | 0.4 | 0.0269 | 0.35 | 69.4 | 0 | 0.098 | 0.006 | 0
server | 0.61 | 0.042 | 0.53 | 72 | 0 | 0.14 | 0.01 | 0
F.W.C | 0.63 | 0.0417 | 0.55 | 56.6 | 0 | 0.066 | 0.007 | 0
entrance hall | 4.76 | 0.328 | 4.14 | 54.1 | 0.061 | 0.146 | 0.04 | 0
LOBBY | 13.1 | 0.8085 | 11.39 | 92.4 | 0.463 | 0.248 | -0.558 | 0.005
info desk | 3.31 | 0.2277 | 2.87 | 172.4 | 0.335 | 0.352 | 0.003 | 0.002
book repair | 2.92 | 0.2011 | 2.54 | 114.7 | 0.118 | 0.575 | 0.062 | 0.004
lobby | 3.44 | 0.2172 | 2.99 | 153.7 | 0.097 | 0.544 | 0.4 | 0.005
book keeper | 2.81 | 0.1939 | 2.45 | 124.4 | 0 | 0.476 | 0.046 | 0
receptions | 8.56 | 0.5899 | 7.45 | 69.3 | 0 | 0.53 | 0.153 | 0
references hall | 14.42 | 0.9932 | 12.54 | 75.5 | 0.752 | 0.823 | 0.469 | 0
reading room | 27.93 | 1.9243 | 24.29 | 111.9 | 2.222 | 1.127 | -0.406 | 0.023
Totals | 267.04 | 18.0945 | 232.21 | 103.6 | 13.042 | 16.505 | 1.529 | 16.061

## Slide 24
U value for external wall after adding insulation

## Slide 25
Heating and cooling capacity after adding external wall insulation
Zone | Design Capacity (kW) | Design Capacity (W/m2)
first-floor heating load =51.330 |  | 
office 1 | 5.35 | 41.3975
secretary | 1.01 | 63.6387
Main office | 1.81 | 44.2567
documentation | 1.01 | 45.2525
meeting room | 4.55 | 45.1679
Reading room 2 | 7.35 | 52.4308
study room | 3.9 | 45.0229
server | 0.25 | 29.7539
M.W.C | 0.21 | 36.6893
reading room | 11.8 | 46.7581
references hall | 5.53 | 31.7337
F.W.C | 0.36 | 32.9037
lobby | 8.2 | 35.808
ground floor heating load=49.410 |  | 
office | 0.58 | 33.1085
computer lap | 9.1 | 48.6597
entrance 1 | 0.73 | 27.2664
police room | 0.98 | 33.0677
multipurpose hall | 8.88 | 46.5608
M.W.C | 0.16 | 27.6251
server | 0.22 | 25.7873
F.W.C | 0.29 | 26.2807
entrance hall | 2.07 | 23.5814
LOBBY | 4.49 | 31.658
info desk | 0.95 | 49.5334
book repair | 1.05 | 41.1894
lobby | 0.95 | 42.4458
bookkeeper | 1.05 | 46.3657
receptions | 3.56 | 28.8505
references hall | 5.6 | 29.3248
reading room | 8.75 | 35.0366
total heating load =100.740 |  | 
Zone | Design Capacity (kW) | Design Flow Rate (m3/s) | Total Cooling Load (kW) | Design Cooling Load Per Floor Area(W/m2) | Glazing Gains (kW) | Wall Gains (kW) | Floor Gains (kW) | Roof and Ceiling Gains (kW)
office 1 | 11.3 | 0.7786 | 9.83 | 87.4 | 1.242 | -0.244 | -1.507 | 1.225
secretary | 1.72 | 0.1182 | 1.49 | 108.4 | 0.303 | -0.373 | -0.446 | 0.144
Main office | 3.07 | 0.2113 | 2.67 | 74.9 | 0.193 | 0.198 | 0.148 | 0.564
documentation | 1.9 | 0.1309 | 1.65 | 84.8 | 0.195 | 0.025 | 0.093 | 0.332
meeting room | 9.07 | 0.6245 | 7.88 | 90.1 | 0.394 | -0.073 | 0.221 | 1.294
Reading room 2 | 15.1 | 1.0404 | 13.13 | 107.8 | 0 | 0.53 | -0.041 | 1.938
study room | 9.52 | 0.6556 | 8.27 | 109.8 | 0.612 | 0.503 | 0.11 | 1.286
server | 0.48 | 0.0327 | 0.41 | 55.6 | 0 | 0.106 | 0.008 | 0.137
M.W.C | 0.54 | 0.0337 | 0.47 | 93.2 | 0 | 0.049 | -0.002 | 0.091
reading room | 29.54 | 2.0348 | 25.68 | 117.1 | 1.217 | 0.626 | 2.754 | 3.752
references hall | 13.41 | 0.9237 | 11.66 | 76.9 | 0.593 | 0.265 | 0.066 | 2.569
F.W.C | 0.82 | 0.0519 | 0.71 | 74.9 | 0 | -0.004 | -0.011 | 0.162
lobby | 21.82 | 1.3406 | 18.97 | 95.2 | 0.409 | -0.222 | -0.334 | 3.107
office | 1.39 | 0.096 | 1.21 | 79.7 | 0 | 0.281 | 0.026 | 0
computer lap | 21.7 | 1.4952 | 18.87 | 116 | 2.026 | -0.443 | -1.775 | 0.004
entrance 1 | 1.84 | 0.1215 | 1.6 | 68.4 | 0.118 | 0.099 | 0.017 | 0
police room | 2.3 | 0.1587 | 2 | 78 | 0.275 | -0.013 | -0.082 | 0.002
multipurpose hall | 18.3 | 1.2607 | 15.91 | 95.9 | 1.406 | 0.277 | 0.224 | 0.019
M.W.C | 0.38 | 0.0254 | 0.33 | 65.5 | 0 | 0.081 | 0.005 | 0
server | 0.57 | 0.0393 | 0.5 | 67.4 | 0 | 0.11 | 0.008 | 0
F.W.C | 0.61 | 0.0405 | 0.53 | 54.9 | 0 | 0.057 | 0.006 | 0
entrance hall | 4.68 | 0.3222 | 4.07 | 53.2 | 0.057 | 0.1 | 0.028 | 0
LOBBY | 12.33 | 0.7584 | 10.72 | 87 | 0.469 | -0.17 | -0.626 | 0.003
info desk | 2.61 | 0.1801 | 2.27 | 136.4 | 0.347 | -0.048 | 0.059 | 0.001
book repair | 2.44 | 0.168 | 2.12 | 95.9 | 0.121 | 0.228 | 0.028 | 0.002
lobby | 2.95 | 0.184 | 2.57 | 131.8 | 0.101 | 0.213 | 0.349 | 0.002
bookkeeper | 2.59 | 0.1787 | 2.26 | 114.7 | 0 | 0.356 | 0.028 | 0
receptions | 8.31 | 0.5724 | 7.23 | 67.3 | 0 | 0.422 | 0.135 | 0
references hall | 13.68 | 0.9425 | 11.9 | 71.6 | 0.759 | 0.455 | 0.358 | 0
reading room | 24.61 | 1.6954 | 21.4 | 98.6 | 1.882 | 0.572 | 3.605 | 0.016
Totals | 239.56 | 16.2159 | 208.32 | 93 | 12.718 | 3.961 | 3.451 | 16.651

## Slide 26
U value for Roof after adding insulation

## Slide 27
Heating and cooling capacity after adding a Roof and external wall insulation
Zone | Design Capacity (kW) | Design Capacity (W/m2)
first-floor heating load =47.56 |  | 
office 1 | 5.44 | 42.0627
secretary | 1.02 | 64.5172
Main office | 1.84 | 44.9809
documentation | 1.03 | 46.0947
meeting room | 4.62 | 45.8741
Reading room 2 | 7.44 | 53.1274
study room | 3.96 | 45.7272
server | 0.26 | 30.6886
M.W.C | 0.22 | 37.6683
reading room | 11.96 | 47.4086
references hall | 5.65 | 32.4208
F.W.C | 0.37 | 33.7327
lobby | 8.37 | 36.5278
ground floor heating load=47.26 |  | 
office | 0.58 | 33.301
computer lap | 9.13 | 48.8192
entrance 1 | 0.73 | 27.2864
police room | 0.98 | 33.1056
multipurpose hall | 8.91 | 46.6949
M.W.C | 0.16 | 27.7915
server | 0.22 | 25.9686
F.W.C | 0.29 | 26.4123
entrance hall | 2.07 | 23.5909
LOBBY | 4.51 | 31.8148
info desk | 0.95 | 49.6971
book repair | 1.05 | 41.3598
lobby | 0.95 | 42.5994
bookkeeper | 1.05 | 46.5595
receptions | 3.59 | 29.0423
references hall | 5.64 | 29.5169
reading room | 8.79 | 35.2223
total heating load =95.256 |  | 
Zone | Design Capacity (kW) | Design Flow Rate (m3/s) | Total Cooling Load (kW) | Design Cooling Load Per Floor Area(W/m2) | Glazing Gains (kW) | Wall Gains (kW) | Floor Gains (kW) | Roof and Ceiling Gains (kW)
office 1 | 10.44 | 0.7191 | 9.08 | 80.7 | 1.269 | -0.089 | -1.236 | 0.019
secretary | 1.6 | 0.1104 | 1.39 | 101.3 | 0.305 | -0.329 | -0.429 | -0.018
Main office | 2.83 | 0.1952 | 2.46 | 69.2 | 0.197 | 0.331 | 0.218 | 0.154
documentation | 1.77 | 0.1216 | 1.54 | 78.8 | 0.2 | 0.112 | 0.12 | 0.08
meeting room | 8.66 | 0.5968 | 7.53 | 86.1 | 0.4 | 0.288 | 0.436 | 0.355
Reading room 2 | 14.49 | 0.9984 | 12.6 | 103.4 | 0 | 0.919 | 0.328 | 0.65
study room | 8.98 | 0.6188 | 7.81 | 103.7 | 0.61 | 0.724 | 0.356 | 0.418
server | 0.43 | 0.0297 | 0.37 | 50.4 | 0 | 0.159 | 0.018 | 0.04
M.W.C | 0.5 | 0.0315 | 0.44 | 87.3 | 0 | 0.082 | 0.003 | 0.025
reading room | 28.59 | 1.9699 | 24.86 | 113.3 | 1.473 | 0.946 | 3.192 | 1.136
references hall | 12.29 | 0.8468 | 10.69 | 70.5 | 0.623 | 0.582 | 0.592 | 0.716
F.W.C | 0.77 | 0.0486 | 0.67 | 70.2 | 0 | 0.061 | 0.001 | 0.043
lobby | 20.25 | 1.24 | 17.61 | 88.4 | 0.406 | 0.411 | 0.142 | 0.733
office | 1.39 | 0.0955 | 1.21 | 79.4 | 0 | 0.277 | 0.025 | 0
computer lap | 21.65 | 1.4912 | 18.82 | 115.7 | 2.028 | -0.426 | -1.751 | 0.004
entrance 1 | 1.83 | 0.1213 | 1.59 | 68.3 | 0.117 | 0.097 | 0.016 | 0
police room | 2.3 | 0.1582 | 2 | 77.7 | 0.275 | -0.017 | -0.083 | 0.002
multipurpose hall | 18.23 | 1.2561 | 15.85 | 95.6 | 1.408 | 0.284 | 0.238 | 0.019
M.W.C | 0.38 | 0.0252 | 0.33 | 65 | 0 | 0.08 | 0.005 | 0
server | 0.57 | 0.039 | 0.49 | 66.8 | 0 | 0.107 | 0.008 | 0
F.W.C | 0.61 | 0.0403 | 0.53 | 54.6 | 0 | 0.055 | 0.006 | 0
entrance hall | 4.67 | 0.3219 | 4.06 | 53.1 | 0.056 | 0.099 | 0.027 | 0
LOBBY | 12.25 | 0.7533 | 10.65 | 86.4 | 0.467 | -0.148 | -0.611 | 0.003
info desk | 2.61 | 0.1796 | 2.27 | 136 | 0.347 | -0.056 | 0.056 | 0.001
book repair | 2.42 | 0.1669 | 2.11 | 95.3 | 0.121 | 0.228 | 0.029 | 0.002
lobby | 2.95 | 0.1835 | 2.56 | 131.4 | 0.101 | 0.21 | 0.347 | 0.002
bookkeeper | 2.58 | 0.1776 | 2.24 | 113.9 | 0 | 0.354 | 0.028 | 0
receptions | 8.22 | 0.5664 | 7.15 | 66.6 | 0.001 | 0.437 | 0.153 | 0
references hall | 13.56 | 0.9341 | 11.79 | 71 | 0.763 | 0.461 | 0.375 | 0
reading room | 24.55 | 1.6915 | 21.35 | 98.3 | 1.883 | 0.537 | 3.557 | 0.016
Totals | 232.37 | 15.7284 | 202.06 | 90.2 | 13.05 | 6.777 | 6.166 | 4.403

## Slide 28
Heating and cooling capacity after all treatments
Zone | Design Capacity (kW) | Design Capacity (W/m2)
first-floor heating load =33.600 |  | 
office 1 | 3.97 | 30.6691
secretary | 0.5 | 31.9093
Main office | 1.31 | 31.9097
documentation | 0.73 | 32.5363
meeting room | 3.15 | 31.3002
Reading room 2 | 4.78 | 34.1555
study room | 2.99 | 34.5164
server | 0.17 | 19.8961
M.W.C | 0.13 | 21.9144
reading room | 7.07 | 28.0106
references hall | 3.67 | 21.0486
F.W.C | 0.21 | 19.6739
lobby | 4.92 | 21.4688
ground floor heating load=33.290 |  | 
office | 0.39 | 22.1651
computer lap | 6.96 | 37.1985
entrance 1 | 0.44 | 16.4319
police room | 0.64 | 21.6476
multipurpose hall | 6.72 | 35.2483
M.W.C | 0.1 | 17.0038
server | 0.13 | 15.1669
F.W.C | 0.17 | 15.703
entrance hall | 1.13 | 12.8384
LOBBY | 2.5 | 17.6203
info desk | 0.7 | 36.5465
book repair | 0.71 | 27.8976
lobby | 0.55 | 24.5327
bookkeeper | 0.52 | 22.7888
receptions | 2.25 | 18.2454
references hall | 3.48 | 18.2442
reading room | 5.9 | 23.6303
total heating load =66.890 |  | 
Zone | Design Capacity (kW) | Design Flow Rate (m3/s) | Total Cooling Load (kW) | Design Cooling Load Per Floor Area(W/m2) | Glazing Gains (kW) | Wall Gains (kW) | Floor Gains (kW) | Roof and Ceiling Gains (kW)
office 1 | 7.15 | 0.4923 | 6.21 | 55.3 | 1.147 | 0.433 | 0.011 | 0.385
secretary | 0.95 | 0.0654 | 0.83 | 60 | 0.239 | 0.016 | -0.03 | 0.045
Main office | 2.05 | 0.141 | 1.78 | 50 | 0.22 | 0.349 | 0.141 | 0.166
documentation | 1.26 | 0.0868 | 1.1 | 56.2 | 0.226 | 0.14 | 0.084 | 0.087
meeting room | 6.34 | 0.4369 | 5.51 | 63 | 0.457 | 0.299 | 0.303 | 0.39
Reading room 2 | 10.11 | 0.6962 | 8.79 | 72.1 | 0 | 0.609 | 0.103 | 0.612
study room | 7.09 | 0.4666 | 6.16 | 79.25 | 0.658 | 0.576 | 0.009 | 0.37
server | 0.3 | 0.0209 | 0.26 | 35.5 | 0 | 0.157 | 0.014 | 0.046
M.W.C | 0.32 | 0.02 | 0.28 | 56 | 0 | 0.062 | 0 | 0.024
reading room | 16.93 | 1.1662 | 14.72 | 67.1 | 1.658 | 0.886 | 1.48 | 1.153
references hall | 9.25 | 0.6089 | 8.04 | 53.1 | 0.719 | 0.404 | 0.261 | 0.701
F.W.C | 0.51 | 0.0316 | 0.45 | 46.9 | 0 | 0.042 | -0.002 | 0.043
lobby | 12.73 | 0.7638 | 11.07 | 55.6 | 0.308 | 0.528 | 0.221 | 0.857
office | 0.95 | 0.0657 | 0.83 | 54.6 | 0 | 0.202 | 0.016 | 0
computer lap | 16.48 | 1.1354 | 14.33 | 79.125 | 1.999 | 0.062 | -0.367 | 0.002
entrance 1 | 1.31 | 0.0788 | 1.14 | 48.9 | 0.085 | 0.075 | 0.009 | 0
police room | 1.54 | 0.106 | 1.34 | 52.1 | 0.286 | 0.046 | -0.019 | 0.002
multipurpose hall | 13.64 | 0.9395 | 11.86 | 71.5 | 1.574 | 0.365 | 0.225 | 0.008
M.W.C | 0.28 | 0.0175 | 0.25 | 48.8 | 0 | 0.046 | 0.002 | 0
server | 0.4 | 0.0278 | 0.35 | 47.5 | 0 | 0.051 | 0.002 | 0
F.W.C | 0.46 | 0.0283 | 0.4 | 41.6 | 0 | 0.026 | 0.002 | 0
entrance hall | 3.07 | 0.1907 | 2.67 | 34.9 | 0.035 | 0.08 | 0.013 | 0
LOBBY | 7.13 | 0.4252 | 6.2 | 50.3 | 0.353 | 0.127 | -0.074 | 0.001
info desk | 1.52 | 0.1047 | 1.32 | 79.3 | 0.403 | 0.139 | 0.033 | 0.003
book repair | 1.56 | 0.1077 | 1.36 | 61.4 | 0.134 | 0.19 | 0.024 | 0.001
lobby | 1.35 | 0.0889 | 1.18 | 60.5 | 0.13 | 0.199 | 0.065 | 0.001
bookkeeper | 1.33 | 0.0913 | 1.15 | 58.6 | 0 | 0.268 | 0.029 | 0
receptions | 5.57 | 0.3838 | 4.84 | 45.1 | 0 | 0.3 | 0.114 | 0
references hall | 9.36 | 0.6149 | 8.14 | 49 | 0.826 | 0.359 | 0.301 | 0
reading room | 15.97 | 1.1001 | 13.89 | 64 | 2.129 | 0.659 | 1.395 | 0.011
Totals | 156.92 | 10.5028 | 136.45 | 60.9 | 13.587 | 7.694 | 4.368 | 4.908

## Slide 29
Thermal comfort
The total site energy is=78.62 kwh/m2
PMV between (-0.7-0.7)

## Slide 30
Energy baseline analysis for building

## Slide 31
CFD analysis
Internal CFD
External CFD

## Slide 32
Photovoltaic design

## Slide 33: Structural Aspects

## Slide 34: Center of columns

## Slide 35: 3D Modeling of Al-Istiqlal University Library Design codes are ACI 319, ASCE, UBC-97. The slab system is a Two-way Ribbed Slab. Subjected loads are as follows: Live load =5 kN/m² SID = 4.47 kN/m² Bearing capacity =200 KN/m² Materials used: f’c concrete for (columns + footing + two way ribbed slab ) f'c=28 Mpa. Steel fy=420 Mpa.

## Slide 36: Computability Check
All elements within each area seamlessly integrate, ensuring the absence of any instabilities present in the overall structure

## Slide 37: Equilibrium Check (part one )
Load | From Etabs | By hand | Error %
Dead load | 21133.27 | 21020.32 | 0.53
Live load | 11872.185 | 12027.35 | 0.72
Super dead load |  | 13145.8289 | 0.83
Load | From Etabs | By hand | Error %
Dead load | 21133.27 | 21020.32 | 0.53
Live load | 11872.185 | 12027.35 | 0.72
Super dead load |  | 13145.8289 | 0.83
Equilibrium Check (part two )
Load | From Etabs | By hand | Error %
Dead load | 27761.337 | 27001.25 | 2.81
Live load | 14395.23 | 14395.5 | 0.00187
Super dead load |  | 15393.5 | 0.25
Load | From Etabs | By hand | Error %
Dead load | 27761.337 | 27001.25 | 2.81
Live load | 14395.23 | 14395.5 | 0.00187
Super dead load |  | 15393.5 | 0.25

## Slide 38: Internal force
Element | From Etabs | BY hand | Error %
Beam | 1583 | 1505 | 5.1%
Column (0.4*1.2) | 28 | 7399.64 | 0.17%
Element | From Etabs | BY hand | Error %
Beam | 1583 | 1505 | 5.1%
Column (0.4*1.2) |  | 7399.64 | 0.17%

## Slide 39: Seismic design Checks

## Slide 40: T-Period check
  T method A = Ct*(height of building) 3/4
  Then the maximum allowed limit is (1.4* T method A =0.552)
  T period from Etabs =0.544  1.4 method A=0.552  OK
Part one
Part two
  T method A = Ct*(height of building) 3/4
  Then the maximum allowed limit is (1.4* T method A =0.582)
  T period from Etabs =0.37  1.4 method A=0.582  OK

## Slide 41: Model Mass Participation Ratio
Part one
Part two
Sum Ux and Uy 0.9  ok
Sum Ux and Uy 0.9  ok

## Slide 42: Base shear check
Part one
Part two
In this check the base shear of EQx or EQy from response spectrum (ETABS) must be bigger than base shear from the equivalent static(Manual).

## Slide 43: Drift check
Part one
Part two
story | height | DIS X | DIS Y | DRIFT X | DRIFT Y | Delta X | Delta Y | Limitation
base | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
basement | 2550 | 1.35 | 0.52 | 1.35 | 0.52 | 5.197 | 2.002 | 63.75
ground | 4420 | 11.159 | 3.74 | 9.809 | 3.22 | 37.76 | 12.4 | 101.75
first | 4420 | 20.265 | 6.994 | 9.106 | 3.254 | 35.058 | 12.52 | 101.75
story | height | DIS X | DIS Y | DRIFT X | DRIFT Y | Delta X | Delta Y | Limitation
base | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
basement | 2550 | 1.215 | 0.321 | 1.215 | 0.321 | 4.677 | 1.235 | 63.75
ground | 4420 | 4.938 | 1.001 | 3.723 | 0.68 | 14.33 | 2.618 | 101.75
first | 4420 | 9.221 | 1.766 | 4.282 | 0.765 | 16.48 | 2.94 | 101.75
staircase | 2900 | 3.392 | -0.466 | -5.829 | -0.093 | -22.44 | -1.79 | 72.5

## Slide 44: Mat foundation
Section

## Slide 45: Water tank
Section

## Slide 46: Column
column | dimension | reinforced | ties | # of the column in two parts
C1 | 110*40 | 16ø18 | 2ø10 | 1
C2 | 100*40 | 14ø18 | 2ø10 | 8
C3 | 120*40 | 18ø18 | 3ø10 | 18

## Slide 47: Shear wall
Part one
Part two

## Slide 48: Beams

## Slide 49: Basement slab

## Slide 50: Ground floor slab

## Slide 51: First floor slab

## Slide 52: Electromechanical Aspects

## Slide 53: Electromechanical Aspects
01
Artificial Lighting
02
Power
03
HVAC
04
Fire
05
Water supply
06
Drainage
07
Acoustics

## Slide 54: Artificial Lighting
Standard Illuminance (Lux), CCT, CRI and UGR for space
Room type | Lux recommendation | UGR | CCT | CRI
reading room | 500 | 19 | 4000 | 80
reference hall | 200 | 19 | 4000 | 80
multipurpose hall | 500 | 19 | 4000 | 80
toilet | 200 | 22 | 4000 | 90
reception area | 300 | 22 | 4000 | 80
parking | 100 | 25 | 4000 | 80
Office | 300 | 19 | 4000 | 80
lobby | 100 | 25 | 4000 | 80

## Slide 55: Artificial Lighting
Office

## Slide 56: Artificial Lighting
Space | E(lux) | UO | UGR
Office | 312 | 0.58 | 17
Computer lab | 304 | 0.57 | 20
Reading hall | 552 | 0.58 | 20
Reference hall | 204 | 0.5 | 22
Multiparous hall | 515 | 0.47 | 15
lobby | 121 | 0.5 | 21
W.C | 205 | 0.52 | 15
Storage | 204 | 0.52 | 19

## Slide 57: Artificial Lighting
Basement floor

## Slide 58: Artificial Lighting
ground floor

## Slide 59: Artificial Lighting
first floor

## Slide 60: power
Basement floor

## Slide 61: power
ground floor

## Slide 62: power
first floor

## Slide 63: power
main distribution board

## Slide 64: HVAC design
The system that was used is a VRF system.

## Slide 65: HVAC design
The design capacity = 156.92 KW
Outdoor unit:

## Slide 66: HVAC design
Outdoor unit:

## Slide 67: HVAC design
Fan coil unit

## Slide 68: HVAC design
Diffuser selection

## Slide 69: HVAC
ground floor

## Slide 70: HVAC
first floor

## Slide 71: HVAC

## Slide 72: Fire fighting design

## Slide 73: Fire fighting design
Basement floor

## Slide 74: Fire fighting design
ground floor

## Slide 75: Fire fighting design
first floor

## Slide 76: Fire fighting design
ground floor

## Slide 77: Fire fighting design
first floor

## Slide 78: Fire fighting design

## Slide 79: Integration(lighting, HVAC ,Fire)
Basement floor

## Slide 80: Integration(lighting, HVAC ,Fire)
ground floor

## Slide 81: Integration(lighting, HVAC ,Fire)
first floor

## Slide 82: Acoustical design

## Slide 83: Acoustical design
Space | Reverberation time 60
Meeting room | 0.5-1.0
Reading hall | 0.4-1.2
Multipurpose hall | 0.6-1.5

## Slide 84: Acoustical design
Reverberation Time RT60 (Sec) | 125Hz | 250Hz | 500Hz | 1000Hz | 2000Hz | 4000Hz
 | 0.9 | 0.66 | 0.68 | 0.59 | 0.70 | 0.87
(0.5-1.0) | good | good | good | good | good | good
When 100% occupancy :
When 0% occupancy :
Reverberation Time RT60 (Sec) | 125Hz | 250Hz | 500Hz | 1000Hz | 2000Hz | 4000Hz
 | 1.0 | 0.76 | 0.68 | 0.70 | 0.86 | 1.01
(0.5-1.0) | good | good | good | good | good | good
Reverberation time (RT60) For Meeting room :

## Slide 85: Acoustical design
Material used :
50 mm (2 inches) thick Mineral Wool

## Slide 86: Acoustical design
Sound power level (SPL) For Multi-purpose hall :

## Slide 87: Acoustical design
When 100% occupancy :
Sound power level (SPL) For Multi-purpose hall :
Point | SPL125Hz | SPL250Hz | SPL500Hz | SPL1000Hz | SPL2000Hz | SPL4000Hz
1 | 74.64 | 75.05 | 75.70 | 75.02 | 75.37 | 75.85
2 | 72.74 | 73.37 | 74.29 | 73.32 | 73.83 | 74.50
3 | 72.34 | 73.02 | 74.01 | 72.97 | 73.52 | 74.24
4 | 72.16 | 72.87 | 73.89 | 72.82 | 73.38 | 74.12
5 | 71.93 | 72.67 | 73.73 | 72.62 | 73.21 | 73.97
6 | 71.64 | 72.43 | 73.55 | 72.37 | 73.00 | 73.80
7 | 71.55 | 72.35 | 73.49 | 72.30 | 72.93 | 73.74
8 | 71.49 | 72.30 | 73.45 | 72.24 | 72.89 | 73.70
9 | 71.47 | 72.29 | 73.44 | 72.23 | 72.87 | 73.69
10 | 71.44 | 72.26 | 73.42 | 72.21 | 72.85 | 73.68

## Slide 88: Acoustical design
When 0% occupancy :
Sound power level (SPL) For Multi-purpose hall :
Point | SPL125Hz | SPL250Hz | SPL500Hz | SPL1000Hz | SPL2000Hz | SPL4000Hz
1 | 74.96 | 75.51 | 75.70 | 75.62 | 76.17 | 76.98
2 | 73.23 | 74.03 | 74.29 | 74.18 | 74.93 | 75.97
3 | 72.87 | 73.73 | 74.01 | 73.89 | 74.69 | 75.79
4 | 72.71 | 73.60 | 73.89 | 73.77 | 74.58 | 75.70
5 | 72.51 | 73.44 | 73.73 | 73.61 | 74.45 | 75.60
6 | 72.26 | 73.24 | 73.55 | 73.42 | 74.29 | 75.48
7 | 72.18 | 73.17 | 73.49 | 73.35 | 74.24 | 75.44
8 | 72.12 | 73.13 | 73.45 | 73.31 | 74.21 | 75.42
9 | 72.11 | 73.12 | 73.44 | 73.30 | 74.20 | 75.41
10 | 72.09 | 73.10 | 73.42 | 73.28 | 74.18 | 75.40

## Slide 89: Acoustical design
Number of Speakers used for the hall is speakers.

## Slide 90: Water supply system
Underground tank
capacity of 35 m3.

## Slide 91: Water supply system
Roof Tanks
Water consumption is 33600 liters per day.
Tanks dimension is 1.6 * 2 m
7 Tanks used

## Slide 92: Water supply system
For Ground Floor

## Slide 93: Water supply system
For First Floor

## Slide 94: Water supply system
Roof Tanks

## Slide 95: Water supply system

## Slide 96: Water drainage system

## Slide 97: Water drainage system
For Parking

## Slide 98: Water drainage system
Slope | Max DFU | Inch
2% | 21 | 2
1% | 180 | 4
1% | 700 | 6
For Ground Floor

## Slide 99: Water drainage system
Slope | Max DFU | Inch
2% | 21 | 2
1% | 180 | 4
1% | 700 | 6
For First Floor

## Slide 100: Water drainage system
Slope | Max DFU | Inch
2% | 21 | 2
1% | 180 | 4
1% | 700 | 6
For Site Plan
Manhole in site plan

## Slide 101: Water drainage system
For Rainwater

## Slide 102: Quantity surveying & cost estimate
ILS | 131,498.4 | Earthwork | 1
ILS | 3,988,718.5 | Structural elements | 2
ILS | 858,365.0 | External works elements | 3
ILS | 291,476.4 | Interior walls | 4
ILS | 2,905,368.2 | Finishes | 5
ILS | 336,796.4 | Electrical work | 6
ILS | 1,708,565.1 | Mechanical work | 7
ILS | 11,818,299.1 | Total Project Cost | 8
Unit cost per m =2007.6 M2/ILS