An Najah National University

Faculty of Engineering & Information Technology

Energy Efficiency Opportunities at 
Al-Amour steel tubes and profiles industry

Prepared by

Ghassan Sakhel

Hamza Mohsen

Yousef Ishtewe

Supervisor

Dr. Aysar Yasin

This project is Submitted in Partial fulfillment of the Requirments for the Bachelor Degree on Energy Engineering and Environment Department, Faculty of Engineering and Information Technology, An-Najah Naional University, Nablus – Palestine.

May, 2017

Acknowledgment

We would like to thank our supervisor, Dr. Aysar Yasin, for his guidance, encouragements and support to complete this project.

Our sincere gratitude to AL Amour industry for helping us with the project, and our deep thanks to Eng. Yousef al amour for coordinate our visit to the industry and Eng. Majde jabr and Eng. Osama alqm for helping us collecting the required measurements.

Table of Contents

Abstract	viii

Chapter 1 Introduction	1-1

1.1: Overview	1-2

1.2: Problem statement	1-2

1.3: Project objectives and motivations	1-3

1.4: Scope of the work	1-3

1.5: Research questions	1-3

1.6: Hypothesis	1-4

1.7: Organization of the report	1-4

Chapter 2 Al-Amour Industry	2-5

Chapter 3 Constraints, Standard and Earlier Course Work	3-13

3.1: Constraints	3-14

3.2: Standards	3-15

3.3: Earlier coursework	3-16

Chapter 4 Methodology	4-18

Chapter 5 Literature Review	5-22

Chapter 6 Theoretical Background	6-26

6.1: Electrical motors	6-27

6.2: Lighting system	6-33

6.3: Compressed air system	6-36

6.4: High frequency welding	6-39

Chapter 7 Collected Data and Analysis of Energy Performance	7-40

7.1: Electric motor	7-44

7.2: Lighting system	7-48

7.3: Compressed air system	7-50

7.4: High frequency welding	7-51

7.5: Evaluation of the overall energy consumption	7-51

Chapter 8 Energy Conservation Opportunities and Economic Evaluation	8-52

8.1: Electrical motors	8-53

8.2: Lighting system	8-56

8.2.1 Energy conservation opportunities	8-56

8.3: Compressed air system	8-57

8.3.1 Energy opportunities	8-57

8.3.2 Economic analysis	8-57

8.4: High frequency welding	8-58

8.5: Evaluation of the overall energy saving opportunities	8-59

8.6: Greenhouse gases impact	8-60

Chapter 9 Conclusion and Recommendations	9-61

References	9-64

Appendices	67

Appendix 1: Electrical bill of the steel tubes and profile factory	67

Appendix 2: Used standards	68

Appendix 3: Name Plate data for the electrical motor	72

Appendix 4: Clamp meter measurements	73

Appendix 5: Power analyser measurements	74

Appendix 6: Toshiba- high efficiency motor catalogue	108

List of Figure

Figure 2-1: Layout of slitting line. (kcico, 2010)	2-9

Figure 2-2: Layout of mild steel welded tube line. (RLT Group, 2010)	2-10

Figure 2-3: high frequency induction welding process	2-11

Figure 4-1: methodology procedure	4-19

Figure 6-1: Typical motor Efficiency vs. Load factor (Natural Resources Canada, 2015)	6-30

Figure 6-2:Standard motors vs high efficiency motors	6-32

Figure 7-1: Clamp Meter device (PCE Instruments, 2016)	7-41

Figure 7-2: Light Meter Device (Magnaflux , 2010)	7-42

Figure 7-3: Thermo Meter Device (zytemp, 2014)	7-42

Figure 7-4: Power Analyzer Device (PCE Instruments, 2016)	7-43

Figure 7-5: power star hqi-t/ metal halide lamp	7-49

Figure 7-6: energy consumption percentage	7-51

Figure 8-1: load factor improvement	8-54

Figure 8-2: comparison of the annual cost between the current motors and suggested replacement	8-54

Figure 8-3: monthly electric bill for the factory	8-59

List of Tables

Table 2-1: The Round Pipes Dimension	2-7

Table 2-2: Square and Rectangular Tubes Dimension	2-7

Table 7-1: A sample of the name plate reading of the electric motor.	7-44

Table 7-2: A sample of measured data using clamp meters.	7-45

Table 7-3: load factor and efficiency of the electric motor	7-47

Table 7-4: measured illumination levels	7-48

Table 7-5: lamp data sheet	7-49

Table 7-6: measured data from the compressor	7-50

Table 8-1: rated power and efficiency for current and suggested motors	8-53

Table 8-2: saving by replace the electric motors with high efficiency motors	8-55

Table A-1: electrical bill of the factory	67

Table A-2: standard illumination levels	68

Table A-3: standard rated efficiency for the electrical motor	70

Table A-4: Name Plate data of the electrical motors	72

Table A-5: clamp Meter Measurement	73

Table A-6: power analyser measurements for motor A/2PL	74

Table A-7: power analyser measurements for motor B/2L	82

Table A-8: Power analyser measurements for the air compressor	90

Table A-9: power analyser measurements for the HF welding	101

Table A-10: catalogue of the suggested motor	108

List of Equation

Equation 1:motor power consumption	6-28

Equation 2:motor energy consumption	6-29

Equation 3:power Factor	6-29

Equation 4:load factor	6-29

Equation 5:motor efficiency	6-30

Equation 6: saving on motor, using load shedding	6-31

Equation 7: power factor correction	6-31

Equation 8: saving from installing energy efficient motors	6-32

Equation 9: lighting system energy consumption	6-33

Equation 10: lamp saving, unnecessary lamp	6-34

Equation 11:the optimum number of fixtures	6-34

Equation 12: cost, spot re-lamping	6-35

Equation 13: cost, group re-lamping	6-35

Equation 14: saving, high efficient lamps	6-35

Equation 15: power consumption in compressor	6-36

Equation 16:energy consumption, compressor	6-36

Equation 17:the additional power for the coverage of the wasted energy	6-37

Equation 18:leakage percentage	6-37

Equation 19:power reduction caused by decreasing inlet temperature	6-38

Equation 20: energy consumption, HF welding	6-39

Equation 21: EUI, HF welding	6-39

# Abstract

The high-energy bills and fuel requirements have always been a major concern for every organization. Demand on energy is continuously increasing while resources are limited. In order to overcome this problem energy management has to be applied. This report is an energy audit at Al-Amour steel tubes and profiles factory, Bedya, Palestine, which has a good potential for energy efficiency practices. The report aims to obtain an overview of the existing energy consumption and analyse energy efficiency opportunities to minimize energy bill by reducing consumption and maximize efficiency of the production lines. The factory has two main production lines, which mainly consist of electric motor, compressed air system high frequency welding and lighting system, the audit was conducted through various steps. First of all is visiting the factory to find out the used equipment and takes an overview of the production lines, through meeting the manager, engineers and employees, after that the main reading of the electric motor and lighting system were taken and tabulated, to analyse the energy performance and energy conservation opportunities. It was found that the annual energy consumption was 353,162 kWh/year. Where electric motors consume 48%, HF welding 45%, compressor 6.5% and the lighting less than 0.5% of the total consumption. The main energy conservation opportunities were to replace some of the existing motors with high efficient motors and to fix the leakage on the pipeline of the compressed air system. The total estimated saving was about 7.85% of the total consumption.

# Introduction

## Overview

Since the first oil crises in the 1970s, the word start investigates in an alternating source of energy. Renewable energy was used since Palaeolithic times such as Geothermal energy for heating. The most important features of renewable energy are low running cost like photovoltaic cells and hydro power. On the other hand, it has high initial investment and a big number of limitations. All of that limitations leaded to energy management solution.

After the crises of petrol happened, some energy engineers start looking for many solutions such as energy saving, but it was the beginning, because that period of time saws up and down in the energy management. Late 80’s, the impact of the Natural Gas Policy Act began to be felt so energy managers found they could sometimes save significant amounts of money by buying “spot market” natural gas and arranging transportation. About the only thing that could be done in purchasing electricity was to choose the appropriate rate schedule and optimize parameters such as power factor, demand, ratchet clauses, time of use. With the arrival of the Energy Policy Act of 1992, electricity deregulation moved closer to reality, creating the opportunity of purchasing electricity from wherever the best deal could be found and to wheel the electric energy through the grid.

## Problem statement

Palestine is considered as one of the poorest countries considering the usage of energy resources. Nearly all main energy resources like fossil fuels and electricity are imported from Israel. This makes Israeli control the quantity, price, tariff, condition and form of each source of energy to Palestine.

The direction towards getting use from renewable energy sources such as solar and photovoltaic energy from sun was a competitive and good option to Palestinians; especially Palestine has been gifted with huge solar radiation. This type of renewable energy was excellently utilized in water heating, but without clear feasibility to use it in utilizing electricity because of the high cost of photovoltaic system.

The industrial sector is one of the main energy consuming sectors in Palestine that suffers from incredible energy consumption and bad management.

The proceeding toward reducing energy consumption in all energy consuming sectors is considered one of the quickest and feasible measure to bring down and reduce the problem of energy and reduction in environmental emissions in Palestine.

## Project objectives and motivations

- Improving the performance of the production line: Becoming economically competitive in the global marketplace, which requires reducing the cost of production or services, reducing industrial energy intensiveness, and meeting customer service needs for quality and delivery times.

- Rising the efficiency of the motors: energy management makes the most of motors work on the rated load and that increase the efficiency of that motors.

- Increase the power factor of the factory: the energy management depends on capacitor installation, which rise the power factor so that the real power decrease.

- Reduce the environment impacts: energy management reduces the load on power plants as fewer kilowatt hours of electricity are needed. If a plant burns coal or fuel oil, then a significant amount of acid rain is produced from the Sulphur dioxide emitted by the power plant. Acid rain problems then are reduced through energy management, as are NOx problems.

- Reduce the bill of the factory: increasing the efficiency of the motors and the power factor will make a reduction in the electricity bills.

## Scope of the work

The project was done on the second building of the industry that produce profile and metal pipes, the energy performance analysis was done on the main energy consumption in the factory were electric motor, a compressed air system, high frequency welding and lighting system. And applying energy efficiency methods for the production lines, and find energy efficiency opportunities and give the appropriate recommendation.

## Research questions

The idea of the project starts from answering such questions that is followed:

Does Al-Amour factory have a high-energy consumption?

Where does most of the energy consumed?

Is it consumed by the bad behaviour of the workers?

Does the motors are properly selected?

Does the industry suffer from low power factor?

Does the lighting quality is satisfied?

Does the air compressor has air leakage?

## Hypothesis

It is hypothesized that the most of energy consumption has consumed by the motors.

It is hypothesized that the motors load factor is less than 50%.

It is hypothesized that power factor is less than 90%.

It is hypothesized that the quality of lighting in the industry is not accepted according to the standards.

It is hypothesised that following energy management measures in the industry reduces the energy consumption to more than 85%.

## Organization of the report

This report was organized as following:

- Chapter one: is an introduction to energy management and the project.

- Chapter two: is an introduction to AL-Amour industry

- Chapter three: Constraints, Standard and Earlier Course Work, this chapter views the main difficulties that the auditing team face, used standards and earlier courses that help the making of this project.

- Chapter four: Research methodology, this chapter views the methodology that the auditor had used to collect and analysed the final results.

- Chapter five: Literature Review, the chapter review previous studies from different sources.

- Chapter six: Theoretical Background, this chapter views the theoretical aspect and equation that will be used in the analyses of the energy efficiency opportunities.

- Chapter seven: Collected Data and Analysis of Energy Performance, the chapter reviews the devices that bean used to measure the required data along with soma tabulated measurements. And evaluate the energy performance indicator

- Chapter eight: Energy Conservation Opportunities and Economic Evaluation, the chapter analyse the energy conservation opportunities for the different system in the factory and evaluate the economic analysis.

# Al-Amour Industry

Al-Amour Industrial and Trading (AIT) company was founded in 1999. Located at Bedya, Salfit. It has two building the first one with its area of 3000 m2 and the second building is Steel Tubes and Profiles established in 2014 with one single floor and area 4000 m2, the total area of the Factory is about 7000 m2. (Alamour Industrial And Trading, 2016 )

The factory includes three main division illustrated below:

- Trading division: metals and steel trading, gypsum boards and accessories and timber and roof tiles.

- Manufacturing division: steel structures, agriculture water tanks, prefabricated offices and units and light weight houses.

- Production division: galvanized roll forming, steel tubes and profiles, corrugated sheets, fencing works and barbed wires, sandwich panels. (Alamour Industrial And Trading , 2016)

This project will take a case study in the steel tube and profile factory, it’s a separately part of the industry, the factory was chosen because of the high-energy consumption and to give the audit team good opportunity to focus on one main factory as a case study. The main two product of the factory is steel tube and profiles with different diameters, the raw material of the factory is a roll of steel with total length of over a 1200 meter and different width and diameter. The factory has two production lines, the first line cuts the steel roll to 4-5 thinner rolls, the second line use the thinner roll from the first line to form the steel tube and profile. Each line has eight electric motor, the second line has a cooling tower to control the temperature of the main electrical board.

Steel tubes and profiles production:

AIT don’t only provide specialty materials with easy welding and forming characteristics, but also provide its customers with additional services such as production of pipes and profiles to a certain length beyond the standard.

Round Pipes:

AIT manufactures a wide range of hot rolled steel (HR- Black), Galvanized (GI) and Cold rolled steel (CR) pipes. Pipes are cold rolled to the required diameters and thicknesses then welded along their length, the pipes are manufactured using carbon steel in accordance with the Standard EN10025. Table 2-1 shows the round pipes dimensions.

Table 2-1: The Round Pipes Dimension

| Pipe Diameters: | 16 mm – 2.5 mm |
| --- | --- |
| Wall Thickness: | 1.0 mm – 3.5 mm |
| Pipe Lengths: | Standard lengths in stock are 6 and 12 meters (any length up to 12.3 m can be ordered). |

Oval pipes and any special type of pipe required by the customer, custom tailored to the customer’s needs.

Square and Rectangular Tubes:

AIT manufactures a very broad range of square and rectangular steel tubes. Tubes category:

Hot Rolled Steel (HR- Black)

Galvanized (GI)

Cold Rolled Steel (CR)

Square tubes are cold rolled then welded along their length, the profiles are manufactured using carbon steel in accordance with the Standard EN10025. Table 2 shows the round pipes dimensions

Table 2-2: Square and Rectangular Tubes Dimension

| Pipe Diameters: | 15x15 mm to 60x60 mm 30x20 mm to 80x40 mm |
| --- | --- |
| Wall Thickness: | 1.0 mm – 3.0 mm |
| Pipe Lengths: | Standard lengths of 6m and 12m (different lengths at the customer’s request up to 12 meters can be ordered). |

AIT pipes, tubes and profiles can be used in industry, agriculture, fencing, construction, lighting poles, traffic light poles, furniture and more. (Alamour Industrial And Trading, 2016)

AIT industry got a certificate of quality management (ISO 9001: 2000 / IWA1)/

Process Manufacture:

In this section, we will explain the process manufacturing in Al-Amour steel tubes and profiles factory which has two production line the first one is Slitting Line and the second line is mild steel welded tube line.

- Slitting line:

Slitting is a shearing process in which the width of an original steel coil is reduced into multiple narrower steel rolls, called strips these strips recoiled to be use in the second production line, the outside edges of the original coil are trimmed this creates an accurate register cut. In this production line, there 2 or 3 workers.

Slitting lines which consist of four basic devices:

- The Uncoiler: which tightly grips the original steel coil on its inside diameter using an expandable mandrel. The coil is fed into the slitter by rotating the mandrel by using hydraulic system and motors, the motors will be refereed later on the report as no. 1 and 2 these two-motor works less than one minutes in every slitting process.

- The Slitter: which consists multiple cutting knives. These knives partially penetrate the original steel sheet causing a fracture then slit the steel sheet and separating it to narrower steel sheets. The outside edges of the original coil are trimmed by cutting knives and recoiled by using tow motors the motors will be refereed later on the report as no. 3 and 4.

- A Tensioning device: which is placed between the Slitter and the subsequent Recoiler. A tensioning device is needed to pass the steel sheets through the cutting knives, the motor will be referred as no. “B”. the motor has an external fan and will be referred to as fan 2

- The Recoiler: which takes up the slit coils on a driven and recoiled to be use in the second production line, the motor will be referred as no. “A”. the motor has an external fan and will be referred to as fan 1.

Figure 2-1: Layout of slitting line. (kcico, 2010)

- Mild steel welded tube line:

A mild steel welded tube line typically consists of the following equipment:

- Uncoiler: The Uncoiler pays strip out to the line. The typical Uncoiler has two arms so that a second coil can be readied while the first is being run.

- Shear/End Welder: The end welder is key to producing continuous tube. Its function is to shear the trailing edge of the first coil and the leading edge of the next coil, then weld the two together so that the strip can be fed continuously through the mill.

- Strip Accumulator: Strip must be stored so that the mill will have an ample supply while the end weld is being completed. The way used to store strip are the horizontal accumulators to create a storage bank of strip in the form of a large coil by using motors the motors will be refereed later on the report as no. 1 and 2, which the mill then depletes during the end welding process.

- Forming/Welding Mill: It consists of vertical and horizontal passes that form the strip into an open tube there is many driven vertical stands. They break the edge of the strip and form it into an initial U shape then to make it to tube profile by pulled the strip through the vertical stands by using motor the motor will be refereed later on the report as no. “B”. The weld area forges the strip into a closed tube and then removes the bead created during the weld. We will explain this in detail later.

- Sizing Mill: Once the tube is pulled by using motor the motors will be refereed later on the report as no. “A” then formed and cooled, the sizing section brings it to its final diameter. Also, if the tube is to be reshaped, that is accomplished here.

- Cutoff System: A typical cutoff system used is the double-cut flying shear by using motor the motor will be refereed later on the report as no. “C” The press receives a signal from a length encoder mounted at the end of the mill. The encoder signals the die set to accelerate to the speed of the tube. The die set powered by a direct current (DC) motor.

Figure 2-2: Layout of mild steel welded tube line. (RLT Group, 2010)

Welding Process:

Principals of HF welding process operation:

Induction welding is a form of Electrical Resistance Welding (ERW) in which the large rotary transformer common in low frequency ERW is replaced by a “virtual transformer” consisting of the work coil (primary winding) and the tube itself (secondary winding). A ferromagnetic core inside the tube has a similar role to the laminated iron core in a conventional transformer.

Figure 2-3: high frequency induction welding process

Current flowing in the coil causes a magnetic field to develop surrounding the coil, part of which intersects with the open tube. This causes an electric field on the outer surface of the tube which in turn creates a voltage difference across the edges of the strip. At the frequencies used for induction welding, the interaction between electric and magnetic fields can cause currents to flow in unexpected ways. The “skin effect” confines current to within a few thousandths of an inch of the surface, so the voltage across the strip edges tends to cause current to flow circumferentially around the inside surface of the tube in the opposite direction to the induced current on the outside

surface.

An impeder is simply a bar of ferromagnetic material placed inside the tube within the weld area. Such materials have the effect of raising the inductance of a circuit surrounding them. The resistance of the inside surface of the tube is extremely low but at high frequencies, it is inductance (or more specifically inductive reactance) that is the primary factor in determining current flow. The sum of reactance and resistance is known as impedance.  (WRIGHT, 2008)

# Constraints, Standard and Earlier Course Work

## Constraints

The difficulties, which had faced the team up to now in the project, are illustrated below

- Lack of data: One of the most important challenges that faced the team in this project is the lack of data and experience related in Energy Management here in Palestine, there is no data related in energy consumptions in the Palestinian factories so there is no reference data for initial compering between the factories in energy consumption in Palestine this is mainly because it’s a new strategy here.

- Absence of energy policy: One of the most important challenges that were faced in this project is the absence of energy policies generally, there is no electrical design plans for the electrical device connections in the factory especially the motors connections and no electrical and energy engineers are specialized in the factory and that was a non-negligible obstacle.

- Obstacles in data measurement: As for obstacles facing us in the process of recording data, we were unable to expand the recording process to some motors, as doing so necessarily requires a total shut-down of the production line and disassembling certain production lines and recording data related to them.

- Time: As with any graduation project, time factor is a very important and sensitive issue, time of delivering the project was limited. The nature of the work required visiting the factory several times in order to verify the mechanism of work in the upcoming implementation steps. This has consumed too much time especially in selecting relevant meetings dates because the factory electrical engineer wasn’t available all the time in the factory it was called when there is a problem in the factory so the meetings was depending on the electrical engineer because he is the only person who can understanding the connections of the motors and the only person has the authorities to open the main electrical distributions in the factory. As well as selecting relevant meetings with the factory, where it worked coincides with the university working hours except on Saturday, which was the only suitable dates for the team and the factory managers and the electrical engineer.

- Lack of documentations: One of the most difficult problems we encountered in the second stage of the project is documentations of data for the machines and its catalogues, to understand the behaviour of the machines, although it is one of the most important data necessary to rationalize energy consumption and help the energy audit to find solutions for high energy consumption problem.

## Standards

- Electrical Motor

The motors used in Al-Amour factory manufactured in China and must be certified and registered by the Label office and provided with an energy label confirming that they meet certain efficiency standards. The energy label must be attached to the motor itself or to the packing immediately around it. It must show the following information:

− Name of the manufacturer.

− Energy efficiency level of the motor.

− Code identifying the National Standard applied.

To qualify for the China Energy Label, motors must meet the requirements specified in Chinese National Standard “GB 18613-2012”. This standard, which was issued by the General Administration of Quality Supervision, Inspection and Quarantine of the People’s Republic of China, specifies the minimum allowable energy efficiency values, and energy efficiency grades for small and medium sized three-phase induction and asynchronous motors. Motor efficiency must be equal to or better than the specified value at 100% of the rated output power. Efficiency is measured in accordance with Standard GB/T1032, which is identical to “IEC 60034-2-1” and the grades are in line with the classes in “IEC/EN 60034-30”.

Standard “GB 18613-2012” specifies three different energy efficiency levels, Grades 1-3, where Grade 1 represents best-in-class performance. Energy efficiencies of motors shall fall into 3 grades, among which the grade 1 claims the highest energy efficiency. The measured efficiency of differently graded motors at the rated output power shall not be lower than the specified value in the appendix in Table A-3Table A-3: standard rated efficiency for the electrical motor.

The current standard replaced the past editions which are “GB 18613-2002”, and “GB 18613-2006”. (Quality Supervision, Inspection and Quarantine Administration, 2011)

- Lighting

This European Standard EN 12464-1:2002 was approved by CEN on 16 October 2002. CEN members are bound to comply with the CEN/CENELEC Internal Regulations which stipulate the conditions for giving this European Standard the status of a national standard without any alteration. Up-to-date lists and bibliographical references concerning such national standards may be obtained on application to the Management Centre or to any CEN member.

This standard EN 12464-1:2002 specifies requirements for lighting systems for most indoor work places and their associated areas in terms of quantity and quality of illumination. In addition, recommendations are given for good lighting practice. This Standard specifies many parameters related for good lighting practice it is essential that in addition to the required illuminance, qualitative and quantitative needs are satisfied. Some of these parameters are:

- Luminance distribution.

- Glare.

- Directionality of light.

- Colour rendering and colour appearance of the light.

The measured illuminance value in Al-Amour factory doesn’t satisfied the standard illuminance. In appendix at Table A-2: standard illumination levels gives the maintained illuminance Em on the reference surface for the interior area and task or activity given. (CEN national Members, 2012)

## Earlier coursework

The following courses were and will be used for the project

- Energy management - 65521

This is one of the most important courses that will be the used in the project. At this course, several important issues and principles of energy management are defined such as, justifications of energy consumption; energy scrutiny and analysis, and the formulation of the power management options, economic evaluation of the implementation of the control. Techniques of justifications of energy consumption, the most important rationalization of energy consumption in the factory is Electrical Motors.

- Energy and Environment - 64235

This course covers energy systems and the environment, conventional energy sources and renewable energy, energy situation in Palestine and sources of various applications, the implications of the use of renewable energy, the rationalization of energy consumption on the environment and reducing harmful emissions, the implications of the increase of pollution in the air, water, soil, temperature and pollution resulting from the inconvenience, the causes of climate change the global, regional and local levels, and ways to combat pollution; environmental laws in the fight against pollution. Sustainability: Global Warming; emissions of greenhouse gases, and the mitigation of their effects and sustainability; external influences energy systems in the future, and the impact of clean energy technologies.

- Electrical Machines and its lab - 63391, 63392

This two course covers the information about the main types of generators and motors used in industries and commercial buildings and to become familiar with the measurements of voltage, current, power, torque & speed. The performance of each machine was studied in details.

- Principles of Scientific & Technical Writing Research - 64300

This course in its broad perspective introduces the key concepts related to scientific research and technical writing within an engineering framework. This course covers and demonstrate an understanding the importance of scientific research and the role of professional technical writing.

- Maintenance Management -64535

At this course, several important issues and principles of energy management are defined such as the common problem faced the energy auditor in the facility, the energy policy must be followed to reduce energy consumptions of the facility, the energy manager certified CEM, the types of maintenance and the maintenance policy in the facility.

# Methodology

In order to answer the research questions an energy audit was performed in AL-Amour Industry, the study was conducted in the steel tube and profile factory as case study of the overall energy performance of the industry. The energy audit study was conducted through various steps. As shown in the following figure.

Figure 4-1: methodology procedure

- Data collection

The first stage of the energy audit is to gather preliminary information of the faculty such as: geographic location, facility layout and identify the mechanism of the production line throw some technical details such as: process diagram, drawings and equipment inventory.

- Field visit

- Initial walk through tour

The first step of the field visit will help the auditing team understand the preliminary data of the industry such as: the layout of the factory and mechanism of the production line

- Introductory meeting

After the initial walk through the factory, the auditing team conducted a first meeting with executive manager and the supervised engineers to layout the method, time plan and expected goals of the energy audit.

- Audit interview

The auditing team conducted some interviews with staff to understand the behaviour of the worker.

- Gathering detailed data

The auditing team gathered the needed information, including collecting details of the energy consuming equipment such as brand, model, power and hours of operation. Using some metering device to measure the needed values to estimate the energy consumption and to conduct the energy saving opportunities, such as: voltage, current, power and power factor.

The required data was gathered during several visits to the industry with coordination with the industry engineers and our department instructors.

- Analysis of energy performance

The energy performance of the equipment was analysed, as well as the equipment consuming higher energy and compared to the energy standard in order to determine the potential for reducing consumption and to define the energy saving measures to improve global energy performance. Load factor and efficiency for the electrical motor was estimated as the primary indicator of the energy performance, electrical consumption was the primary indictor of energy performance for the lighting system and compressed air system and energy production index was estimated to estimated energy consumption over production for the high frequency welding. More details and mathematical equation are illustrated in Chapter 6.

- Analysis of energy saving opportunities

After collecting the required data, energy saving opportunities was identified and analysed based on the theoretical background and literature review done by the auditing team. The analysed data manage the auditor to detect energy saving measures to reduce energy consumption.  Energy and cost savings of these measures was assessed, together with investment needed and payback.

- Energy audit report

Following the energy audit, an energy audit report was implemented, which included the following information:

- Technical scope: this point includes facilities, services and included areas and level of depth in the analysis and detail required.

- Methodology: this point includes the analysis of the state of art of the facilities (energy inputs, technologies and services), measurement results and energy balance.

- Suggested energy saving measures: this point includes a description of each energy saving measure, including potential energy savings, economic savings, investment needed and payback.

- Conclusions: this point includes the recommended measures, total energy savings, total economic savings, total investment and payback.

# Literature Review

In order to understand the project, the auditor have studied some literature reviews in the field of energy efficiency and conservation in the industrial sector. The literature referred for this report was articles, master degree thesis and research papers mostly published in international journals.

T. Tantisattayakul et al, (2016) studied the potential of energy saving in the petrochemical industry in Thailand, the researchers divided energy conservation measurement into six categories; steam saving, seam optimization, cogeneration, power saving by efficient chillers, energy efficiency and waste energy recovery. The analyses were performed in energy, environment and economical respective, they found out that, from energy and environmental perspectives, the cogeneration was the most capable of reducing energy consumption and greenhouse gas emission, however it was the lowest cost effective method. From economic point of view, the most cost effective measure category was steam saving and steam loss reduction. The researchers point out that the most popular method was energy efficiency due to its simplicity, wide range of application and low investment cost.

K. Natarajan, (2015) investigated electrical energy conservation strategies and energy management practices and policies, which enhance the conservation of electrical energy in industries. A three-pronged approach to energy conservation was presented: capacity utilization, fine-tuning and technology up gradation.

Alajlan, Smlai and Elani, (1998) studied the sharp increase of the electrical energy consumption in Saudi Arabia, and the need of energy efficiency technology. They divided energy efficiency technologies into three main groups; electrical equipment, energy conservation in building (throw thermal insulation to the building envelope) and energy conservation supporting tools (public awareness and information). The researchers estimated that 25% of the new energy generating capacity will be reduced if the three factor were implemented.

B. Yaseen, (2008) investigated the potential of energy conservation opportunities in some Palestinian industrial facilities, through conducting energy audits in some industries in Palestine (the facilities consider to be high energy consumers), and he found out a good potential for energy saving in the audited facilities. The researcher estimated that on the national level (10% - 20%) savings from the total energy consumption in the industrial sector could be achieved by implementing some energy conservation measures with no and low cost investment.

Palestinian energy & environment research centre, (2011) studied energy consumption for “JACIR PALACE INTERCONTINENTAL HOTEL” in Bethlehem, Palestine and the possible energy conservation, the study was carried out on the lighting system, boilers, HVAC system and motors load, they found out there was a good energy saving opportunities with low cost investment. The saving was estimated around 30% with SPBP of 1.31 years.

Nassorah, (2016) studied the possibility of implementation energy efficiency opportunities and renewable energy in the industrial sector of Palestine in order to contribute in solving the problem of energy in the West Bank. Three industrial facilities were taken as a sample which consider large energy consumers according to the Palestinian classification, the study of the energy efficiency opportunities include the analysing of tariff, power factor, load, lighting, motors and boilers, and he found out that the possible saving of the energy efficiency opportunities range between 15.7% to 18.7%, and the possible saving from the on-grid PV system is estimated to be around 10 %, and the total annual reduction of CO2 emissions would be 2,285 tons.

Shaikh, Memon and Hussain, (2016) studied the benefit of installing high efficiency motors over the stranded efficiency motors of similar rating in the industrial sector of Pakistan. They have conducted some personal visits to the industries in order to collect the necessary measurements about the current motors (SEMs), 20 motors with different rating and application were compared with similar (EEMs) and they found that the additional investment required to buy the efficient motors would be recover within 0.22 years.

Chirakalwasan, (2006) in his article he describes the efficiency and the usage of induction motors for energy conservation such as speed reduction and variable speed drive. The article also describes two methods to estimate the operated efficiency for electric motors, the first method was to find the part load of the motor and to estimate the efficiency from the manufacture or standard part load-efficiency tables, in the absence of the part load-efficiency tables the author describe a second method to estimate the efficiency by using a mathematical equation estimating the electrical losses and the efficiency.

Vishnu and Vasanthakumar, (2015) studied experimentally the performance of air compressor systems. They conducted the experiment on a sample of twelve compresses that were operated in a manufacturing plant in India, some performance parameters were calculated experimentally such as: volumetric efficiency and power consumption. They found out that the majority of compressors at the plant are running at efficiencies less than 70%. But due to cost problem the auditors suggested that only the lowest efficient compressor with an efficiency of 30.7% should be replace with an energy efficient one, and for the other compressors preventive measures were to be taken to improve efficiency such as: air leakage maintenance and periodic check for the air filtering system and control valves.

As it was discussed in the hypothesis of the report, most audited industries in Palestine suffered from low energy efficiency and good potential of energy saving as B. Yaseen, (2008) and Nassorah, (2016) show in their studies. Energy efficiency is the most popular method to reduce operating cost as T. Tantisattayakul et al, (2016) discussed in their study. The audited team suppose that replacing energy efficient motor over standard efficient motor will reduce consumption as Shaikh, Memon and Hussain, (2016) show in their study, and as Vishnu and Vasanthakumar, (2015) show in their experiment, periodic maintenance of the air leakage and control valve could be the primary concern for better energy efficiency for the air composers system.

# Theoretical Background

Energy conservation and efficiency opportunities vary depending on the system and operation condition, many of them have been established with exact procedure and equation, or do be determine depended on the operation condition of the device.

This chapter discusses the main energy consumption in the industry which are the electrical motor, lighting system, compressed air and the high frequency welding.

## Electrical motors

Type of electrical motors

- Direct-Current Motors

Direct-Current motors, as the name implies, use direct, i.e. unidirectional, current. Used in special applications, they only represent about 10% of motors used in industry.

- Synchronous Motors

AC power is fed to the stator of the synchronous motor. The rotor is fed by dc from a separate source. The rotor field locks onto the stator rotating field and rotates at the same speed. The speed of the rotor is a function of the supply frequency and the number of magnetic poles in the stator.

- Induction Motors

In induction motors a magnetic field is induced in the rotor windings by the magnetic fields set up in the stator by ac power supplies. They are the cheapest and simplest type of electric ac motor.

Energy performance indicators

- Electrical consumption

The consumption of the electrical motor is illustrated in the following equation

Pin=√3×V×I×cos∅1000 kW

Equation 1:motor power consumption

Where

V =Average voltage between any two phases in Volt

V= Vab+Vbc + Vac 3

Vab: Voltage between phase a and b

Vbc: Voltage between phase b and c

Vac: Voltage between phase a and c

I = Average current of the motor in Ampere

I=I ab+I bc+I ac 3

Iab: current at line a, b

Ibc: current at line b, c

Iac: current at line a, c

Cos∂ = Power Factor

cos ∂=PF1 +PF2 +PF33

PF1: Power Factor for phase 1

PF2: Power Factor for phase 2

PF3: Power Factor for phase 3

Energy consuption=Demand power Pin×Operating hour kWh

Equation 2:motor energy consumption

- Power Factor

The power factor of the motor is real power divided into apparent power, the real power and the apparent power can be found directly from power analyser.

Power factor = Real power / Total power

Power factor= Real powerTotal power

Equation 3:power Factor

As the load on the motor decrease, the active current decrease, so that the power factor decrease, the relation between the percent of the load with power factor, when the percent of the load increase, the power factor increase.

- Load factor

The load factor is the operated load on the motor to the rated load. The load factor can be estimated as the following equation shows

Load %=Pin(Pratedηrated)

Equation 4:load factor

Where:

Pin: measured or calculated power consumption

Prated: rated power or nameplate nominal power.

ηrated: rated efficiency on the name plate of the motor.

- Efficiency

The efficiency of the motor is the power output to the input power.

η=Power outoutPower input×100%

Equation 5:motor efficiency

The rated efficiency can be obtained from the nameplate as illustrated Table 7-1. If the rated efficiency wasn’t found on the nameplate of the motor it can be estimated from the national standard of the manufacture. And since the used motors in the industry were Chinese, (GB18613-2012)

The actual efficiency or operated efficiency of the electrical motor various from the rated efficiency, depending on some factors. One of the most important factor is the load factor as Figure 6-1 shows the relation between motor efficiency and load factor.

Figure 6-1: Typical motor Efficiency vs. Load factor (Natural Resources Canada, 2015)

The operated efficiency of the electric motors can be estimated from the calculated load factor as Figure 6-1shows, the efficiency increase as the power factor increase until it reaches the maximum or rated value. The figure also shows that the efficiency of the bigger motor varies less above 25 % load factor.

Energy conservation opportunities

There are many energy efficiency opportunities on electrical motor, this section focused on five main methods.

- Load Scheduling

- Switch off the unnecessary Motors: by turning of the motors that not used, there is an amount of saving happened that can be calculated as:

Saving($)=Demand kW×Timeh×Cost ($kWh)

Equation 6: saving on motor, using load shedding

- Schedule Motor Operations to Lower Overall Demand: the motors should be scheduled to ensure that the necessary motors operate at the needed time.

- Drive Maintenance and Alignment

Operation of a motor is affected by maintenance. the maintenance could be cleaning the motor or filters against the dust, or it could be by make the temperature and the moisture is good, or by noticing any noticeable increase in motor drive vibration.

- Power Factor Correction

Induction motor uses magnetizing current to convert the electrical energy into mechanical energy. This magnetizing current or reactive current component of the total current lags behind the applied voltage by 90 Ø and results in a phase displacement. This reactive current can come from the utility and there is a penalty is paying for it, or from the capacitors.

The capacitor size that should be used can be calculated for the following equation,

Q=Pinη×tan∅1-(tan∅2)

Equation 7: power factor correction

Where

P = Motor Rating (kW)

η = Motor Efficiency

Ø1 = Phase angle before correction

Ø2 = Phase angle after correction

- Balance Motor Phase Voltages

Motors should operate within turbulence between phases of 5% of the rated voltage. the unbalance phase voltage increases the losses and temperature.

- Choice Energy Efficient Motors

Energy efficiency motor might be expensive comparing with standard efficiency motor. However, it has many advantages such as: reduce the losses and the heat generation, lower operating costs, Improved Bearing Life and improved power factor (Turner, 2007).

Figure 6-2:Standard motors vs high efficiency motors

Saving kWh=Prated×load%×1ηstd-1ηEE×Hrshyear×cost of energy$kWh

Equation 8: saving from installing energy efficient motors

Hrs: the estimated annual operated hours of the electric motor

## Lighting system

lighting system consists of:

- light sources (lamps).

- luminaires (or ﬁxtures).

- ballasts.

Lighting system consume 5-25% of the total energy consumption in the total industrial facilities. Light measured in lumens by the light meter, per unit surface area., illumination (lux)

To get a reference point on the lighting system, the illumination of the industry will be measured to be compare to standard value.

Energy performance indicator

Electrical consumption:

Consumption ($) = kw of each lamp *number of lamps *operating hours* cost of electricity($/Kwh)

Electrical consuption (kWhyear )=power kWlamps×number of lamps lamps×operated hours  hrsyear

Equation 9: lighting system energy consumption

Energy conservation opportunities

This section focus on four main energy conservation opportunities, three of them depend on the current value of illumination.

- Switch off Unnecessary Lights

That can be done manually or automatically by using a controller that contains photo sensors or time switchers.

Saving ($) = kw of each lamp closed *number of lamps *operating hours* cost of electricity($/Kwh)

Saving ($year)=power (kwlamp)× namber of lamps×hrs×cost of electricity ($kWh)

Equation 10: lamp saving, unnecessary lamp

- Fixture De-lamping

By remove the unnecessary lamp and keep updating it to reduce the cost.

N=E*An*∅*Ku*Km

Equation 11:the optimum number of fixtures

Where

E is illumination lm/m² (lux), A: area in m², n: number of lamps in the unit, Φ: luminous flux in lumen, Ku is reflectance factor (it depends on the colour of walls) (0.6-0.8) and Km is maintenance factor (it depends on the condition of the lamp, clean or not, 0.6- 0.8).

- Task lighting

It’s a method to reach the prober illumination level on the work surface by putting lamps close to the needed work areas.

- Maintenance by cleaning from the dust and re-lamping

The dust could be a main factor for reducing light utilization by up to 40 percent and increases heat production, so cleaning the lamp and reflector and the surface of the rooms important. As for re-lamping, there is two types which is spot re-lamping and group re-lamping that is used normally because it reduces lamp costs (discounts), allow lamp maintenance to be scheduled, maintain higher and more uniform lighting levels and insure the correct lamp use. The cost of re-lamping is defined by below equation:

- Spot re-lamping

Cost=L+S

Equation 12: cost, spot re-lamping

S: spot replacement labour cost per lamp.

L: Price per lamp.

- Group re-lamping

Cost=L-GI

Equation 13: cost, group re-lamping

Where:

L: Price per lamp.

G: group replacement labour cost per lamp.

I: group re-lamping interval.

- Installing high efficiency lamps.

Saving ($year)=number of lamps*(powerold lamps-powernew lamps kW)×hrs (hr)×cost of elctricity ( $/kWh)

Equation 14: saving, high efficient lamps

## Compressed air system

Compressed air is air kept under a pressure that is greater than atmospheric pressure. It serves many domestic and industrial purposes.

Compressed air systems consist of a supply side, which includes compressors and air treatment, and a demand side, which includes distribution and storage systems and end-use equipment.

A properly managed supply side will result in clean, dry, stable air being delivered at the appropriate pressure in a dependable, cost-effective manner.

A properly managed demand side minimizes wasted air and uses compressed air for appropriate applications.

Energy performance indicator:

Electrical consumption

P= 3*V*I*cosθ

Equation 15: power consumption in compressor

Where:
V and I are the average measured voltage and current respectively.

Energy consumption:

E= P, avg (kW) ×Hrs (hyear)

Equation 16:energy consumption, compressor

Energy saving opportunities in compressor

- Leak Reduction. Leaks can found using Ultra sonic leak detector and it can be a significant source of wasted energy in a compressed air system, sometimes wasting 20-30% of a compressor's output. A typical plant that has not been well maintained will likely have a leak rate equal to 20% of total compressed air production capacity or more. On the other hand, proactive leak detection and repair can reduce leaks to less than 10% of compressor output. Leakage expressed in terms of the percentage of compressor capacity lost. The percentage lost to leakage should be less than 10% in a well-maintained system. Poorly maintained systems can have losses as high as 20-40% of air capacity and power.

the additional power demand for the coverage of the wasted energy is:

Aditional power kw=WLoaded-WUnloaded*TT+t

Equation 17:the additional power for the coverage of the wasted energy

Where

W loaded: Power requirement during "loaded" mode (kW)

W unloaded: Power requirement during "unloaded" mode (kW)

T = Time running "loaded" (sec)

t = Time running "unloaded" (sec)

Leakage %= T+100T+t

Equation 18:leakage percentage

Where:

T is the loaded time in and t is unloaded time in minutes.

- Inlet Temperature of the compressor. The inlet temperature of the air has an impact on the density of the air at the intake of the compressor and will influence the kinetic energy transferred by the blades to the air. Increased density at lower intake temperatures will result in higher power consumption of the compressor.

As a rule of thumb, each 3°C lower air temperature will save 1% compressor energy. In addition to energy savings, compressor capacity is increased when cold air from outside is used.

W2=W1*[1+0.00341*T2-T1]

Equation 19:power reduction caused by decreasing inlet temperature

W1, W2 = initial and final ideal compression powers (kW)

T1, T2 = initial and final inlet air temperatures (°C)

- Maintain separators, filters, dryers and valves. Regularly check and replace filters. Blocked filters will cause a significant pressure drop and so waste energy. Replace manual, disc and timed drains with new electronic level sensing drains to reduce the amount of waste. Electronic level sensing drains help to optimize the time that drains are open for.

- Install variable speed Drive. Variable speed drives can be fitted to the motors of screw and vane compressors, and most suppliers are now offering factory-fitted, variable-speed units. These allow the motor to be run at the rate required in order to fulfil demand at that time. This method can save considerable amounts of energy.

## High frequency welding

The industry has a high frequency welding to form the pipes, the energy consumption of the welding is shown in the equation

Energy (kWhyear)=P,avg×Hrs

Equation 20: energy consumption, HF welding

Where:

Pavg is the average power measured using the power analyser

Hrs is the annual operated hours

EUI kWhPipe=Enery (kWh/minute)#pipes (pipe/minute)

Equation 21: EUI, HF welding

The above equation shows the energy unity index as kWh per produce pipe

# Collected Data and Analysis of Energy Performance

To obtain the best result for successful energy efficiency opportunities, the energy audit requires to make some measurements during the study in the industry. This chapter include some details of the instruments that were used during the project and samples of the collected data. As well as the energy performance analysis of the energy consuming systems.

- Clamp Meter

These are very useful instruments for measuring current in a wire without having to make any live electrical connections. The clamp is opened up and put around one insulated conductor, and the meter reads the current in that conductor. Also, used to measure voltage first by setting the clamp meter to the voltage symbol “V” to read the voltage on the conductor.

Figure 7-1: Clamp Meter device (PCE Instruments, 2016)

- Light meter

A lux meter is a device for measuring brightness, specifically, the intensity with which the brightness appears to the human eye. The lux is a unit of measurement of brightness, or more accurately, illuminance. It ultimately derives from the candle, the standard unit of measurement for the power of light. A candle is a fixed amount, roughly equivalent to the brightness of one candle. The lux takes into account the surface area over which this light is spread, which affects how bright it appears. One lux equals one lumen of light spread across a surface one square meter. A lux meter works by using a photo cell to capture light.

Figure 7-2: Light Meter Device (Magnaflux , 2010)

- Thermometer

Digital thermometer is a device measures the air temperature almost instantly. The LCD display to read the temperature in either Celsius or Fahrenheit, and receive a temperature read in 10 seconds this device was used to read the inlet air temperature of the compressor.

Figure 7-3: Thermo Meter Device (zytemp, 2014)

- Power Analyzer

An instrument for measuring various parameters of an electrical power distribution system is often called an energy analyzer. The term is also used for computer software for analyzing the use of electrical or other energy use, for example determining how electrical power is consumed in a building with a view to reducing waste, calculate loads and costs associated with air conditioning, heating, and on-site power generation. An electrical energy analyzer might measure for single- and three-phase systems volts RMS, amps RMS, power factor, instantaneous power in watts (W), instantaneous volt-amperes (VA), reactive volt-amperes (VAR), frequency (Hz), average and maximum powers (W), energy in watt-hours (Wh), and phase angles.

Figure 7-4: Power Analyzer Device (PCE Instruments, 2016)

## Electric motor

The factory has two main production line each consist of several electric motors and a cooling tower the name plate reading and some measured data were taken using clamp meters and a power analyzer, as shown in the following tables.

- Name plate

The nameplate rating of the electrical motors was tabulated, the electrical motor was referred to as number. Table 7-1 includes a sample of the collected reading from the electric motor name plate

More detailed are included in the Table A-4, page 72

Table 7-1: A sample of the name plate reading of the electric motor.

| Electric motor | Rated power (kW) | Full load current (A) | Rated voltage (V) | Speed (RPM) | IP | Rated Efficiency | Rated Power factor |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 1st production line |  |  |  |  |  |  |  |
| 2 |  | 5.5 | 12 | 380 | 55 |  |  |
| 3 | 4 | 8.8 | 380 | 1440 |  | 84.2% | 0.82 |
| 2nd production line |  |  |  |  |  |  |  |
| 2 | 11 | 22.6 | 380 | 1460 | 44 | 88% | 0.84 |
| 4 | 90 | 7.45 | 180 | 1500-2800 | 21S |  |  |
| Colling tower |  |  |  |  |  |  |  |
| Pump 1 | 7.5 | 15 | 380 | 2900 |  |  |  |
| Pump 2 | 1.5 | 3.44 | 380 | 2800 |  |  |  |

The shown table describe the name plates data for the existing motors in the factory, it is obvious that some data is missing such as starting current and voltage, efficiency and power factor, these data does not exist because most of motors doesn't contains it on its name plate.

- Measured data

Measured data were necessary to conduct the energy performance analysis. To obtained the needed measurement the electrical motors were divided into two group the first one which had a higher rated power with respect to the rest and suspected to have a variable load, so the data were obtained using a power analyzer. The second group were the motors had a smaller rated power and were operating at nearly constant load, and the required measurement could be obtained by using clamp meters.

Motors “A” and “B” from the first and second production line and the induction welding were considered within the first group, the rest were considered within the second group.

Detailed power analyser measurements are included in Appendix 5: Power analyser measurements, page 74.

Table 7-2 includes a sample of the collected data from the electric motor using clamp meters

More detailed tables are included in the Table A-5, page 73.

Table 7-2: A sample of measured data using clamp meters.

| Electric motor | Phase current (A) |  |  |  | Line voltage (V) |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | A | B | C | Avg. | AB | BC | AC | Avg. |
| 1st production line |  |  |  |  |  |  |  |  |
| 2 | 5 | 4.88 | 4.8 | 4.9 | 393 | 384 | 388 | 389 |
| 3 | 4.45 | 3.9 | 4 | 4.1 | 391 | 382 | 386 | 386 |
| 2nd production line |  |  |  |  |  |  |  |  |
| 1 | 12.9 | 12.3 | 12 | 12.4 | 414 | 409 | 410 | 411 |
| 2 | 15 | 15.1 | 15.3 | 15.1 | 410 | 411 | 409 | 410 |
| Cooling tower |  |  |  |  |  |  |  |  |
| Pump 1 | 10.1 | 10 | 9 | 9.7 | 405 | 405 | 406 | 405 |
| Pump 2 | 3.1 | 3.2 | 3 | 3.1 | 406 | 405 | 408 | 406 |

Energy performance analysis

As it was discussed in the research methodology the primary indicator of the energy performance of the electrical motor are the electrical consumption, load factor and efficiency.

- Electrical consumption

The electrical consumption of the electrical motor can be estimated from Equation 2

Energy consumption=Demand power Pin×Operating hour kWh

Pin can be calculated from measured data as Equation 1 shows below

Pin=√3×V×I×cos∅1000 kW

- Load factor

Load %=Pin(Pratedηrated)

Equation 4:load factor, describes the mathematical equation to calculate the load factor, as it shown in the equation the needed measurement are the input power, rated power and efficiency.

The rated power and efficiency can be obtained from the name plate of the electrical motor as Table 7-1 shows. Some motor name plate didn’t include the rated efficiency, in this case the readings were obtained from the “National Standard of the People’s Republic of China” Table A-3, page 70.

Pin=√3×V×I×cos∅1000 kW

Calculation sample is illustrated below, for motor # 3 from the first production line

Pin=√3×V×I×cos∅1000=3×4.1×386*0.821000=2.25 kW

Energy consumption=2.25×1200=2710 kWh/year
load %=Pin(Pratedηrated)=2.540.84=47.4%

- Efficiency

The operated efficiency was estimated as a ratio with the load factor as Figure 6-1 shows.

The load% for motor number 3 from the first production line was calculated to be 47.4% and the rated power was 4 kW. the estimated efficiency from Figure 6-1 is 81%.

Table 7-3 shows the various electric motor by number, rated power in kilo Watt, rated efficiency, percentage of load factor and the estimated operated efficiency.

Table 7-3: load factor and efficiency of the electric motor

| Electric motor | Rated power (kW) | Rated efficiency | Load factor | Estimated efficiency |
| --- | --- | --- | --- | --- |
| 1/1PL | 3.70 | 83.0% | 79.0% | 83.0% |
| 2/1PL | 5.50 | 85.7% | 41.6% | 81.0% |
| Fan 1/1PL | 3.00 | 83.5% | 51.0% | 80.0% |
| 3/1PL | 4.00 | 84.6% | 47.8% | 81.0% |
| 4/1PL | 4.00 | 84.6% | 47.8% | 81.0% |
| Fan 2/1PL | 3.00 | 83.5% | 56.7% | 80.0% |
| C/1PL | 11.00 | 85.0% | 49.7% | 83.0% |
| 1/2PL | 11.00 | 88.0% | 59.3% | 85.0% |
| 2/2PL | 15.00 | 90.0% | 54.6% | 86.0% |
| pump1 /2PL | 7.50 | 87.0% | 69.0% | 86.0% |
| pump 2/2PL | 1.50 | 78.5% | 93.6% | 77.0% |
| A/2PL | 90.00 | 83.0% | 32.0% | 82.0% |
| B/2PL | 90.00 | 83.0% | 17.3% | 80.0% |

The total energy consumption by the electric motor is 162,105 kWh

## Lighting system

There are 23 metal halide lamps in the industry, but the industry mainly depends on natural lighting during the day time and only thirteen lamps for additional illumination during cloudy days, and the rest of the lamps were burn out.

To estimate the performance of the lighting levels in the factory using “EN 12464-1:2002” standard shown in Table A-2, page 68. and compare it with the measured lighting values.

Some measurement of the illumination was taken in different location of the factory using the light meter. The illumination levels were measured using the lux meter, and the average values are shown in the table below.

Table 7-4: measured illumination levels

| Time | Location | Lighting system | Measured illumination |
| --- | --- | --- | --- |
| Before Midday | First Production Line | Off | 75 Lux |
|  |  | On | 115 Lux |
|  | Second Production Line | Off | 93 Lux |
|  |  | On | 172 Lux |
| After Midday | First Production Line | Off | 170 Lux |
|  | Second Production Line | Off | 315 Lux |

As it shown the table above the illuminations levels before midday are low without lighting. And for better work area the lamps should be turn on for additional three hour before midday to improve the illumination levels to an Acceptable value.

Table 7-5 shows technical data for the used metal lamps. And Figure 7-5 shows a picture of the lamp.

Table 7-5: lamp data sheet

| Nominal power | 400 W |
| --- | --- |
| Rated luminous flux | 34,000 lm |
| Rated lamp efficacy | 81 lm/W |
| Energy efficiency class | A |

Figure 7-5: power star hqi-t/ metal halide lamp

Electrical consumption

The industry depends mainly on natural lighting and turn on thirteen lamp after midday during cloudy days and the early morning of Ramadan month.

The annual operated hours of the lamps are

- 3 hours after midday during cloudy days, around 52 days/ year (meteoblue, 2014)

- 3 hours during the early morning of Ramadan month, 30 days/year

Total operating horse are 246 hour/ year

The electrical consumption of the lighting system can be found using  REF _Ref483075246 \h Equation 9.

Electrical consuption (kWhyear )=13 lamp ×0.4 kW×246 (hyear )=1,280 (kWhyear )

## Compressed air system

The industry has one compressor with a rated power of 22 kW and a storage tank of about three m3, which feed pneumatic air valve and moving strips to help the worker push the profile the shipping area. The compressor operates at a pressure between 7-8.3 bar and its needed the whole day. The power analyzer was used to measure the needed data to complete the performance analysis. Such as the time and power consumed during load and unload condition. Table 7-6 shows the average measured data from the power analyzer. More detailed tables are included in Table A-8, page 90.

Table 7-6: measured data from the compressor

| Power Avg., load | Time, load | Power Avg., no load | Time, no load | Power Avg., Total |
| --- | --- | --- | --- | --- |
| 14.9 kW | 44.2 % | 3.6 kW | 55.8% | 7.42 kW |

The annual electrical consumption of the compressor can be found using Equation 16:energy consumption, compressor

E= P, avg kW×Hrs hyear=7.42 ×3000=22,264 kWhyear

## High frequency welding

The industry has a high frequency welding in the second production line after to form the pipes. The power analyzer was used to measure the needed data to complete the performance analysis as shown in the Table A-9, page 101. The measurements of the welding were obtained as the factory form a pipe with a nominal dimeter of 2 inch.

The main energy performance indicator is the electrical consumption and energy unit index as shown in Equation 20 and Equation 21

Energy kWhyear=73.16×2100=153.638 (kWhyear )

EUI kWhPipe=Enery (kWh/minute)# pipes (pipe/minute)=1.22 (kWh/minute)6 (pipe/minute)=0.203 (kWh/pipe)

## Evaluation of the overall energy consumption

The total estimated energy consumption from the industry is 338,913 kWh/year. Figure 7-6 shows the percentages of energy consumption in the industry excluding the lighting system for its small amount.

Figure 7-6: energy consumption percentage

# Energy Conservation Opportunities and Economic Evaluation

## Electrical motors

The main energy conservation opportunities that can be implemented on electrical motors as it was discussed in Chapter 6 is to improve the load factor and to replace the current motors with high efficient motors. the analysis was estimated to replace the current motors with motors that has better load factor and higher efficiency using “TOSHIBA”, electric motor catalogue. Table A-10, page 108.

Table below shows the rated power and estimated efficiency for the current electric motors with the suggested replacement from Toshiba’s catalogue.

Table 8-1: rated power and efficiency for current and suggested motors

| Current motor |  |  | Suggested motor |  |  |
| --- | --- | --- | --- | --- | --- |
| Motor number | Rated Power | Efficiency | Model number | Rated Power | Efficiency |
| 1/1PL | 3.70 kW | 83.0% | 813-B0030 | 3.00 | 90.2% |
| 2/1PL | 5.50 kW | 81.0% | 813-B0031 | 3.00 kW | 90.2% |
| Fan 1/1PL | 3.00 kW | 80.0% | 813–B0020 | 2.20 kW | 88.5% |
| 3/1PL | 4.00 kW | 81.0% | 813–B0020 | 2.20 kW | 88.5% |
| 4/1PL | 4.00 kW | 81.0% | 813–B0020 | 2.20 kW | 88.5% |
| Fan 2/1PL | 3.00 kW | 80.0% | 813–B0020 | 2.20 kW | 88.5% |
| C/1PL | 11.00 kW | 83.0% | 813–B0070 | 7.50 kW | 91.5% |
| 1/2PL | 11.00 kW | 85.0% | 813–B0070 | 7.50 kW | 91.5% |
| 2/2PL | 15.00 kW | 86.0% | 813–B0110 | 11.00 kW | 92.4% |
| pump1 /2PL | 7.50 kW | 86.0% | 813–B0070 | 7.50 kW | 91.5% |
| pump 2/2PL | 1.50 kW | 77.0% | 813–B0015 | 1.5 kW | 86.2% |
| A/2PL | 90.00 kW | 85% | 813–B0370 | 37 kW | 94.5% |
| B/2PL | 90.00 kW | 85% | 813–B0371 | 37 kW | 94.5% |

Figure 8-1: load factor improvement

Figure 8-1 shows the estimated improvement in load factor for the suggested motors.

The estimated saving from replacing the current motor can be estimated from Equation 8. A sample of the estimated saving is calculated below, for motor A/2PL

Saving ($year)=90 kW ×0.328×10.85- 10.945×2100 hyear×0.172 $kWh=1,246 ($year)

Figure 8-2: comparison of the annual cost between the current motors and suggested replacement

As shown in Figure 8-2, the annual saving from replacing the electrical motor with high efficient motor is better to be implemented for motors with high operating hours and rated power

Table below shows the annual saving from installing high efficient motors for motors with more the cooling tower pumps and motor A and B from the second production line.

Table 8-2: saving by replace the electric motors with high efficiency motors

| Current motor | Suggested motor | Saving ($/year) | Saving % |
| --- | --- | --- | --- |
| pump1 /2PL | 813–B0070 | 129.09 | 6.99% |
| pump 2/2PL | 813–B0015 | 69.49 | 13.86% |
| A/2PL | 813–B0370 | 1245.94 | 11.83% |
| B/2PL | 813–B0371 | 672.94 | 11.83% |
| Total |  | 2,117.5 | 10.71% |

Table 8-2 shows the total saving from replacing the cooling tower pumps and motor A and B from the second production line could save 2,117 $ per year. The estimated energy reduction is 12,308 kWh/year.

## Lighting system

The used lighting system consist of 23 lamps, 10 of them were burn out, and they operate only when needed at estimated period of 264 hour/ year, as discussed in Chapter 7

### Energy conservation opportunities

- The number of necessary lamps can be found from Equation 11

N = (300*450)/ (1*34000*0.5*0.7) = 11.3 = 12 lamp

There are 13 working lamps working in the factory

The lamps in the factory works about 264 hours, but this make a problem in the illumination before midday, the lamps should be switched on about 3 hours in the morning for 300 days per year to cover the shortage in the illumination at the factory. This leads to increase the energy consumption which can be found from the following Equation:

E=P*operating hours=13×0.4×(264+900)=6,052.8 kWh/year

Additional energy is needed to cover the shortage in the illumination levels. This additional energy can be reduced by using high efficient lamps.

- Install led lamps with 250w

Using Equation 14, the saving can be estimated to be

Saving (kWhyear)=13×0.4-0.25×1164=2,269.8 kWh/year

Economical evaluation

- The additional hours needed can have a such of cost which can be calculated from the next Equation.

Additional cost=Additional energy*costkWh =(6,052-1,280) ×0.172=476.7 $/year

Install high efficiency lighting lamps each lamp cost 7 $ and 3 $ for labor.

The annual saving = 2269*0.17 = 385.7 $

SBP = Implementation cost/Saving per year = 13*10/385.7 = 0.337 year.

## Compressed air system

### Energy opportunities

- Reduce leak.

The additional power needed for overage leak is found from Equation 17

Additional power=14.9-3.6210210+265=4.99 Kw

And leakage % also from Equation 18

Leakage % = (210*100)/ (210+265) = 65.3%  of the total consumption.

- Reduce inlet temperature of the compressor

The reduction of the inlet temperature of the compressor can make a good saving, and it can be calculating use Equation 19.

W2 = 7.47 *[1+0.00341*17-21] = 7.31 Kw

Saving = (7.47-7.31) *3000= 480 kWh/ Year.

Total energy reduction of 15,450 kWh/year

### Economic analysis

- Air leakage cost=Additional power*operating hours*CostkWh   = 4.99 * 3000*0.17

= 2544 $

If we assume that 90 % of the leaks can be arrested, so the annual saving will be about 2290 $.

The investment cost summarizes on improving the maintenance procedure, retrofitting control valves and fittings. The estimation cost, according to the maintenance manager, around 150 $.

SBP = 150/2290 = 0.065 Year.

- Saving $=Energy saved*costkWh = 480*0.17 = 81.6$

The investment cost required for this saving is the price and the installation cost of the duct which estimated at 160 $.

SBP = 160/81.6 = 1.96 Years.

## High frequency welding

We could save a big amount of apparent power by increasing the power factor of welding and calculate the needed amount of reactive power from. Equation

Q=p avg (tancos-1PF1tancos-1PF2)

=73.16127(tancos-10.452866tancos-10.85) = 100 kVAR

The welding needs a 144.1622 kVAR ,100 can be used from the capacitors and 44.1622 kVAR from the utility.

## Evaluation of the overall energy saving opportunities

the annual electric bill for the industry is shown in the table below

Figure 8-3: monthly electric bill for the factory

Is it shown in the figure the annual energy consumed is 353,162 kWh. And the total estimated energy consumed in Chapter 7 was 338,913 with an 4% error of estimating the total energy consumption.

The total energy saved is equal to energy saved in the electric motor and compressed air system

Energy saved,totalkWhyear =motors12,308+comprossor15,450=27,758 kWh

Saving $year=27,758×0.172=4,774 $/year

Saving%=EsavedEtotal×100%=22,758353,162×100%=7.85%

The estimated energy saving in the factory is 7.85% of the total bill.

## Greenhouse gases impact

The estimated greenhouse gases reduction will be estimated from the estimated.

MassNatural Gas=Energysaved MJyearEFFpower plant×calorific value=27,758×3.60.4×40=6.25 ton of natural gas/year

Greenhouse gasses reduction can be estimated using the following equations

CH4 at 98%=0.98×6.25=6.12 ton/year

- carbon dioxide CO2=4416×6.12=16.83tonyear

- water vapor  (H20)=3616×6.12=13.77tonyear

N2 at 0.6%=0.006×6.25=0.035tonyear

- nitrogen dioxide  NO2=9228×0.035=0.11tonyear

# Conclusion and Recommendations

High population growth, increasing living standards and rapid industrial growth has led to tremendous energy demand in the Palestine in recent years. The energy situation in Palestine is highly different compared to other countries in the Middle East due to non-availability of natural resource, financial crunch and unstable political condition.

Palestine is heavily dependent on Israel for meeting its energy requirements. Almost all petroleum products are imported through Israeli companies.  Israel controls energy imports into Palestine and thus prevents open trade in electricity and petroleum products between Palestine and other countries. So, the most of Palestinian should look forward to use renewable energy such as photovoltaic cell and solar water heaters, also applied energy audit strategy that comes to use in a widely range.

This project is an energy audit on Al-Amour factory to assessment the energy consumption, also analyse the readings, finding opportunities for saving and give the suitable recommendations. The savings could reduce the financial burden of the current energy bills at the factory. There would also be environmental benefits derived from implementing energy conservation measures. There would be tremendous reduction of localized gaseous emissions to the environment. The energy manager should also take the responsibility of educational awareness campaigns as way of changing the attitudinal behaviours of employees and even the management towards energy conservation.

The total energy consumption of the industry is 353,162 kWh/year, where the most of the energy is used by the electric motor 48%, HF welding 45% and compressor 7% of the total electrical consumption and the lighting system is less than 0.5% of the total consumption.

The energy saving opportunities for the electrical motor were analysed after calculating the main energy performance indicator which are load factor and operated efficiency, and the main energy conservation opportunities was to replace the current motor with high efficient motor with smaller rated power to improve the load factor and efficiency. the result of changing the cooling power pumps and motor A and B from the second production line was 12,308 kWh/year or 2,117 $/year.

As for the compressed air system, leaks from the piping was estimated to cost the factory 4.99 kW at estimated 3000 hour of operation per year. And reducing the inlet temperature by 4 ℃ would save 480 kWh/year. The total saving was estimated to reach 2,647 $/year.

The estimated energy saving is 7.85% from the total energy consumption from the motors and compressor.

The illuminations levels were measured in the industry before midday and without using the lighting, and the illuminations levels were below the standard acceptable range. And so, the lighting will have to be turn on for additional 3 hours every day to improve the illumination levels, the additional operating hour will cost 476 $/year. But it could be reduced by 62.5 % if the current lamps were to be replaced with high efficient lamps with SPBP of 4 months.

The high frequency welding has a low power factor of about 0.45, to improve the average power factor to 0.85 and to reduce the reactive power demanded on the utility. 100 kVAR capacitors is needed

In the end, we recommend to make a good maintenance programme for the electrical motors and to replace low efficient motors with high efficient ones, make a periodic check to fix the leakage in the pipelines of the air compressor and to increase the operating hours of the lighting and replacing the lamps with high efficient lamps.

# References

ALAJLAN, S., SMIAI, M., & ELANI, U. (1998). EFFECTIVE TOOLS TOWARD ELECTRICAL ENERGY CONSERVATION IN SAUDI ARABIA. Energy Convers., 1337-1349.

Alamour Industrial And Trading . (2016, Decemper 5). Alamour Industrial And Trading Main Divisions. Retrieved from Alamour Industrial And Trading Home: http://alamourco.ps

Alamour Industrial And Trading. (2016 , Decemper 5). Alamour Industrial And Trading Guide. Retrieved from Alamour Industrial And Trading Guide: http://alamourco.ps/pdffile/index.html#/0

Alamour Industrial And Trading. (2016, Decemper 5). Alamour Industrial and Trading. Retrieved from ALamour Steel Tubes and Profiles: http://alamourco.ps/?TemplateId=info&PageId=29&MenuId=16&Lang=1

CEN national Members. (2012, may 20). Light and lighting - Lighting of work places. EUROPEAN COMMITTEE FOR STANDARDIZATION. Brussels, Belgium, Belgium: CEN national Members.

Chirakalwasan, R. (2006). Motor load and efficiency . ASHRAE Thailand Journal, 21-33.

kcico. (2017, may 2). Layout of slitting line. Retrieved from kcico: http://www.kcico.com.tw/english/ecoil.htm

Magnaflux . (2010, january 12). Magnaflux Devices. Retrieved from Magnaflux Products: http://magnaflux.com/Magnaflux/Products/UV-Lamps/Light-Meters.htm

meteoblue. (2014). Climate Palestine - meteoblue. Retrieved from meteoblue : https://www.meteoblue.com/en/weather/forecast/modelclimate/palestine_united-states-of-america_4717232

Nassorah, A. O. (2016). Techno- Economic analysis of implementaion energy managment resourses in some factories in West Bank. Nablus.

Natarajan, K. (2016). Some Strategies for Electrical Energy Conservation and Management in Industries. Energy Engineering, 33-64.

Natural Resources Canada. (2015, 12 10). Motor Selection. Retrieved from Natural Resources Canada: http://www.nrcan.gc.ca/energy/products/reference/15297

Palestinian energy & environment research centre. (2011). Energy Audit Report on JACIR PALACE INTERCONTINENTAL HOTEL. PALESTINIAN ENERGY & NATURAL RESOURCES AUTHORITY.

PCE Instruments. (2016, may 6). Clamp Meter PCE-GPA 62. Retrieved from PCE Instruments: https://www.pce-instruments.com/english/measuring-instruments/test-meters/clamp-meter-pce-instruments-clamp-meter-pce-gpa-62-det_59796.htm

PCE Instruments. (2016, March 4). Power Analyzer PCE-PA 8000. Retrieved from PCE Measuring Instruments: https://www.pce-instruments.com/english/measuring-instruments/test-meters/power-quality-analyser-power-analyzer-pce-instruments-power-analyzer-pce-pa-8000-det_60720.htm

Quality Supervision, Inspection and Quarantine Administration. (2011, may 2). National Standard of the People’s Republic of China. The Standardization Administration of China. chicago, china, china: EuropElectro.

RLT Group. (2017, may 2). Layout of mild steel welded tube. Retrieved from steel pipe mill: http://www.rollforming-reliantt.com/1-5-steel-pipe-mill.html

Shaikh, M., Memon, A., & Hussain, M. (2016). Data on electrical energy conservation using high efficiency motors for the confidence bounds using statistical techniques.

Tantisattayakul, T., Soontharothai, J., Limphitakphong, N., Pharino, C., Chavalparit, O., & Kanchanapiya, P. (2016). Assessment of energy efficiency measures in the petrochemical industry in Thailand. Cleaner Production.

Toshiba. (2010, may 3). STANDARD HIGH EFFICIENCY MOTOR FEATURES INCLUDE. TOSHIBA INTERNATIONAL CORPORATION PTY LTD. Tokyo , Japan, Japan: TOSHIBA INTERNATIONAL CORPORATION PTY LTD.

Turner, W. C. (2007). ENERGY MANAGEMENT HANDBOOK (Vol. 6). Lilburn: The Fairmont Press.

WRIGHT, J. (2008). Electronic Heating Equipment. Washington: Sumner.

Yaseen, B. (2008). Energy efficiency improvement and cost saving measures in some different industries in Palestine. Nablus.

zytemp. (2014, may 4). TCT032/TCT012/TCT013. Retrieved from Zytemp: http://www.zytemp.com/products/tct013.asp

# Appendices

## Appendix 1: Electrical bill of the steel tubes and profile factory

Table A-1: electrical bill of the factory

| Month | Electric bill (Nis) | Electric bill ($) | Energy consumption (kWh) |
| --- | --- | --- | --- |
| January | 19,935 | 5,522.00 | 31,998.39 |
| February | 15,773 | 4,369.12 | 25,317.82 |
| March | 25,106 | 6,954.36 | 40,298.56 |
| April | 18,887 | 5,231.70 | 30,316.21 |
| May | 19,386 | 5,369.92 | 31,117.17 |
| June | 17,712 | 4,906.22 | 28,430.18 |
| July | 14,506 | 4,018.16 | 23,284.11 |
| August | 17,099 | 4,736.42 | 27,446.23 |
| September | 17,573 | 4,867.72 | 28,207.06 |
| October | 16,543 | 4,582.41 | 26,553.77 |
| November | 18,750 | 5,193.75 | 30,096.31 |
| December | 18,750 | 5,193.75 | 30,096.31 |
| Total | 220,020 | 60,945.54 | 353,162.12 |

## Appendix 2: Used standards

Table A-2: standard illumination levels

| Type of interior, task or activity | Standard Illumination (lm /m²) or lux |
| --- | --- |
| Open die forging | 200 |
| Drop forging | 300 |
| Welding | 300 |
| Rough and average machining: tolerances ≥ 0,1 mm | 300 |
| Precision machining; grinding: tolerances < 0,1 mm | 500 |
| Scribing; inspection | 750 |
| Wire and pipe drawing shops; cold forming | 300 |
| Plate machining: thickness ≥ 5 mm | 200 |
| Sheet metalwork: thickness < 5 mm | 300 |
| Tool making; cutting equipment manufacture | 750 |
| Assembly |  |
| Rough | 200 |
| Medium | 300 |
| Fine | 500 |
| precision | 750 |
| Galvanizing | 300 |
| Surface preparation and painting | 750 |
| Tool, template and jig making, precision mechanics, micromechanics | 1000 |

Table A-3: standard rated efficiency for the electrical motor

| Rated power (Kw) | Efficiency % |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Grade 1 |  |  | Grade 2 |  |  | Grade 3 |  |  |
|  | 2 poles | 4 poles | 6 poles | 2 poles | 4 poles | 6 poles | 2 poles | 4 poles | 6 poles |
| 0.75 | 84.9 | 85.6 | 83.1 | 80.7 | 82.5 | 78.9 | 77.4 | 79.6 | 57.9 |
| 1.1 | 86.7 | 87.4 | 84.1 | 82.7 | 84.1 | 81 | 79.6 | 81.4 | 78.1 |
| 1.5 | 87.5 | 88.1 | 86.2 | 84.2 | 85.3 | 82.5 | 81.3 | 82.5 | 79.8 |
| 2.2 | 89.1 | 89.7 | 87.1 | 85.9 | 86.7 | 84.3 | 83.2 | 84.3 | 81.8 |
| 3 | 89.7 | 90.3 | 88.7 | 87.1 | 87.7 | 85.6 | 84.6 | 85.5 | 83.3 |
| 4 | 90.3 | 90.9 | 89.7 | 88.1 | 88.6 | 86.8 | 85.8 | 86.6 | 84.6 |
| 5.5 | 91.5 | 92.1 | 89.5 | 89.2 | 89.6 | 88 | 87 | 87.7 | 88 |
| 7.5 | 92.1 | 92.6 | 90.2 | 90.1 | 90.4 | 89.1 | 88.1 | 88.7 | 87.2 |
| 11 | 93 | 93.6 | 91.5 | 91.2 | 91.4 | 90.3 | 89.4 | 89.8 | 88.7 |
| 15 | 93.4 | 4 | 92.5 | 91.9 | 92.1 | 91.2 | 90.3 | 90.6 | 89.7 |
| 18.5 | 93.8 | 94.3 | 93.1 | 92.4 | 92.6 | 91.7 | 90.9 | 91.2 | 90.4 |
| 22 | 94.4 | 94.7 | 93.9 | 92.7 | 93 | 92.2 | 91.3 | 91.6 | 90.9 |
| 30 | 94.5 | 95 | 94.3 | 93.3 | 93.6 | 92.9 | 92 | 92.3 | 91.7 |
| 37 | 94.8 | 95.3 | 94.6 | 93.7 | 93.9 | 93.3 | 92.5 | 92.7 | 92.2 |
| 45 | 95.1 | 95.6 | 94.9 | 94 | 94.2 | 93.7 | 92.9 | 93.1 | 92.7 |
| 55 | 95.4 | 95.8 | 95.2 | 94.3 | 94.6 | 94.1 | 93.2 | 93.5 | 93.1 |
| 75 | 95.6 | 96 | 95.4 | 94.7 | 95 | 94.6 | 93.8 | 94 | 93.7 |
| 90 | 95.8 | 95.2 | 95.6 | 95 | 95.2 | 94.9 | 94.1 | 94.2 | 94 |
| 110 | 96 | 96.4 | 95.6 | 95.2 | 95.4 | 95.1 | 94.3 | 94.5 | 94.3 |
| 132 | 96 | 96.5 | 95.8 | 95.4 | 95.6 | 95.4 | 94.6 | 94.7 | 94.6 |
| 160 | 96.2 | 96.5 | 96 | 95.6 | 95.8 | 95.6 | 94.8 | 94.9 | 94.8 |
| 200 | 96.3 | 96.6 | 96.1 | 95.8 | 96 | 95.8 | 95 | 95.1 | 95 |
| 250 | 96.4 | 96.7 | 961 | 95.8 | 96 | 95.8 | 95 | 95.1 | 95 |
| 315 | 96.5 | 96.8 | 96.1 | 95.8 | 96 | 95.8 | 95 | 95.1 | 95 |
| 355-375 | 96.6 | 96.8 | 96.1 | 95.8 | 96 | 95.8 | 95 | 95.1 | 95 |

## Appendix 3: Name Plate data for the electrical motor

Table A-4: Name Plate data of the electrical motors

| Motor # | Power- rated (kW) | F.L current- rated (A) | Voltage- rated (V) | RPM | IP | EFF,rated | PF,rated |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 1/1PL | 3.70 | 8.40 | 380.00 | 1440.00 |  | 83.00% | 0.81 |
| 2/1PL | 5.50 | 12.00 | 380.00 | 1440.00 | 55.00 | 85.70% | 0.81 |
| Fan 1/1PL | 3.00 | 6.30 | 380.00 | 2280.00 |  | 83.50% | 0.84 |
| 3/1PL | 4.00 | 8.80 | 380.00 | 1440.00 |  | 84.60% | 0.82 |
| 4/1PL | 4.00 | 8.80 | 380.00 | 1440.00 |  | 84.60% | 0.82 |
| Fan 2/1PL | 3.00 | 6.30 | 380.00 | 2280.00 |  | 83.50% | 0.87 |
| C/1PL | 11.00 | 22.60 | 380.00 | 1460.00 | 44.00 | 85.00% | 0.87 |
| 1/2PL | 11.00 | 22.60 | 380.00 | 1460.00 | 44.00 | 88.00% | 0.84 |
| 2/2PL | 15.00 | 29.90 | 380.00 | 1450.00 | 44.00 | 90.00% | 0.85 |
| pump1 /2PL | 7.50 | 15.00 | 380.00 | 2900.00 |  | 87.00% | 0.87 |
| pump 2/2PL | 1.50 | 5.44 | 380.00 | 2800.00 |  | 78.50% | 0.82 |
| A/2PL | 90.00 |  |  |  |  | 82.98% | 0.87 |
| B/2PL | 90.00 |  |  |  |  | 82.98% | 0.74 |

## Appendix 4: Clamp meter measurements

Table A-5: clamp Meter Measurement

| Motor # | Line A- Current (A) | Line B- Current (A) | Line C- Current (A) | Current (A)- R.M. S | Line AB- Voltage (V) | Line BC- Voltage (V) | Line AC- Voltage (V) | Voltage (V)- R.M. S |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1/1PL | 6.70 | 6.30 | 6.50 | 6.50 |  |  |  | 388.00 |
| 2/1PL | 5.00 | 4.88 | 4.80 | 4.89 |  |  |  | 388.00 |
| Fan 1/1PL | 3.10 | 3.40 | 3.30 | 3.27 |  |  |  | 388.00 |
| 3/1PL | 4.45 | 3.90 | 4.00 | 4.12 |  |  |  | 388.00 |
| 4/1PL | 4.45 | 3.90 | 4.00 | 4.12 |  |  |  | 388.00 |
| Fan 2/1PL | 3.60 | 3.35 | 3.55 | 3.50 |  |  |  | 388.00 |
| C/1PL | 11.00 | 10.80 | 11.20 | 11.00 |  |  |  | 388.00 |
| 1/2PL | 12.90 | 12.30 | 12.00 | 12.40 | 414.00 | 409.00 | 410.00 | 411.00 |
| 2/2PL | 15.00 | 15.10 | 15.30 | 15.13 | 410.00 | 411.00 | 409.00 | 410.00 |
| pump1 /2PL | 10.10 | 10.00 | 9.00 | 9.70 | 405.00 | 405.00 | 406.00 | 405.33 |
| pump 2/2PL | 3.10 | 3.20 | 3.00 | 3.10 | 406.00 | 405.00 | 408.00 | 406.33 |
|  |  |  |  | 59.47 |  |  |  | 387.40 |
| A/2PL |  |  |  | 37.90 |  |  |  | 386.00 |

## Appendix 5: Power analyser measurements

Table A-6: power analyser measurements for motor A/2PL

| No. of reading | Time 16-4-2017 | Average kW | Average kVAR | Average kVA | Average current | Average voltage | Average PF | Load Factor % |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | 14:08:35 | 30.2 | 23.3 | 38.8 | 58.06666667 | 387.8061758 | 0.794333333 | 0.28582 |
| 2 | 14:08:40 | 31 | 23.6 | 39 | 56.1 | 387.5752357 | 0.804333333 | 0.279366 |
| 3 | 14:08:45 | 30.3 | 22.3 | 37.7 | 56.1 | 387.5752357 | 0.791333333 | 0.274756 |
| 4 | 14:08:50 | 29.8 | 23 | 37.6 | 54.46666667 | 387.4597657 | 0.809 | 0.272912 |
| 5 | 14:08:55 | 29.6 | 21.4 | 36.5 | 56.7 | 387.4597657 | 0.796 | 0.279366 |
| 6 | 14:09:00 | 30.3 | 22.9 | 38.1 | 55.9 | 387.6907058 | 0.780333333 | 0.270146 |
| 7 | 14:09:05 | 29.3 | 23.4 | 37.5 | 56.76666667 | 387.1133555 | 0.801 | 0.28121 |
| 8 | 14:09:10 | 30.5 | 22.7 | 38.1 | 57.4 | 387.4597657 | 0.812333333 | 0.288586 |
| 9 | 14:09:15 | 31.3 | 22.5 | 38.5 | 57.1 | 387.5175007 | 0.790333333 | 0.279366 |
| 10 | 14:09:20 | 30.3 | 23.4 | 38.3 | 57.56666667 | 387.3442956 | 0.794333333 | 0.283054 |
| 11 | 14:09:25 | 30.7 | 23.4 | 38.6 | 57.7 | 387.5175007 | 0.797 | 0.284898 |
| 12 | 14:09:30 | 30.9 | 23.2 | 38.7 | 56.23333333 | 387.3442956 | 0.816 | 0.283976 |
| 13 | 14:09:35 | 30.8 | 21.6 | 37.7 | 56.66666667 | 387.4020306 | 0.809333333 | 0.283976 |
| 14 | 14:09:40 | 30.8 | 22.2 | 38 | 50.93333333 | 386.8246804 | 0.844 | 0.265536 |
| 15 | 14:22:42 | 28.8 | 18.2 | 34.1 | 61.33333333 | 386.4205352 | 0.521 | 0.197308 |
| 16 | 14:22:47 | 21.4 | 34.9 | 41 | 59.6 | 384.6307493 | 0.594 | 0.217592 |
| 17 | 14:22:52 | 23.6 | 31.9 | 39.7 | 63.7 | 384.2266041 | 0.591666667 | 0.231422 |
| 18 | 14:22:57 | 25.1 | 34.1 | 42.4 | 63.4 | 384.1688691 | 0.611 | 0.236954 |
| 19 | 14:23:02 | 25.7 | 33.3 | 42.2 | 57.56666667 | 383.995664 | 0.805 | 0.284898 |
| 20 | 14:23:07 | 30.9 | 22.4 | 38.3 | 57.2 | 383.880194 | 0.811666667 | 0.284898 |
| 21 | 14:23:12 | 30.9 | 22.1 | 38 | 58.5 | 383.5337838 | 0.806666667 | 0.289508 |
| 22 | 14:23:17 | 31.4 | 22.8 | 38.9 | 59.1 | 384.3420742 | 0.801666667 | 0.291352 |
| 23 | 14:23:22 | 31.6 | 23.3 | 39.3 | 58.96666667 | 384.1111341 | 0.796666667 | 0.288586 |
| 24 | 14:23:27 | 31.3 | 23.5 | 39.2 | 59.66666667 | 383.7069889 | 0.806333333 | 0.29504 |
| 25 | 14:23:32 | 32 | 23.3 | 39.6 | 59.36666667 | 383.6492539 | 0.794666667 | 0.289508 |
| 26 | 14:23:37 | 31.4 | 23.8 | 39.4 | 57.33333333 | 385.5545098 | 0.783 | 0.2766 |
| 27 | 14:23:42 | 30 | 23.6 | 38.3 | 59.13333333 | 385.0348945 | 0.803 | 0.292274 |
| 28 | 14:23:47 | 31.7 | 23.4 | 39.4 | 59.83333333 | 385.958655 | 0.794 | 0.293196 |
| 29 | 14:23:52 | 31.8 | 24.1 | 40 | 59.83333333 | 385.6699798 | 0.804333333 | 0.296884 |
| 30 | 14:23:57 | 32.2 | 23.5 | 40 | 60.8 | 387.2288255 | 0.806333333 | 0.303338 |
| 31 | 14:24:02 | 32.9 | 24 | 40.8 | 61.13333333 | 387.2865606 | 0.800333333 | 0.302416 |
| 32 | 14:24:07 | 32.8 | 24.6 | 41 | 60.8 | 387.5752357 | 0.805333333 | 0.303338 |
| 33 | 14:24:12 | 32.9 | 24.1 | 40.8 | 61.86666667 | 387.1710905 | 0.795 | 0.30426 |
| 34 | 14:24:17 | 33 | 25.1 | 41.5 | 60.53333333 | 386.8824154 | 0.802666667 | 0.300572 |
| 35 | 14:24:22 | 32.6 | 24.1 | 40.6 | 62 | 387.4597657 | 0.806666667 | 0.309792 |
| 36 | 14:24:27 | 33.6 | 24.5 | 41.6 | 63.03333333 | 387.4020306 | 0.779666667 | 0.30426 |
| 37 | 14:24:32 | 33 | 26.3 | 42.3 | 60.13333333 | 387.2288255 | 0.797333333 | 0.296884 |
| 38 | 14:24:37 | 32.2 | 24.1 | 40.3 | 59.73333333 | 387.2865606 | 0.813 | 0.300572 |
| 39 | 14:24:42 | 32.6 | 23.3 | 40.1 | 61.5 | 387.3442956 | 0.794333333 | 0.302416 |
| 40 | 14:24:47 | 32.8 | 25 | 41.3 | 60.83333333 | 387.2865606 | 0.795333333 | 0.29965 |
| 41 | 14:24:52 | 32.5 | 24.6 | 40.8 | 59.46666667 | 387.1710905 | 0.8 | 0.294118 |
| 42 | 14:24:57 | 31.9 | 23.9 | 39.9 | 60.13333333 | 387.1710905 | 0.808333333 | 0.300572 |
| 43 | 14:25:02 | 32.6 | 23.7 | 40.3 | 56.7 | 387.1710905 | 0.791 | 0.277522 |
| 44 | 14:25:07 | 30.1 | 23.1 | 38 | 56.6 | 387.3442956 | 0.784 | 0.274756 |
| 45 | 14:25:12 | 29.8 | 23.5 | 38 | 55.93333333 | 387.3442956 | 0.804333333 | 0.278444 |
| 46 | 14:25:17 | 30.2 | 22.3 | 37.5 | 56.66666667 | 387.3442956 | 0.803333333 | 0.282132 |
| 47 | 14:25:22 | 30.6 | 22.3 | 38 | 58.43333333 | 387.4020306 | 0.803333333 | 0.29043 |
| 48 | 14:25:27 | 31.5 | 23.3 | 39.2 | 59.93333333 | 387.4597657 | 0.792333333 | 0.294118 |
| 49 | 14:25:32 | 31.9 | 24.3 | 40.2 | 59.76666667 | 387.3442956 | 0.802666667 | 0.296884 |
| 50 | 14:25:37 | 32.2 | 23.8 | 40.1 | 60.86666667 | 387.2865606 | 0.798 | 0.300572 |
| 51 | 14:25:42 | 32.6 | 24.5 | 40.8 | 60.26666667 | 387.3442956 | 0.798 | 0.297806 |
| 52 | 14:25:47 | 32.3 | 24.3 | 40.4 | 60.9 | 387.2288255 | 0.800333333 | 0.301494 |
| 53 | 14:25:52 | 32.7 | 24.4 | 40.8 | 61.33333333 | 387.0556205 | 0.8 | 0.303338 |
| 54 | 14:25:57 | 32.9 | 24.7 | 41.1 | 62 | 386.9978854 | 0.788666667 | 0.302416 |
| 55 | 14:26:02 | 32.8 | 25.4 | 41.5 | 62.1 | 387.2865606 | 0.786666667 | 0.302416 |
| 56 | 14:26:07 | 32.8 | 25.6 | 41.6 | 61 | 386.9978854 | 0.797 | 0.300572 |
| 57 | 14:26:12 | 32.6 | 24.6 | 40.9 | 62.26666667 | 386.8824154 | 0.780666667 | 0.300572 |
| 58 | 14:26:17 | 32.6 | 26 | 41.7 | 60.33333333 | 387.0556205 | 0.798333333 | 0.297806 |
| 59 | 14:26:22 | 32.3 | 24.4 | 40.4 | 61 | 386.9978854 | 0.804333333 | 0.303338 |
| 60 | 14:26:27 | 32.9 | 24.2 | 40.9 | 61.36666667 | 387.4020306 | 0.799666667 | 0.303338 |
| 61 | 14:26:32 | 32.9 | 24.8 | 41.2 | 60.83333333 | 387.8061758 | 0.797 | 0.300572 |
| 62 | 14:26:37 | 32.6 | 24.5 | 40.9 | 60.73333333 | 387.4597657 | 0.787 | 0.295962 |
| 63 | 14:26:42 | 32.1 | 25 | 40.8 | 60.16666667 | 387.6329707 | 0.804 | 0.29965 |
| 64 | 14:26:47 | 32.5 | 23.9 | 40.4 | 61.5 | 387.4020306 | 0.777333333 | 0.295962 |
| 65 | 14:26:52 | 32.1 | 25.8 | 41.3 | 61.16666667 | 387.4597657 | 0.794 | 0.300572 |
| 66 | 14:26:57 | 32.6 | 24.9 | 41 | 60.33333333 | 387.6907058 | 0.801666667 | 0.29965 |
| 67 | 14:27:02 | 32.5 | 24.1 | 40.5 | 61.16666667 | 387.6907058 | 0.788666667 | 0.298728 |
| 68 | 14:27:07 | 32.4 | 25.2 | 41.1 | 61.46666667 | 387.8061758 | 0.787 | 0.29965 |
| 69 | 14:27:12 | 32.5 | 25.4 | 41.3 | 61.2 | 387.8061758 | 0.782666667 | 0.296884 |
| 70 | 14:27:17 | 32.2 | 25.4 | 41.1 | 60.86666667 | 387.5752357 | 0.783333333 | 0.29504 |
| 71 | 14:27:22 | 32 | 25.3 | 40.8 | 60.36666667 | 387.6329707 | 0.784 | 0.293196 |
| 72 | 14:27:27 | 31.8 | 25.1 | 40.5 | 59.33333333 | 387.8639108 | 0.789333333 | 0.29043 |
| 73 | 14:27:32 | 31.5 | 24.3 | 39.9 | 60 | 387.9216459 | 0.793333333 | 0.29504 |
| 74 | 14:27:37 | 32 | 24.4 | 40.3 | 59.46666667 | 387.8061758 | 0.793333333 | 0.292274 |
| 75 | 14:27:42 | 31.7 | 24.1 | 39.9 | 58.83333333 | 388.3835261 | 0.790333333 | 0.288586 |
| 76 | 14:27:47 | 31.3 | 24.1 | 39.6 | 58.56666667 | 387.9793809 | 0.798333333 | 0.289508 |
| 77 | 14:27:52 | 31.4 | 23.8 | 39.3 | 59.1 | 387.9216459 | 0.797666667 | 0.292274 |
| 78 | 14:27:57 | 31.7 | 23.9 | 39.7 | 59.76666667 | 387.4020306 | 0.782333333 | 0.289508 |
| 79 | 14:28:02 | 31.4 | 24.8 | 40.1 | 58.86666667 | 387.7484408 | 0.791 | 0.288586 |
| 80 | 14:28:07 | 31.3 | 24 | 39.5 | 55.46666667 | 387.8639108 | 0.81 | 0.278444 |
| 81 | 14:28:12 | 30.2 | 21.7 | 37.3 | 58.06666667 | 387.5175007 | 0.773666667 | 0.278444 |
| 82 | 14:28:17 | 30.2 | 24.5 | 39 | 57.66666667 | 387.4020306 | 0.783 | 0.279366 |
| 83 | 14:28:22 | 30.3 | 24 | 38.7 | 57.33333333 | 388.152586 | 0.798666667 | 0.283976 |
| 84 | 14:28:27 | 30.8 | 23.2 | 38.5 | 57.5 | 387.8061758 | 0.812666667 | 0.289508 |
| 85 | 14:28:32 | 31.4 | 22.4 | 38.6 | 58.56666667 | 388.210321 | 0.796333333 | 0.289508 |
| 86 | 14:28:37 | 31.4 | 23.6 | 39.4 | 57.33333333 | 388.0948509 | 0.807 | 0.286742 |
| 87 | 14:28:42 | 31.1 | 22.6 | 38.5 | 59.46666667 | 387.8061758 | 0.780333333 | 0.287664 |
| 88 | 14:28:47 | 31.2 | 24.8 | 39.9 | 58.86666667 | 387.9793809 | 0.799333333 | 0.291352 |
| 89 | 14:28:52 | 31.6 | 23.8 | 39.5 | 59.3 | 387.6329707 | 0.775666667 | 0.284898 |
| 90 | 14:28:57 | 30.9 | 25.1 | 39.8 | 58.4 | 387.5175007 | 0.809333333 | 0.292274 |
| 91 | 14:29:02 | 31.7 | 23 | 39.2 | 59.76666667 | 387.5752357 | 0.784333333 | 0.29043 |
| 92 | 14:29:07 | 31.5 | 24.6 | 40.1 | 58.56666667 | 387.8639108 | 0.792333333 | 0.287664 |
| 93 | 14:29:12 | 31.2 | 23.9 | 39.3 | 57.83333333 | 387.4597657 | 0.795666667 | 0.284898 |
| 94 | 14:29:17 | 30.9 | 23.4 | 38.8 | 57.73333333 | 387.8639108 | 0.800666667 | 0.286742 |
| 95 | 14:29:22 | 31.1 | 23 | 38.8 | 59.76666667 | 387.4597657 | 0.777333333 | 0.287664 |
| 96 | 14:29:27 | 31.2 | 25.2 | 40.1 | 58.93333333 | 387.5752357 | 0.780666667 | 0.284898 |
| 97 | 14:29:32 | 30.9 | 24.6 | 39.6 | 57.4 | 387.8061758 | 0.814 | 0.289508 |
| 98 | 14:29:37 | 31.4 | 22.3 | 38.5 | 60.86666667 | 387.3442956 | 0.790666667 | 0.297806 |
| 99 | 14:29:42 | 32.3 | 24.9 | 40.8 | 59.53333333 | 387.8061758 | 0.789666667 | 0.291352 |
| 100 | 14:29:47 | 31.6 | 24.4 | 40 | 59.53333333 | 387.6907058 | 0.802666667 | 0.295962 |
| 101 | 14:29:52 | 32.1 | 23.8 | 40 | 60 | 387.5175007 | 0.809666667 | 0.300572 |
| 102 | 14:29:57 | 32.6 | 23.6 | 40.3 | 60.13333333 | 387.5752357 | 0.802333333 | 0.298728 |
| 103 | 14:30:02 | 32.4 | 24 | 40.4 | 60.83333333 | 387.6907058 | 0.777333333 | 0.293196 |
| 104 | 14:30:07 | 31.8 | 25.5 | 40.8 | 60.8 | 387.8061758 | 0.776 | 0.292274 |
| 105 | 14:30:12 | 31.7 | 25.7 | 40.8 | 59.8 | 387.6907058 | 0.799 | 0.295962 |
| 106 | 14:30:17 | 32.1 | 24.1 | 40.1 | 60.16666667 | 387.3442956 | 0.782333333 | 0.291352 |
| 107 | 14:30:22 | 31.6 | 24.9 | 40.4 | 58.56666667 | 387.5175007 | 0.790333333 | 0.286742 |
| 108 | 14:30:27 | 31.1 | 23.9 | 39.3 | 58.13333333 | 387.5752357 | 0.809666667 | 0.291352 |
| 109 | 14:30:32 | 31.6 | 22.9 | 39 | 60.46666667 | 388.0371159 | 0.762 | 0.28582 |
| 110 | 14:30:37 | 31 | 26.1 | 40.6 | 59.06666667 | 388.6144662 | 0.781333333 | 0.286742 |
| 111 | 14:30:42 | 31.1 | 24.7 | 39.7 | 57.83333333 | 388.268056 | 0.797333333 | 0.28582 |
| 112 | 14:30:47 | 31 | 23.5 | 38.9 | 58.16666667 | 388.268056 | 0.795333333 | 0.286742 |
| 113 | 14:30:52 | 31.1 | 23.7 | 39.1 | 57.8 | 388.4412611 | 0.786333333 | 0.282132 |
| 114 | 14:30:57 | 30.6 | 24 | 38.9 | 57.96666667 | 388.268056 | 0.784333333 | 0.282132 |
| 115 | 14:31:02 | 30.6 | 24.1 | 39 | 59.6 | 388.6144662 | 0.794333333 | 0.294118 |
| 116 | 14:31:07 | 31.9 | 24.2 | 40.1 | 60.43333333 | 388.4989961 | 0.779333333 | 0.292274 |
| 117 | 14:31:12 | 31.7 | 25.4 | 40.7 | 58.86666667 | 388.4989961 | 0.776666667 | 0.283976 |
| 118 | 14:31:17 | 30.8 | 24.8 | 39.6 | 58.56666667 | 388.210321 | 0.809666667 | 0.294118 |
| 119 | 14:31:22 | 31.9 | 23 | 39.4 | 60.03333333 | 387.9793809 | 0.801 | 0.297806 |
| 120 | 14:31:27 | 32.3 | 24.1 | 40.3 | 60.53333333 | 388.0371159 | 0.783 | 0.294118 |
| 121 | 14:31:32 | 31.9 | 25.1 | 40.7 | 59.33333333 | 388.152586 | 0.799666667 | 0.294118 |
| 122 | 14:31:37 | 31.9 | 24 | 39.9 | 58.86666667 | 388.210321 | 0.795 | 0.29043 |
| 123 | 14:31:42 | 31.5 | 23.8 | 39.6 | 59.6 | 388.268056 | 0.795 | 0.294118 |
| 124 | 14:31:47 | 31.9 | 24.2 | 40.1 | 58 | 387.9216459 | 0.782333333 | 0.28121 |
| 125 | 14:31:52 | 30.5 | 24.2 | 39 | 57.4 | 388.152586 | 0.802666667 | 0.28582 |
| 126 | 14:31:57 | 31 | 22.9 | 38.6 | 58 | 388.268056 | 0.796666667 | 0.286742 |
| 127 | 14:32:02 | 31.1 | 23.5 | 39 | 59.46666667 | 388.3257911 | 0.782666667 | 0.288586 |
| 128 | 14:32:07 | 31.3 | 24.8 | 40 | 58.83333333 | 388.4412611 | 0.780666667 | 0.284898 |
| 129 | 14:32:12 | 30.9 | 24.8 | 39.6 | 58.7 | 388.268056 | 0.802666667 | 0.292274 |
| 130 | 14:32:17 | 31.7 | 23.5 | 39.5 | 59.53333333 | 388.268056 | 0.799 | 0.29504 |
| 131 | 14:32:22 | 32 | 23.9 | 40 | 60.76666667 | 388.268056 | 0.783 | 0.29504 |
| 132 | 14:32:27 | 32 | 25.4 | 40.9 | 59.83333333 | 388.3835261 | 0.789333333 | 0.293196 |
| 133 | 14:32:32 | 31.8 | 24.6 | 40.2 | 58.73333333 | 388.4989961 | 0.804666667 | 0.293196 |
| 134 | 14:32:37 | 31.8 | 23.5 | 39.5 | 60.66666667 | 388.210321 | 0.786666667 | 0.295962 |
| 135 | 14:32:42 | 32.1 | 25.1 | 40.8 | 60.23333333 | 388.3257911 | 0.789333333 | 0.29504 |
| 136 | 14:32:47 | 32 | 24.9 | 40.5 | 59.43333333 | 388.3835261 | 0.807 | 0.297806 |
| 137 | 14:32:52 | 32.3 | 23.4 | 40 | 59.7 | 388.4412611 | 0.810666667 | 0.300572 |
| 138 | 14:32:57 | 32.6 | 23.4 | 40.2 | 60.4 | 388.152586 | 0.792666667 | 0.296884 |
| 139 | 14:33:02 | 32.2 | 24.6 | 40.6 | 58.56666667 | 388.3257911 | 0.789333333 | 0.286742 |
| 140 | 14:33:07 | 31.1 | 24.1 | 39.4 | 59.6 | 388.7299362 | 0.789 | 0.292274 |
| 141 | 14:33:12 | 31.7 | 24.5 | 40.1 | 59.63333333 | 388.7876713 | 0.798666667 | 0.295962 |
| 142 | 14:33:17 | 32.1 | 24 | 40.2 | 65.9 | 387.8061758 | 0.767333333 | 0.31348 |
| 143 | 14:33:22 | 34 | 28.4 | 44.3 | 75.46666667 | 387.4020306 | 0.767333333 | 0.358658 |
| 144 | 14:33:27 | 38.9 | 32.4 | 50.6 | 70.56666667 | 386.8824154 | 0.748333333 | 0.326388 |
| 145 | 14:33:32 | 35.4 | 31.2 | 47.3 | 76.53333333 | 386.4205352 | 0.794 | 0.375254 |
| 146 | 14:33:37 | 40.7 | 31 | 51.2 | 60.3 | 386.7092103 | 0.779 | 0.29043 |
| 147 | 14:33:42 | 31.5 | 25.3 | 40.4 | 58.46666667 | 386.7092103 | 0.788 | 0.284898 |
| 148 | 14:33:47 | 30.9 | 23.9 | 39.1 | 56.5 | 386.4205352 | 0.802333333 | 0.280288 |
| 149 | 14:33:52 | 30.4 | 22.4 | 37.8 | 55.83333333 | 386.4205352 | 0.783 | 0.270146 |
| 150 | 14:33:57 | 29.3 | 23.1 | 37.4 | 56.76666667 | 387.1133555 | 0.79 | 0.277522 |
| 151 | 14:34:02 | 30.1 | 23.2 | 38.1 | 57.8 | 387.3442956 | 0.763 | 0.272912 |
| 152 | 14:34:07 | 29.6 | 25 | 38.8 | 61.16666667 | 386.9978854 | 0.775333333 | 0.293196 |
| 153 | 14:34:12 | 31.8 | 25.8 | 41 | 62.4 | 387.2288255 | 0.769 | 0.296884 |
| 154 | 14:34:17 | 32.2 | 26.7 | 41.8 | 60.46666667 | 387.1710905 | 0.766333333 | 0.286742 |
| 155 | 14:34:22 | 31.1 | 26 | 40.5 | 60.96666667 | 387.2865606 | 0.774333333 | 0.292274 |
| 156 | 14:34:27 | 31.7 | 25.7 | 40.9 | 60.26666667 | 387.6329707 | 0.777666667 | 0.29043 |
| 157 | 14:34:32 | 31.5 | 25.3 | 40.5 | 60.4 | 387.8061758 | 0.793 | 0.296884 |
| 158 | 14:34:37 | 32.2 | 24.6 | 40.6 | 60.83333333 | 387.7484408 | 0.782666667 | 0.29504 |
| 159 | 14:34:42 | 32 | 25.3 | 40.8 | 60.7 | 387.9216459 | 0.769666667 | 0.289508 |
| 160 | 14:34:47 | 31.4 | 26 | 40.8 | 60.5 | 387.6907058 | 0.769666667 | 0.288586 |
| 161 | 14:34:52 | 31.3 | 25.9 | 40.6 | 61.23333333 | 387.5752357 | 0.782666667 | 0.296884 |
| 162 | 14:34:57 | 32.2 | 25.4 | 41.1 | 62.2 | 387.1710905 | 0.770666667 | 0.296884 |
| 163 | 14:35:02 | 32.2 | 26.4 | 41.7 | 62.53333333 | 387.4020306 | 0.778 | 0.301494 |

Table A-7: power analyser measurements for motor B/2L

| No. of reading | Time 16-4-2017 | Average kW | Average kVAR | Average kVA | Average current | Average voltage | Average PF | Load Factor % |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | 13:45:23 | 12.6 | 16.7 | 19.2 | 29.86666667 | 389.1340814 | 0.581 | 0.107874 |
| 2 | 13:45:28 | 11.7 | 16.3 | 20.1 | 27.5 | 389.4227566 | 0.593 | 0.10142 |
| 3 | 13:45:33 | 11 | 14.9 | 18.5 | 23.3 | 389.8269018 | 0.572333333 | 0.08298 |
| 4 | 13:45:38 | 9 | 12.8 | 15.7 | 24.76666667 | 389.6536967 | 0.557 | 0.085746 |
| 5 | 13:45:43 | 9.3 | 13.9 | 16.7 | 23.13333333 | 389.6536967 | 0.563 | 0.081136 |
| 6 | 13:45:48 | 8.8 | 12.9 | 15.6 | 26.33333333 | 389.5959616 | 0.556666667 | 0.091278 |
| 7 | 13:45:53 | 9.9 | 14.8 | 17.8 | 25.26666667 | 389.5959616 | 0.569 | 0.089434 |
| 8 | 13:45:58 | 9.7 | 14 | 17 | 27.23333333 | 389.4227566 | 0.562333333 | 0.094966 |
| 9 | 13:46:03 | 10.3 | 15.2 | 18.4 | 28.1 | 389.3650215 | 0.580666667 | 0.10142 |
| 10 | 13:46:08 | 11 | 15.4 | 18.9 | 29.63333333 | 389.3072865 | 0.580666667 | 0.106952 |
| 11 | 13:46:13 | 11.6 | 16.3 | 20 | 29.06666667 | 389.4804916 | 0.565666667 | 0.102342 |
| 12 | 13:46:18 | 11.1 | 16.2 | 19.6 | 28.8 | 389.4227566 | 0.568 | 0.10142 |
| 13 | 13:46:23 | 11 | 16 | 19.4 | 32.26666667 | 389.1340814 | 0.597 | 0.11986 |
| 14 | 13:46:28 | 13 | 17.4 | 21.7 | 30.1 | 389.0186114 | 0.597333333 | 0.111562 |
| 15 | 13:46:33 | 12.1 | 16.2 | 20.3 | 31.46666667 | 389.2495515 | 0.59 | 0.11525 |
| 16 | 13:46:38 | 12.5 | 17.1 | 21.2 | 33.66666667 | 389.5959616 | 0.589666667 | 0.123548 |
| 17 | 13:46:43 | 13.4 | 18.3 | 22.7 | 35.8 | 389.6536967 | 0.600666667 | 0.13369 |
| 18 | 13:46:48 | 14.5 | 19.3 | 24.2 | 38.83333333 | 389.2495515 | 0.595666667 | 0.143832 |
| 19 | 13:46:53 | 15.6 | 21 | 26.2 | 37.76666667 | 389.2495515 | 0.605333333 | 0.141988 |
| 20 | 13:46:58 | 15.4 | 20.3 | 25.5 | 38.43333333 | 389.5959616 | 0.601333333 | 0.143832 |
| 21 | 13:47:03 | 15.6 | 20.7 | 25.9 | 40.9 | 389.0763464 | 0.577333333 | 0.146598 |
| 22 | 13:47:08 | 15.9 | 22.5 | 27.6 | 41.4 | 389.4227566 | 0.590666667 | 0.15213 |
| 23 | 13:47:13 | 16.5 | 22.5 | 27.9 | 43.23333333 | 388.6722012 | 0.590666667 | 0.158584 |
| 24 | 13:47:18 | 17.2 | 23.5 | 29.1 | 42.9 | 386.7092103 | 0.621666667 | 0.164116 |
| 25 | 13:47:23 | 17.8 | 22.6 | 28.7 | 41.16666667 | 385.9009199 | 0.71 | 0.180712 |
| 26 | 13:47:28 | 19.6 | 19.2 | 27.5 | 45.5 | 385.7277148 | 0.716 | 0.200996 |
| 27 | 13:47:33 | 21.8 | 21 | 30.4 | 40.5 | 386.074125 | 0.740666667 | 0.185322 |
| 28 | 13:47:38 | 20.1 | 18.1 | 27.1 | 44.96666667 | 386.01639 | 0.723333333 | 0.200996 |
| 29 | 13:47:43 | 21.8 | 20.7 | 30.1 | 46.76666667 | 385.958655 | 0.721 | 0.208372 |
| 30 | 13:47:48 | 22.6 | 21.5 | 31.3 | 44.06666667 | 386.1895951 | 0.745 | 0.20284 |
| 31 | 13:47:53 | 22 | 19.6 | 29.5 | 41.63333333 | 386.7669453 | 0.754666667 | 0.194542 |
| 32 | 13:47:58 | 21.1 | 18.1 | 27.9 | 40.16666667 | 386.7092103 | 0.741666667 | 0.1844 |
| 33 | 13:48:03 | 20 | 17.9 | 26.9 | 38.2 | 386.9401504 | 0.742 | 0.17518 |
| 34 | 13:48:08 | 19 | 17 | 25.6 | 38.2 | 386.9401504 | 0.752333333 | 0.177946 |
| 35 | 13:48:13 | 19.3 | 16.8 | 25.6 | 36.13333333 | 386.8824154 | 0.755 | 0.168726 |
| 36 | 13:48:18 | 18.3 | 15.8 | 24.2 | 36.76666667 | 386.9978854 | 0.729666667 | 0.16596 |
| 37 | 13:48:23 | 18 | 16.8 | 24.6 | 37.3 | 387.2865606 | 0.73 | 0.168726 |
| 38 | 13:48:28 | 18.3 | 17 | 25 | 37.8 | 387.2865606 | 0.728333333 | 0.17057 |
| 39 | 13:48:33 | 18.5 | 17.3 | 25.3 | 36.66666667 | 386.8824154 | 0.751666667 | 0.17057 |
| 40 | 13:48:38 | 18.5 | 16.1 | 24.6 | 36.43333333 | 386.8824154 | 0.723666667 | 0.163194 |
| 41 | 13:48:43 | 17.7 | 16.7 | 24.4 | 35.9 | 386.7092103 | 0.727333333 | 0.16135 |
| 42 | 13:48:48 | 17.5 | 16.5 | 24 | 36.56666667 | 386.9978854 | 0.745333333 | 0.168726 |
| 43 | 13:48:53 | 18.3 | 16.1 | 24.5 | 36.33333333 | 386.7669453 | 0.746666667 | 0.167804 |
| 44 | 13:48:58 | 18.2 | 16.1 | 24.3 | 35.3 | 386.8824154 | 0.772 | 0.168726 |
| 45 | 13:49:03 | 18.3 | 14.9 | 23.6 | 36.1 | 387.4597657 | 0.746333333 | 0.166882 |
| 46 | 13:49:08 | 18.1 | 16 | 24.2 | 37.86666667 | 387.2865606 | 0.723333333 | 0.169648 |
| 47 | 13:49:13 | 18.4 | 17.5 | 25.4 | 37.6 | 386.8824154 | 0.725 | 0.168726 |
| 48 | 13:49:18 | 18.3 | 17.2 | 25.2 | 37.03333333 | 387.3442956 | 0.739333333 | 0.169648 |
| 49 | 13:49:23 | 18.4 | 16.5 | 24.8 | 36.06666667 | 386.9401504 | 0.743666667 | 0.16596 |
| 50 | 13:49:28 | 18 | 16.1 | 24.2 | 37.3 | 386.7092103 | 0.746666667 | 0.172414 |
| 51 | 13:49:33 | 18.7 | 16.4 | 25 | 38.1 | 386.1895951 | 0.701333333 | 0.165038 |
| 52 | 13:49:38 | 17.9 | 18.1 | 25.5 | 37.1 | 386.2473301 | 0.732333333 | 0.167804 |
| 53 | 13:49:43 | 18.2 | 16.8 | 24.8 | 37.73333333 | 386.3050651 | 0.736333333 | 0.171492 |
| 54 | 13:49:48 | 18.6 | 17 | 25.2 | 35.96666667 | 386.3050651 | 0.734666667 | 0.163194 |
| 55 | 13:49:53 | 17.7 | 16.2 | 24.1 | 34.76666667 | 386.01639 | 0.761 | 0.163194 |
| 56 | 13:49:58 | 17.7 | 15 | 23.2 | 35.53333333 | 385.958655 | 0.74 | 0.162272 |
| 57 | 13:50:03 | 17.6 | 15.9 | 23.7 | 38.06666667 | 386.13186 | 0.740666667 | 0.174258 |
| 58 | 13:50:08 | 18.9 | 17 | 25.5 | 37.9 | 386.074125 | 0.74 | 0.173336 |
| 59 | 13:50:13 | 18.8 | 16.9 | 25.3 | 38.33333333 | 386.2473301 | 0.743333333 | 0.176102 |
| 60 | 13:50:18 | 19.1 | 17 | 25.6 | 38.43333333 | 386.3050651 | 0.714 | 0.169648 |
| 61 | 13:50:23 | 18.4 | 18 | 25.7 | 41.26666667 | 387.4597657 | 0.728333333 | 0.186244 |
| 62 | 13:50:28 | 20.2 | 18.9 | 27.7 | 40.6 | 387.8639108 | 0.731666667 | 0.1844 |
| 63 | 13:50:33 | 20 | 18.5 | 27.3 | 37.26666667 | 387.8061758 | 0.738333333 | 0.17057 |
| 64 | 13:50:38 | 18.5 | 16.8 | 25 | 36.13333333 | 387.6329707 | 0.749 | 0.167804 |
| 65 | 13:50:43 | 18.2 | 16 | 24.3 | 36 | 387.5752357 | 0.728 | 0.162272 |
| 66 | 13:50:48 | 17.6 | 16.6 | 24.2 | 35.13333333 | 387.2865606 | 0.78 | 0.169648 |
| 67 | 13:50:53 | 18.4 | 14.7 | 23.6 | 36.73333333 | 387.4597657 | 0.782333333 | 0.177946 |
| 68 | 13:50:58 | 19.3 | 15.3 | 24.6 | 36.76666667 | 387.5175007 | 0.777666667 | 0.177024 |
| 69 | 13:51:03 | 19.2 | 15.4 | 24.7 | 36.76666667 | 387.5752357 | 0.769666667 | 0.17518 |
| 70 | 13:51:08 | 19 | 15.6 | 24.7 | 36.63333333 | 387.6907058 | 0.775333333 | 0.176102 |
| 71 | 13:51:13 | 19.1 | 15.4 | 24.6 | 40.53333333 | 386.8824154 | 0.740666667 | 0.185322 |
| 72 | 13:51:18 | 20.1 | 18.3 | 27.2 | 38.9 | 386.4205352 | 0.767 | 0.1844 |
| 73 | 13:51:23 | 20 | 16.6 | 26 | 36.5 | 386.1895951 | 0.778 | 0.17518 |
| 74 | 13:51:28 | 19 | 15.3 | 24.4 | 37.93333333 | 386.2473301 | 0.755666667 | 0.177024 |
| 75 | 13:51:33 | 19.2 | 16.5 | 25.4 | 39.7 | 386.3050651 | 0.744666667 | 0.182556 |
| 76 | 13:51:38 | 19.8 | 17.7 | 26.6 | 35.3 | 386.8246804 | 0.786333333 | 0.171492 |
| 77 | 13:51:43 | 18.6 | 14.6 | 23.6 | 39.36666667 | 386.7092103 | 0.746 | 0.181634 |
| 78 | 13:51:48 | 19.7 | 17.5 | 26.4 | 37.7 | 386.1895951 | 0.772333333 | 0.17979 |
| 79 | 13:51:53 | 19.5 | 16 | 25.2 | 39.8 | 386.13186 | 0.743 | 0.182556 |
| 80 | 13:51:58 | 19.8 | 17.7 | 26.6 | 40.5 | 386.2473301 | 0.734 | 0.183478 |
| 81 | 13:52:03 | 19.9 | 18.4 | 27.1 | 42.7 | 385.9009199 | 0.721333333 | 0.189932 |
| 82 | 13:52:08 | 20.6 | 19.8 | 28.5 | 43.46666667 | 386.074125 | 0.711333333 | 0.190854 |
| 83 | 13:52:13 | 20.7 | 20.4 | 29.1 | 43.76666667 | 386.074125 | 0.725666667 | 0.196386 |
| 84 | 13:52:18 | 21.3 | 20.1 | 29.3 | 39.66666667 | 386.6514753 | 0.747666667 | 0.183478 |
| 85 | 13:52:23 | 19.9 | 17.5 | 26.6 | 39 | 386.5937402 | 0.753666667 | 0.181634 |
| 86 | 13:52:28 | 19.7 | 17.1 | 26.1 | 41.4 | 386.2473301 | 0.731333333 | 0.187166 |
| 87 | 13:52:33 | 20.3 | 18.8 | 27.7 | 38.3 | 386.13186 | 0.771 | 0.182556 |
| 88 | 13:52:38 | 19.8 | 16.2 | 25.6 | 36.6 | 386.2473301 | 0.734333333 | 0.16596 |
| 89 | 13:52:43 | 18 | 16.6 | 24.5 | 36.73333333 | 386.01639 | 0.744666667 | 0.168726 |
| 90 | 13:52:48 | 18.3 | 16.4 | 24.5 | 37.1 | 385.9009199 | 0.757333333 | 0.173336 |
| 91 | 13:52:53 | 18.8 | 16.1 | 24.8 | 37.03333333 | 385.5545098 | 0.774666667 | 0.177024 |
| 92 | 13:52:58 | 19.2 | 15.5 | 24.7 | 39.8 | 385.6699798 | 0.747 | 0.183478 |
| 93 | 13:53:03 | 19.9 | 17.5 | 26.6 | 39.93333333 | 385.7277148 | 0.748666667 | 0.1844 |
| 94 | 13:53:08 | 20 | 17.6 | 26.7 | 41.23333333 | 385.9009199 | 0.722333333 | 0.183478 |
| 95 | 13:53:13 | 19.9 | 19.1 | 27.6 | 39.2 | 385.7277148 | 0.754333333 | 0.182556 |
| 96 | 13:53:18 | 19.8 | 17.1 | 26.2 | 42.26666667 | 385.9009199 | 0.732666667 | 0.190854 |
| 97 | 13:53:23 | 20.7 | 19.3 | 28.2 | 41.36666667 | 385.7854499 | 0.746333333 | 0.190854 |
| 98 | 13:53:28 | 20.7 | 18.3 | 27.6 | 39.86666667 | 386.074125 | 0.737333333 | 0.181634 |
| 99 | 13:53:33 | 19.7 | 17.9 | 26.7 | 38.83333333 | 385.9009199 | 0.757 | 0.181634 |
| 100 | 13:53:38 | 19.7 | 16.9 | 25.9 | 40.86666667 | 386.1895951 | 0.756333333 | 0.190854 |
| 101 | 13:53:43 | 20.7 | 17.8 | 27.3 | 40.96666667 | 386.01639 | 0.740333333 | 0.187166 |
| 102 | 13:53:48 | 20.3 | 18.4 | 27.4 | 39.4 | 385.8431849 | 0.757333333 | 0.1844 |
| 103 | 13:53:53 | 20 | 17.1 | 26.3 | 41.4 | 385.6699798 | 0.736 | 0.188088 |
| 104 | 13:53:58 | 20.4 | 18.6 | 27.6 | 40 | 385.2658346 | 0.736666667 | 0.181634 |
| 105 | 13:54:03 | 19.7 | 18 | 26.7 | 38.33333333 | 385.3813047 | 0.752333333 | 0.177946 |
| 106 | 13:54:08 | 19.3 | 16.8 | 25.6 | 38.33333333 | 385.5545098 | 0.760666667 | 0.17979 |
| 107 | 13:54:13 | 19.5 | 16.6 | 25.6 | 37.36666667 | 385.3235697 | 0.769 | 0.177024 |
| 108 | 13:54:18 | 19.2 | 15.9 | 24.9 | 38.9 | 384.8616894 | 0.758 | 0.181634 |
| 109 | 13:54:23 | 19.7 | 16.8 | 25.9 | 37.36666667 | 385.0926295 | 0.761333333 | 0.17518 |
| 110 | 13:54:28 | 19 | 16.1 | 24.9 | 38.83333333 | 385.0926295 | 0.729 | 0.174258 |
| 111 | 13:54:33 | 18.9 | 17.7 | 25.9 | 39.8 | 385.3813047 | 0.751333333 | 0.1844 |
| 112 | 13:54:38 | 20 | 17.5 | 26.6 | 40.5 | 385.7277148 | 0.749 | 0.187166 |
| 113 | 13:54:43 | 20.3 | 17.9 | 27.1 | 39.13333333 | 385.7854499 | 0.748666667 | 0.180712 |
| 114 | 13:54:48 | 19.6 | 17.2 | 26.1 | 38.86666667 | 385.6122448 | 0.753666667 | 0.180712 |
| 115 | 13:54:53 | 19.6 | 17 | 26 | 38.13333333 | 385.6699798 | 0.761 | 0.178868 |
| 116 | 13:54:58 | 19.4 | 16.5 | 25.5 | 37.53333333 | 386.13186 | 0.779666667 | 0.180712 |
| 117 | 13:55:03 | 19.6 | 15.6 | 25.1 | 38.3 | 386.1895951 | 0.748666667 | 0.177024 |
| 118 | 13:55:08 | 19.2 | 16.9 | 25.6 | 39.53333333 | 386.074125 | 0.736666667 | 0.17979 |
| 119 | 13:55:13 | 19.5 | 17.8 | 26.4 | 38.23333333 | 385.8431849 | 0.789333333 | 0.186244 |
| 120 | 13:55:18 | 20.2 | 15.5 | 25.5 | 38.53333333 | 385.9009199 | 0.759666667 | 0.180712 |
| 121 | 13:55:23 | 19.6 | 16.6 | 25.8 | 37.13333333 | 385.5545098 | 0.784666667 | 0.17979 |
| 122 | 13:55:28 | 19.5 | 15.2 | 24.8 | 37 | 386.01639 | 0.787333333 | 0.17979 |
| 123 | 13:55:33 | 19.5 | 15.1 | 24.7 | 36.63333333 | 386.4205352 | 0.802333333 | 0.181634 |
| 124 | 13:55:38 | 19.7 | 14.6 | 24.5 | 37.16666667 | 386.7092103 | 0.771 | 0.177024 |
| 125 | 13:55:43 | 19.2 | 15.7 | 24.9 | 35.26666667 | 386.7092103 | 0.766333333 | 0.166882 |
| 126 | 13:55:48 | 18.1 | 15.1 | 23.6 | 33.33333333 | 386.5937402 | 0.787 | 0.162272 |
| 127 | 13:55:53 | 17.6 | 13.6 | 22.3 | 33.8 | 386.4782702 | 0.790333333 | 0.165038 |
| 128 | 13:55:58 | 17.9 | 13.8 | 22.6 | 35.33333333 | 386.4782702 | 0.764666667 | 0.166882 |
| 129 | 13:56:03 | 18.1 | 15.1 | 23.7 | 37.8 | 386.1895951 | 0.745666667 | 0.174258 |
| 130 | 13:56:08 | 18.9 | 16.8 | 25.3 | 37.73333333 | 386.13186 | 0.747666667 | 0.174258 |
| 131 | 13:56:13 | 18.9 | 16.6 | 25.2 | 34.03333333 | 386.6514753 | 0.784333333 | 0.165038 |
| 132 | 13:56:18 | 17.9 | 14.1 | 22.8 | 36.1 | 386.074125 | 0.777 | 0.173336 |
| 133 | 13:56:23 | 18.8 | 15.1 | 24.1 | 33.9 | 386.2473301 | 0.784 | 0.164116 |
| 134 | 13:56:28 | 17.8 | 14 | 22.7 | 34.93333333 | 386.2473301 | 0.747333333 | 0.16135 |
| 135 | 13:56:33 | 17.5 | 15.4 | 23.4 | 35.23333333 | 385.9009199 | 0.767333333 | 0.166882 |
| 136 | 13:56:38 | 18.1 | 15 | 23.5 | 34.66666667 | 386.1895951 | 0.800666667 | 0.171492 |
| 137 | 13:56:43 | 18.6 | 13.7 | 23.2 | 36.86666667 | 386.1895951 | 0.768666667 | 0.17518 |
| 138 | 13:56:48 | 19 | 15.7 | 24.7 | 37.16666667 | 386.13186 | 0.759666667 | 0.174258 |
| 139 | 13:56:53 | 18.9 | 16.1 | 24.8 | 38.2 | 386.13186 | 0.762 | 0.17979 |
| 140 | 13:56:58 | 19.5 | 16.5 | 25.5 | 38.23333333 | 386.13186 | 0.750666667 | 0.177024 |
| 141 | 13:57:03 | 19.2 | 16.9 | 25.6 | 39 | 386.2473301 | 0.764 | 0.1844 |
| 142 | 13:57:08 | 20 | 16.7 | 26.1 | 40.93333333 | 386.074125 | 0.768666667 | 0.194542 |
| 143 | 13:57:13 | 21.1 | 17.3 | 27.4 | 39.8 | 386.13186 | 0.776333333 | 0.190854 |
| 144 | 13:57:18 | 20.7 | 16.7 | 26.6 | 35.83333333 | 386.5937402 | 0.791333333 | 0.17518 |
| 145 | 13:57:23 | 19 | 14.6 | 24 | 34.2 | 386.7092103 | 0.786 | 0.16596 |
| 146 | 13:57:28 | 18 | 14.1 | 22.9 | 34 | 386.7669453 | 0.784666667 | 0.165038 |
| 147 | 13:57:33 | 17.9 | 14 | 22.8 | 35.96666667 | 386.8246804 | 0.775 | 0.172414 |
| 148 | 13:57:38 | 18.7 | 15.1 | 24.1 | 36.66666667 | 386.5937402 | 0.772666667 | 0.17518 |
| 149 | 13:57:43 | 19 | 15.4 | 24.5 | 35.56666667 | 386.2473301 | 0.789666667 | 0.173336 |
| 150 | 13:57:48 | 18.8 | 14.5 | 23.8 | 38.96666667 | 386.4205352 | 0.773333333 | 0.186244 |
| 151 | 13:57:53 | 20.2 | 16.4 | 26.1 | 38.43333333 | 386.4782702 | 0.764 | 0.181634 |
| 152 | 13:57:58 | 19.7 | 16.5 | 25.7 | 38.63333333 | 386.5937402 | 0.772 | 0.1844 |
| 153 | 13:58:03 | 20 | 16.4 | 25.9 | 38.6 | 386.3050651 | 0.756333333 | 0.180712 |
| 154 | 13:58:08 | 19.6 | 16.7 | 25.8 | 38 | 386.1895951 | 0.753666667 | 0.177024 |
| 155 | 13:58:13 | 19.2 | 16.7 | 25.4 | 40.3 | 386.074125 | 0.756333333 | 0.188088 |
| 156 | 13:58:18 | 20.4 | 17.5 | 26.9 | 39.7 | 385.7854499 | 0.763333333 | 0.187166 |
| 157 | 13:58:23 | 20.3 | 17 | 26.5 | 39.33333333 | 386.01639 | 0.775 | 0.188088 |
| 158 | 13:58:28 | 20.4 | 16.6 | 26.3 | 41.23333333 | 385.9009199 | 0.745666667 | 0.189932 |
| 159 | 13:58:33 | 20.6 | 18.3 | 27.6 | 40.5 | 385.7854499 | 0.745 | 0.186244 |
| 160 | 13:58:38 | 20.2 | 18 | 27.1 | 41.93333333 | 386.1895951 | 0.743333333 | 0.192698 |
| 161 | 13:58:43 | 20.9 | 18.7 | 28 | 41.2 | 386.9978854 | 0.726666667 | 0.185322 |
| 162 | 13:58:48 | 20.1 | 19 | 27.6 | 42.2 | 386.1895951 | 0.745333333 | 0.194542 |
| 163 | 13:45:23 | 21.1 | 18.6 | 28.2 | 41.4 | 387.1133555 | 0.734 | 0.188088 |

Table A-8: Power analyser measurements for the air compressor

| Measurements during load |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| No. of reading | Date | Average kVA | Average kVAR | Average kW | Average PF | Average Voltage | Average Current |
| 1 | 13/05/17 | 18 | 9.4 | 15.3 | 0.85 | 230.8333333 | 26 |
| 2 | 13/05/17 | 18.2 | 9.8 | 15.3 | 0.841 | 230.9666667 | 26.23333333 |
| 3 | 13/05/17 | 18.2 | 9.6 | 15.5 | 0.852 | 231 | 26.26666667 |
| 4 | 13/05/17 | 18.2 | 9.8 | 15.3 | 0.841 | 230.8666667 | 26.23333333 |
| 5 | 13/05/17 | 18.2 | 9.7 | 15.4 | 0.846 | 230.8 | 26.26666667 |
| 6 | 13/05/17 | 18.3 | 9.6 | 15.5 | 0.847 | 231 | 26.33333333 |
| 7 | 13/05/17 | 18.3 | 9.6 | 15.6 | 0.852 | 231.1 | 26.43333333 |
| 8 | 13/05/17 | 18.4 | 9.8 | 15.6 | 0.848 | 230.9333333 | 26.53333333 |
| 9 | 13/05/17 | 18.4 | 9.8 | 15.6 | 0.848 | 230.8333333 | 26.6 |
| 10 | 13/05/17 | 18.5 | 9.7 | 15.7 | 0.849 | 230.8 | 26.66666667 |
| 11 | 13/05/17 | 18.5 | 9.6 | 15.8 | 0.854 | 230.8333333 | 26.7 |
| 12 | 13/05/17 | 18.5 | 9.6 | 15.8 | 0.854 | 230.3666667 | 26.73333333 |
| 13 | 13/05/17 | 18.6 | 9.7 | 15.8 | 0.849 | 230.4333333 | 26.83333333 |
| 14 | 13/05/17 | 18.6 | 9.7 | 15.8 | 0.849 | 230.4333333 | 26.83333333 |
| 15 | 13/05/17 | 18.6 | 9.8 | 15.8 | 0.849 | 230.5666667 | 26.9 |
| 16 | 13/05/17 | 18.6 | 9.4 | 16.1 | 0.866 | 230.0333333 | 27 |
| 17 | 13/05/17 | 18.6 | 9.8 | 15.9 | 0.855 | 229.8666667 | 27.03333333 |
| 18 | 13/05/17 | 18.7 | 9.7 | 16 | 0.856 | 229.7666667 | 27.1 |
| 19 | 13/05/17 | 18.7 | 9.6 | 16.1 | 0.861 | 229.7333333 | 27.16666667 |
| 20 | 13/05/17 | 18.7 | 9.6 | 16 | 0.856 | 228.4333333 | 27.23333333 |
| 21 | 13/05/17 | 18.7 | 9.4 | 16.2 | 0.866 | 228.5 | 27.33333333 |
| 22 | 13/05/17 | 18.8 | 9.5 | 16.2 | 0.862 | 228.0666667 | 27.43333333 |
| 23 | 13/05/17 | 18.8 | 9.5 | 16.2 | 0.862 | 227.7666667 | 27.46666667 |
| 24 | 13/05/17 | 18.8 | 9.5 | 16.2 | 0.862 | 227.6333333 | 27.5 |
| 25 | 13/05/17 | 18.8 | 9.4 | 16.3 | 0.867 | 227.6666667 | 27.56666667 |
| 26 | 13/05/17 | 18.9 | 9.6 | 16.2 | 0.857 | 227.6666667 | 27.6 |
| 27 | 13/05/17 | 18.9 | 9.4 | 16.4 | 0.868 | 227.7333333 | 27.66666667 |
| 28 | 13/05/17 | 18.9 | 9.3 | 16.5 | 0.873 | 227.5333333 | 27.73333333 |
| 29 | 13/05/17 | 18.9 | 9.3 | 16.5 | 0.873 | 227.5 | 27.73333333 |
| 30 | 13/05/17 | 19 | 9.4 | 16.5 | 0.868 | 227.4666667 | 27.8 |
| 31 | 13/05/17 | 19 | 9.6 | 16.5 | 0.868 | 227.4666667 | 27.9 |
| 32 | 13/05/17 | 19.1 | 9.5 | 16.5 | 0.864 | 227.7666667 | 27.9 |
| 33 | 13/05/17 | 19.1 | 9.4 | 16.6 | 0.869 | 227.7666667 | 28 |
| 34 | 13/05/17 | 15 | 4.3 | 14.4 | 0.96 | 228.9333333 | 21.9 |
| 35 | 13/05/17 | 13.5 | 8.4 | 10.5 | 0.778 | 229.3666667 | 19.6 |
| 36 | 13/05/17 | 12.7 | 8.7 | 9.3 | 0.732 | 230.2666667 | 18.36666667 |
| 37 | 13/05/17 | 12 | 8.4 | 8.6 | 0.717 | 230.4666667 | 17.36666667 |
| 38 | 13/05/17 | 11.4 | 8.5 | 7.5 | 0.658 | 230.7666667 | 16.4 |
| 39 | 13/05/17 | 10.9 | 8.4 | 6.8 | 0.624 | 230.8666667 | 15.7 |
| 40 | 13/05/17 | 10.7 | 8.5 | 6.3 | 0.589 | 232.6333333 | 15.26666667 |
| 41 | 13/05/17 | 10.3 | 8.5 | 5.8 | 0.563 | 232.5666667 | 14.76666667 |
| 42 | 13/05/17 | 10 | 8.5 | 5.2 | 0.52 | 232.6 | 14.36666667 |
| 43 | 13/05/17 | 15.2 | 10.5 | 11 | 0.724 | 229.1666667 | 22.16666667 |
| 44 | 13/05/17 | 17.8 | 9.2 | 15.2 | 0.854 | 228.2666667 | 25.96666667 |
| 45 | 13/05/17 | 17.9 | 9.2 | 15.3 | 0.855 | 228.1666667 | 26.1 |
| 46 | 13/05/17 | 17.9 | 9.2 | 15.3 | 0.855 | 228.3333333 | 26.06666667 |
| 47 | 13/05/17 | 17.9 | 9.3 | 15.3 | 0.855 | 228.7 | 26.06666667 |
| 48 | 13/05/17 | 17.9 | 9.4 | 15.3 | 0.855 | 228.5333333 | 26.16666667 |
| 49 | 13/05/17 | 18 | 9.3 | 15.4 | 0.856 | 228.5 | 26.26666667 |
| 50 | 13/05/17 | 18.1 | 9.5 | 15.4 | 0.851 | 228.3666667 | 26.4 |
| 51 | 13/05/17 | 18.1 | 9.4 | 15.5 | 0.856 | 228.7666667 | 26.43333333 |
| 52 | 13/05/17 | 18.2 | 9.1 | 15.7 | 0.863 | 228.7666667 | 26.46666667 |
| 53 | 13/05/17 | 18.3 | 9.5 | 15.6 | 0.852 | 228.9 | 26.6 |
| 54 | 13/05/17 | 18.3 | 9.3 | 15.7 | 0.858 | 228.7666667 | 26.63333333 |
| 55 | 13/05/17 | 18.4 | 9.6 | 15.7 | 0.853 | 230.0333333 | 26.66666667 |
| 56 | 13/05/17 | 18.4 | 9.5 | 15.8 | 0.859 | 230.2666667 | 26.7 |
| 57 | 13/05/17 | 18.5 | 9.3 | 15.9 | 0.859 | 230.1666667 | 26.76666667 |
| 58 | 13/05/17 | 18.5 | 9.7 | 15.8 | 0.854 | 230.0333333 | 26.83333333 |
| 59 | 13/05/17 | 18.5 | 9.6 | 15.9 | 0.859 | 230.0333333 | 26.86666667 |
| 60 | 13/05/17 | 18.6 | 9.6 | 15.9 | 0.855 | 229.9333333 | 26.96666667 |
| 61 | 13/05/17 | 18.6 | 9.6 | 15.9 | 0.855 | 229.9 | 26.96666667 |
| 62 | 13/05/17 | 18.6 | 9.6 | 16 | 0.86 | 229.9 | 27.03333333 |
| 63 | 13/05/17 | 18.7 | 9.6 | 16 | 0.856 | 230 | 27.1 |
| 64 | 13/05/17 | 18.7 | 9.6 | 16.1 | 0.861 | 229.9666667 | 27.16666667 |
| 65 | 13/05/17 | 18.8 | 9.8 | 16 | 0.851 | 230.0666667 | 27.2 |
| 66 | 13/05/17 | 18.8 | 9.8 | 16.1 | 0.856 | 229.7666667 | 27.3 |
| 67 | 13/05/17 | 18.9 | 9.7 | 16.1 | 0.852 | 229.5666667 | 27.36666667 |
| 68 | 13/05/17 | 18.9 | 9.7 | 16.2 | 0.857 | 229.7 | 27.4 |
| 69 | 13/05/17 | 18.9 | 9.6 | 16.3 | 0.862 | 229.4666667 | 27.46666667 |
| 70 | 13/05/17 | 18.9 | 9.6 | 16.3 | 0.862 | 229.6 | 27.5 |
| 71 | 13/05/17 | 19 | 9.9 | 16.2 | 0.853 | 229.3 | 27.56666667 |
| 72 | 13/05/17 | 19 | 9.7 | 16.3 | 0.858 | 229.2666667 | 27.56666667 |
| 73 | 13/05/17 | 19 | 9.5 | 16.5 | 0.868 | 229.1666667 | 27.66666667 |
| 74 | 13/05/17 | 19 | 9.6 | 16.5 | 0.868 | 229.3 | 27.66666667 |
| 75 | 13/05/17 | 19 | 9.4 | 16.5 | 0.868 | 227.9666667 | 27.8 |
| 76 | 13/05/17 | 19.1 | 9.8 | 16.4 | 0.859 | 228.4 | 27.83333333 |
| 77 | 13/05/17 | 19.1 | 9.7 | 16.5 | 0.864 | 228.4 | 27.9 |
| 78 | 13/05/17 | 19.1 | 9.7 | 16.5 | 0.864 | 228.3333333 | 27.9 |
| 79 | 13/05/17 | 19.1 | 9.7 | 16.5 | 0.864 | 228.1333333 | 27.96666667 |
| 80 | 13/05/17 | 14.4 | 8.4 | 11.7 | 0.813 | 229.4333333 | 20.96666667 |
| 81 | 13/05/17 | 13.4 | 8.6 | 10.2 | 0.761 | 229.6666667 | 19.43333333 |
| 82 | 13/05/17 | 12.5 | 8.5 | 9.2 | 0.736 | 230 | 18.16666667 |
| 83 | 13/05/17 | 11.8 | 8.5 | 8.2 | 0.695 | 230.1 | 17.1 |
| 84 | 13/05/17 | 11.2 | 8.6 | 7.3 | 0.652 | 230.5333333 | 16.2 |
| 85 | 13/05/17 | 15.9 | 10.7 | 11.8 | 0.742 | 229 | 23.2 |
| 86 | 13/05/17 | 17.9 | 9.3 | 15.2 | 0.849 | 228.3 | 26.06666667 |
| 87 | 13/05/17 | 17.9 | 9.4 | 15.3 | 0.855 | 228.3333333 | 26.16666667 |
| 88 | 13/05/17 | 17.9 | 9.3 | 15.3 | 0.855 | 228.2666667 | 26.13333333 |
| 89 | 13/05/17 | 17.9 | 9.2 | 15.3 | 0.855 | 228.2 | 26.1 |
| 90 | 13/05/17 | 17.9 | 9.4 | 15.3 | 0.855 | 228.1666667 | 26.2 |
| 91 | 13/05/17 | 18 | 9.2 | 15.4 | 0.856 | 228.1 | 26.26666667 |
| 92 | 13/05/17 | 18.1 | 9.4 | 15.5 | 0.856 | 228.2 | 26.4 |
| 93 | 13/05/17 | 18.1 | 9.1 | 15.6 | 0.862 | 228.2 | 26.43333333 |
| 94 | 13/05/17 | 18.1 | 9.2 | 15.6 | 0.862 | 228.1 | 26.5 |
| 95 | 13/05/17 | 18.2 | 9.4 | 15.6 | 0.857 | 227.9333333 | 26.6 |
| 96 | 13/05/17 | 18.2 | 9.4 | 15.6 | 0.857 | 227.9666667 | 26.6 |
| 97 | 13/05/17 | 18.3 | 9.4 | 15.7 | 0.858 | 228.2 | 26.7 |
| 98 | 13/05/17 | 18.3 | 9.5 | 15.7 | 0.858 | 228.4666667 | 26.73333333 |
| 99 | 13/05/17 | 18.4 | 9.4 | 15.7 | 0.853 | 228.5 | 26.76666667 |
| 100 | 13/05/17 | 18.4 | 9.3 | 15.8 | 0.859 | 228.2 | 26.83333333 |
| 101 | 13/05/17 | 18.5 | 9.5 | 15.8 | 0.854 | 228.5 | 26.93333333 |
| 102 | 13/05/17 | 18.5 | 9.4 | 15.9 | 0.859 | 228.4333333 | 26.96666667 |
| 103 | 13/05/17 | 18.5 | 9.5 | 15.9 | 0.859 | 228.3666667 | 27.03333333 |
| Average P Loaded = 14.89313725 |  |  |  | T Loaded = 210 Seconds |  |  |  |
| Measurements during unload |  |  |  |  |  |  |  |
| 104 | 13/05/17 | 9.8 | 8.5 | 4.8 | 0.49 | 232.7 | 14.03333333 |
| 105 | 13/05/17 | 9.6 | 8.5 | 4.5 | 0.469 | 232.8333333 | 13.76666667 |
| 106 | 13/05/17 | 9.5 | 8.5 | 4.2 | 0.442 | 232.7666667 | 13.53333333 |
| 107 | 13/05/17 | 9.4 | 8.5 | 3.9 | 0.415 | 232.9333333 | 13.46666667 |
| 108 | 13/05/17 | 9.3 | 8.5 | 3.7 | 0.398 | 233.1333333 | 13.26666667 |
| 109 | 13/05/17 | 9.2 | 8.5 | 3.6 | 0.391 | 232.8 | 13.13333333 |
| 110 | 13/05/17 | 9.1 | 8.4 | 3.4 | 0.374 | 233.1666667 | 13 |
| 111 | 13/05/17 | 9.1 | 8.5 | 3.3 | 0.363 | 233.2 | 13.06666667 |
| 112 | 13/05/17 | 9.1 | 8.5 | 3.3 | 0.363 | 233.1666667 | 13.03333333 |
| 113 | 13/05/17 | 9 | 8.3 | 3.3 | 0.367 | 232.9666667 | 12.86666667 |
| 114 | 13/05/17 | 9 | 8.3 | 3.2 | 0.356 | 232.9333333 | 12.9 |
| 115 | 13/05/17 | 9.1 | 8.5 | 3.2 | 0.352 | 232.9666667 | 13 |
| 116 | 13/05/17 | 9 | 8.4 | 3.3 | 0.367 | 232.9666667 | 12.93333333 |
| 117 | 13/05/17 | 8.9 | 8.3 | 3.2 | 0.36 | 232.6666667 | 12.8 |
| 118 | 13/05/17 | 9 | 8.4 | 3.2 | 0.356 | 232.5 | 12.9 |
| 119 | 13/05/17 | 9 | 8.3 | 3.3 | 0.367 | 232.6 | 12.9 |
| 120 | 13/05/17 | 8.9 | 8.3 | 3.2 | 0.36 | 232.5666667 | 12.76666667 |
| 121 | 13/05/17 | 8.7 | 8.1 | 3.2 | 0.368 | 231.3 | 12.6 |
| 122 | 13/05/17 | 8.8 | 8.2 | 3.2 | 0.364 | 231.3 | 12.66666667 |
| 123 | 13/05/17 | 8.7 | 8 | 3.2 | 0.368 | 231.3666667 | 12.56666667 |
| 124 | 13/05/17 | 8.8 | 8.1 | 3.2 | 0.364 | 231.2 | 12.63333333 |
| 125 | 13/05/17 | 8.8 | 8.1 | 3.2 | 0.364 | 231.2 | 12.63333333 |
| 126 | 13/05/17 | 8.7 | 8 | 3.2 | 0.368 | 231.0666667 | 12.53333333 |
| 127 | 13/05/17 | 8.7 | 8 | 3.2 | 0.368 | 230.9333333 | 12.56666667 |
| 128 | 13/05/17 | 8.8 | 8.2 | 3.2 | 0.364 | 231.1 | 12.66666667 |
| 129 | 13/05/17 | 8.7 | 8 | 3.2 | 0.368 | 231.0333333 | 12.56666667 |
| 130 | 13/05/17 | 8.7 | 8 | 3.2 | 0.368 | 231.2333333 | 12.53333333 |
| 131 | 13/05/17 | 0.7 | 0.2 | 0.7 | 1 | 232.3666667 | 1.033333333 |
| 132 | 13/05/17 | 0 | 0 | 0 | 0 | 232.3 | 0 |
| 133 | 13/05/17 | 0 | 0 | 0 | 0 | 232.3333333 | 0 |
| 134 | 13/05/17 | 0 | 0 | 0 | 0 | 232.5666667 | 0 |
| 135 | 13/05/17 | 0 | 0 | 0 | 0 | 232.4333333 | 0 |
| 136 | 13/05/17 | 0 | 0 | 0 | 0 | 232.5333333 | 0 |
| 137 | 13/05/17 | 0 | 0 | 0 | 0 | 232.3333333 | 0 |
| 138 | 13/05/17 | 0 | 0 | 0 | 0 | 232.3666667 | 0 |
| 139 | 13/05/17 | 0 | 0 | 0 | 0 | 232.3666667 | 0 |
| 140 | 13/05/17 | 0 | 0 | 0 | 0 | 232.4 | 0 |
| 141 | 13/05/17 | 0 | 0 | 0 | 0 | 232.5 | 0 |
| 142 | 13/05/17 | 0 | 0 | 0 | 0 | 232.5666667 | 0 |
| 143 | 13/05/17 | 0 | 0 | 0 | 0 | 232.3666667 | 0 |
| 144 | 13/05/17 | 0 | 0 | 0 | 0 | 232.3 | 0 |
| 145 | 13/05/17 | 0 | 0 | 0 | 0 | 232.3 | 0 |
| 146 | 13/05/17 | 0 | 0 | 0 | 0 | 232.5 | 0 |
| 147 | 13/05/17 | 0 | 0 | 0 | 0 | 232.4 | 0 |
| 148 | 13/05/17 | 0 | 0 | 0 | 0 | 232.6 | 0 |
| 149 | 13/05/17 | 0 | 0 | 0 | 0 | 232.3666667 | 0 |
| 150 | 13/05/17 | 0 | 0 | 0 | 0 | 232.3666667 | 0 |
| 151 | 13/05/17 | 0 | 0 | 0 | 0 | 232.2 | 0 |
| 152 | 13/05/17 | 0 | 0 | 0 | 0 | 232.1666667 | 0 |
| 153 | 13/05/17 | 0 | 0 | 0 | 0 | 232.2333333 | 0 |
| 154 | 13/05/17 | 0 | 0 | 0 | 0 | 232.5333333 | 0 |
| 155 | 13/05/17 | 0 | 0 | 0 | 0 | 232.5 | 0 |
| 156 | 13/05/17 | 0 | 0 | 0 | 0 | 232.7 | 0 |
| 157 | 13/05/17 | 3.7 | 2.7 | 2.5 | 0.676 | 231.7666667 | 5.366666667 |
| 158 | 13/05/17 | 3.9 | 2.7 | 2.7 | 0.692 | 231.9333333 | 5.533333333 |
| 159 | 13/05/17 | 10.7 | 8.4 | 6.7 | 0.626 | 230.9333333 | 15.46666667 |
| 160 | 13/05/17 | 10.3 | 8.4 | 6.1 | 0.592 | 231.1 | 14.9 |
| 161 | 13/05/17 | 10 | 8.4 | 5.6 | 0.56 | 231.5666667 | 14.43333333 |
| 162 | 13/05/17 | 9.8 | 8.3 | 5.1 | 0.52 | 232.0333333 | 14.03333333 |
| 163 | 13/05/17 | 9.5 | 8.3 | 4.8 | 0.505 | 232.1333333 | 13.7 |
| 164 | 13/05/17 | 9.4 | 8.2 | 4.5 | 0.479 | 232.2 | 13.46666667 |
| 165 | 13/05/17 | 9.3 | 8.3 | 4.2 | 0.452 | 232.2 | 13.3 |
| 166 | 13/05/17 | 9.2 | 8.3 | 3.8 | 0.413 | 232.6333333 | 13.13333333 |
| 167 | 13/05/17 | 9.1 | 8.3 | 3.7 | 0.407 | 232.6333333 | 12.96666667 |
| 168 | 13/05/17 | 9 | 8.2 | 3.5 | 0.389 | 232.4333333 | 12.86666667 |
| 169 | 13/05/17 | 9 | 8.3 | 3.4 | 0.378 | 232.4666667 | 12.83333333 |
| 170 | 13/05/17 | 9 | 8.4 | 3.3 | 0.367 | 233.7666667 | 12.9 |
| 171 | 13/05/17 | 9.1 | 8.5 | 3.2 | 0.352 | 233.9666667 | 12.96666667 |
| 172 | 13/05/17 | 9.2 | 8.5 | 3.2 | 0.348 | 233.9666667 | 13.03333333 |
| 173 | 13/05/17 | 9.1 | 8.5 | 3.2 | 0.352 | 233.8333333 | 12.93333333 |
| 174 | 13/05/17 | 9.1 | 8.4 | 3.3 | 0.363 | 233.9666667 | 12.9 |
| 175 | 13/05/17 | 9.1 | 8.5 | 3.2 | 0.352 | 233.8666667 | 13.03333333 |
| 176 | 13/05/17 | 9.2 | 8.5 | 3.2 | 0.348 | 234.0666667 | 13.06666667 |
| 177 | 13/05/17 | 9.1 | 8.5 | 3.3 | 0.363 | 234.0333333 | 12.93333333 |
| 178 | 13/05/17 | 9.1 | 8.5 | 3.2 | 0.352 | 234 | 13 |
| 179 | 13/05/17 | 9.2 | 8.5 | 3.3 | 0.359 | 233.8333333 | 13.1 |
| 180 | 13/05/17 | 9.1 | 8.5 | 3.3 | 0.363 | 233.8333333 | 13 |
| 181 | 13/05/17 | 9.1 | 8.5 | 3.3 | 0.363 | 233.6666667 | 12.93333333 |
| 182 | 13/05/17 | 9.1 | 8.4 | 3.3 | 0.363 | 233.4 | 13 |
| 183 | 13/05/17 | 9.1 | 8.5 | 3.3 | 0.363 | 233.3666667 | 13 |
| 184 | 13/05/17 | 9 | 8.3 | 3.3 | 0.367 | 233.2 | 12.9 |
| 185 | 13/05/17 | 9.1 | 8.5 | 3.2 | 0.352 | 233.3333333 | 13 |
| 186 | 13/05/17 | 9.1 | 8.4 | 3.3 | 0.363 | 232.6333333 | 12.96666667 |
| 187 | 13/05/17 | 8.9 | 8.3 | 3.2 | 0.36 | 232.5333333 | 12.8 |
| 188 | 13/05/17 | 9 | 8.3 | 3.2 | 0.356 | 232.4666667 | 12.83333333 |
| 189 | 13/05/17 | 9 | 8.4 | 3.2 | 0.356 | 232.3 | 12.9 |
| 190 | 13/05/17 | 0 | 0 | 0 | 0 | 232.3666667 | 0 |
| 191 | 13/05/17 | 0 | 0 | 0 | 0 | 232.3666667 | 0 |
| 192 | 13/05/17 | 0 | 0 | 0 | 0 | 232.2666667 | 0 |
| 193 | 13/05/17 | 0 | 0 | 0 | 0 | 232.2 | 0 |
| 194 | 13/05/17 | 0 | 0 | 0 | 0 | 232.3333333 | 0 |
| 195 | 13/05/17 | 0 | 0 | 0 | 0 | 232.4333333 | 0 |
| 196 | 13/05/17 | 0 | 0 | 0 | 0 | 232.7333333 | 0 |
| 197 | 13/05/17 | 0 | 0 | 0 | 0 | 232.4 | 0 |
| 198 | 13/05/17 | 0 | 0 | 0 | 0 | 232.6333333 | 0 |
| 199 | 13/05/17 | 0 | 0 | 0 | 0 | 232.5333333 | 0 |
| 200 | 13/05/17 | 0 | 0 | 0 | 0 | 232.5666667 | 0 |
| 201 | 13/05/17 | 0 | 0 | 0 | 0 | 232.6 | 0 |
| 202 | 13/05/17 | 0 | 0 | 0 | 0 | 232.6 | 0 |
| 203 | 13/05/17 | 0 | 0 | 0 | 0 | 232.6333333 | 0 |
| 204 | 13/05/17 | 0 | 0 | 0 | 0 | 232.8333333 | 0 |
| 205 | 13/05/17 | 0 | 0 | 0 | 0 | 232.8 | 0 |
| 206 | 13/05/17 | 0 | 0 | 0 | 0 | 232.6 | 0 |
| 207 | 13/05/17 | 0 | 0 | 0 | 0 | 232.6666667 | 0 |
| 208 | 13/05/17 | 0 | 0 | 0 | 0 | 232.6333333 | 0 |
| 209 | 13/05/17 | 0 | 0 | 0 | 0 | 232.6666667 | 0 |
| 210 | 13/05/17 | 0 | 0 | 0 | 0 | 232.5333333 | 0 |
| 211 | 13/05/17 | 0 | 0 | 0 | 0 | 232.8666667 | 0 |
| 212 | 13/05/17 | 0 | 0 | 0 | 0 | 232.7333333 | 0 |
| 213 | 13/05/17 | 0 | 0 | 0 | 0 | 232.8 | 0 |
| 214 | 13/05/17 | 0 | 0 | 0 | 0 | 232.7333333 | 0 |
| 215 | 13/05/17 | 3.7 | 2.8 | 2.5 | 0.676 | 231.8 | 5.366666667 |
| 216 | 13/5/17 | 3.9 | 2.7 | 2.8 | 0.718 | 231.9333333 | 5.566666667 |
| Average P Un Loaded = 3.603448276 kW |  |  | T Un Loaded = 265 Second |  |  |  |  |
| Average Power = 7.421538462 kW |  |  | Operating hours = 3000 h |  | Energy consumption = 22,264.62 kWh |  |  |

Table A-9: power analyser measurements for the HF welding

| No. of reading | Time | Average KW | Average KVAR | Average KVA | Average PF | average current | Average voltage |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | 11:31:07 | 74 | 145.9 | 163.6 | 0.452 | 243.6333333 | 223.8 |
| 2 | 11:31:12 | 74.5 | 146 | 163.9 | 0.455 | 244.2333333 | 223.6666667 |
| 3 | 11:31:17 | 74.4 | 145.9 | 163.7 | 0.454 | 243.8666667 | 223.7333333 |
| 4 | 11:31:22 | 74.3 | 145.2 | 163.1 | 0.456 | 243.2666667 | 223.4666667 |
| 5 | 11:31:27 | 74.6 | 145.8 | 163.8 | 0.455 | 244.0333333 | 223.7333333 |
| 6 | 11:31:32 | 74 | 146.1 | 163.7 | 0.452 | 244.1 | 223.5666667 |
| 7 | 11:31:37 | 74.4 | 145.1 | 163 | 0.456 | 242.9333333 | 223.6333333 |
| 8 | 11:31:42 | 74.3 | 145.9 | 163.8 | 0.454 | 244.2 | 223.6 |
| 9 | 11:31:47 | 74.1 | 145.7 | 163.4 | 0.453 | 243.4666667 | 223.7333333 |
| 10 | 11:31:52 | 73.9 | 145.8 | 163.5 | 0.452 | 243.5333333 | 223.7 |
| 11 | 11:31:57 | 74.3 | 144.8 | 162.8 | 0.456 | 242.7333333 | 223.5666667 |
| 12 | 11:32:02 | 74.3 | 145.7 | 163.6 | 0.454 | 243.7333333 | 223.6666667 |
| 13 | 11:32:07 | 74 | 145 | 162.8 | 0.455 | 242.6666667 | 223.6333333 |
| 14 | 11:32:12 | 74.4 | 146.1 | 163.9 | 0.454 | 244.3666667 | 223.6 |
| 15 | 11:32:17 | 74.1 | 145.4 | 163.3 | 0.454 | 243.5333333 | 223.4333333 |
| 16 | 11:32:22 | 74.3 | 144.9 | 162.9 | 0.456 | 243.1666667 | 223.2333333 |
| 17 | 11:32:27 | 73.7 | 145.2 | 162.8 | 0.453 | 242.9 | 223.3333333 |
| 18 | 11:32:32 | 73.9 | 144.8 | 162.6 | 0.454 | 242.6 | 223.3666667 |
| 19 | 11:32:37 | 74.1 | 144.8 | 162.7 | 0.455 | 242.7333333 | 223.3666667 |
| 20 | 11:32:42 | 73.6 | 145.5 | 163.1 | 0.451 | 243.0666667 | 223.6666667 |
| 21 | 11:32:47 | 74.6 | 145.4 | 163.4 | 0.457 | 243.8666667 | 223.3 |
| 22 | 11:32:52 | 73.4 | 144.9 | 162.4 | 0.452 | 241.9666667 | 223.7 |
| 23 | 11:32:57 | 74.1 | 145.1 | 162.9 | 0.455 | 242.7333333 | 223.7 |
| 24 | 11:33:02 | 73.7 | 145 | 162.6 | 0.453 | 242.2666667 | 223.7333333 |
| 25 | 11:33:07 | 73.8 | 144.5 | 162.2 | 0.455 | 242.0333333 | 223.4 |
| 26 | 11:33:12 | 73.8 | 144.5 | 162.3 | 0.455 | 241.9666667 | 223.5333333 |
| 27 | 11:33:17 | 73.8 | 144.6 | 162.3 | 0.455 | 242.1333333 | 223.4666667 |
| 28 | 11:33:22 | 73.6 | 144.8 | 162.3 | 0.453 | 242.0666667 | 223.5 |
| 29 | 11:33:27 | 73.8 | 144.4 | 162.2 | 0.455 | 241.5333333 | 223.8333333 |
| 30 | 11:33:32 | 73.5 | 145.5 | 163 | 0.451 | 243 | 223.6333333 |
| 31 | 11:33:37 | 73.8 | 145.4 | 163.1 | 0.452 | 242.6666667 | 224.0333333 |
| 32 | 11:33:42 | 73.8 | 144.8 | 162.5 | 0.454 | 241.7333333 | 224.1 |
| 33 | 11:33:47 | 73.9 | 144.9 | 162.6 | 0.454 | 241.8333333 | 224.1333333 |
| 34 | 11:33:52 | 73.9 | 145.5 | 163.2 | 0.453 | 242.8 | 224.0333333 |
| 35 | 11:33:57 | 73.5 | 145.3 | 162.8 | 0.451 | 242.0666667 | 224.1333333 |
| 36 | 11:34:02 | 73.5 | 144.8 | 162.4 | 0.453 | 241.6666667 | 223.9333333 |
| 37 | 11:34:07 | 73.8 | 144.7 | 162.4 | 0.454 | 242.1 | 223.6 |
| 38 | 11:34:12 | 73.6 | 144.7 | 162.3 | 0.453 | 241.7666667 | 223.7666667 |
| 39 | 11:34:17 | 73.9 | 145.3 | 163.1 | 0.453 | 242.7666667 | 223.9 |
| 40 | 11:34:22 | 73.8 | 144.6 | 162.3 | 0.455 | 241.6 | 223.9333333 |
| 41 | 11:34:27 | 73.6 | 144.5 | 162.1 | 0.454 | 241.1666667 | 224.0333333 |
| 42 | 11:34:32 | 73.4 | 144.6 | 162.2 | 0.453 | 241.5666667 | 223.7666667 |
| 43 | 11:34:37 | 73.9 | 144.9 | 162.6 | 0.454 | 242.2333333 | 223.7666667 |
| 44 | 11:34:42 | 73.2 | 145.4 | 162.8 | 0.45 | 242.4666667 | 223.8 |
| 45 | 11:34:47 | 73.7 | 144 | 161.7 | 0.456 | 241.0333333 | 223.6333333 |
| 46 | 11:34:52 | 73.8 | 144.9 | 162.6 | 0.454 | 242.6333333 | 223.3666667 |
| 47 | 11:34:57 | 73.5 | 144.4 | 162.1 | 0.453 | 241.6 | 223.5666667 |
| 48 | 11:35:02 | 74 | 145.1 | 162.8 | 0.455 | 242.8 | 223.5 |
| 49 | 11:35:07 | 73.6 | 145 | 162.6 | 0.453 | 242.4 | 223.6333333 |
| 50 | 11:35:12 | 73.6 | 143.9 | 161.6 | 0.455 | 240.7333333 | 223.7333333 |
| 51 | 11:35:17 | 73.7 | 144.2 | 162 | 0.455 | 241.3333333 | 223.6666667 |
| 52 | 11:35:22 | 73.4 | 144.2 | 161.9 | 0.453 | 241 | 223.8333333 |
| 53 | 11:35:27 | 73.3 | 144.8 | 162.2 | 0.452 | 241.8 | 223.6333333 |
| 54 | 11:35:32 | 73.5 | 144 | 161.8 | 0.454 | 241.4333333 | 223.3 |
| 55 | 11:35:37 | 73.8 | 144 | 161.8 | 0.456 | 241.4 | 223.3666667 |
| 56 | 11:35:42 | 73.8 | 144.3 | 162.1 | 0.455 | 241.9333333 | 223.2666667 |
| 57 | 11:35:47 | 73.8 | 144.4 | 162.2 | 0.455 | 242.0666667 | 223.3333333 |
| 58 | 11:35:52 | 73.5 | 144.5 | 162.1 | 0.453 | 241.8333333 | 223.4 |
| 59 | 11:35:57 | 73.5 | 144.8 | 162.4 | 0.453 | 241.9333333 | 223.7 |
| 60 | 11:36:02 | 73.3 | 144.6 | 162.2 | 0.452 | 241.9666667 | 223.4666667 |
| 61 | 11:36:07 | 73.2 | 143.6 | 161.1 | 0.454 | 240.1666667 | 223.6 |
| 62 | 11:36:12 | 73.7 | 144.7 | 162.4 | 0.454 | 242.0666667 | 223.5333333 |
| 63 | 11:36:17 | 73.2 | 144.2 | 161.6 | 0.453 | 240.7666667 | 223.7666667 |
| 64 | 11:36:22 | 72.6 | 144.2 | 161.4 | 0.45 | 240.3666667 | 223.8666667 |
| 65 | 11:36:27 | 71.9 | 143.5 | 160.6 | 0.448 | 239.3 | 223.6333333 |
| 66 | 11:36:32 | 72 | 144.1 | 161.1 | 0.447 | 240.1 | 223.6 |
| 67 | 11:36:37 | 72 | 143.2 | 160.3 | 0.449 | 239.0666667 | 223.4666667 |
| 68 | 11:36:42 | 72.4 | 143.3 | 160.6 | 0.451 | 239.3666667 | 223.5666667 |
| 69 | 11:36:47 | 72.2 | 142.9 | 160.1 | 0.451 | 238.7333333 | 223.5333333 |
| 70 | 11:36:52 | 72.1 | 142.9 | 160 | 0.451 | 238.7 | 223.4333333 |
| 71 | 11:36:57 | 72.2 | 143.1 | 160.2 | 0.451 | 238.9333333 | 223.5333333 |
| 72 | 11:37:02 | 71.9 | 143 | 160.1 | 0.449 | 238.6 | 223.6 |
| 73 | 11:37:07 | 72.2 | 143 | 160.2 | 0.451 | 238.9333333 | 223.5 |
| 74 | 11:37:12 | 71.8 | 142.6 | 159.7 | 0.45 | 238.4 | 223.2333333 |
| 75 | 11:37:17 | 72.3 | 143.4 | 160.6 | 0.45 | 239.6 | 223.3666667 |
| 76 | 11:37:22 | 72.3 | 143.2 | 160.4 | 0.451 | 239.4666667 | 223.2333333 |
| 77 | 11:37:27 | 72.4 | 143.8 | 161 | 0.45 | 240.4333333 | 223.2333333 |
| 78 | 11:37:32 | 72.1 | 143.4 | 160.5 | 0.449 | 239.5666667 | 223.3333333 |
| 79 | 11:37:37 | 71.9 | 142.9 | 160.1 | 0.449 | 238.8 | 223.4333333 |
| 80 | 11:37:42 | 72.5 | 142.7 | 160.1 | 0.453 | 238.8 | 223.4666667 |
| 81 | 11:37:47 | 72.2 | 143.6 | 160.7 | 0.449 | 239.8333333 | 223.3666667 |
| 82 | 11:37:52 | 72.2 | 142.8 | 160 | 0.451 | 238.8333333 | 223.3 |
| 83 | 11:37:57 | 71.7 | 143.6 | 160.5 | 0.447 | 239.5666667 | 223.2666667 |
| 84 | 11:38:02 | 71.6 | 143.2 | 160.1 | 0.447 | 238.8333333 | 223.5 |
| 85 | 11:38:07 | 72.5 | 143.9 | 161.2 | 0.45 | 240.4333333 | 223.4666667 |
| 86 | 11:38:12 | 72.6 | 143 | 160.3 | 0.453 | 239 | 223.6 |
| 87 | 11:38:17 | 72.7 | 143.8 | 161.2 | 0.451 | 240.5 | 223.4333333 |
| 88 | 11:38:22 | 71.6 | 143.1 | 160 | 0.448 | 238.9 | 223.3 |
| 89 | 11:38:27 | 72.3 | 143.2 | 160.4 | 0.451 | 239.5 | 223.1666667 |
| 90 | 11:38:32 | 71.7 | 142.8 | 159.7 | 0.449 | 238.5333333 | 223.2333333 |
| 91 | 11:38:37 | 72 | 143 | 160.1 | 0.45 | 238.7 | 223.6 |
| 92 | 11:38:42 | 71.9 | 143.2 | 160.3 | 0.449 | 239.3 | 223.2333333 |
| 93 | 11:38:47 | 72 | 142.4 | 159.6 | 0.451 | 238.3333333 | 223.1666667 |
| 94 | 11:38:52 | 71.7 | 142.7 | 159.7 | 0.449 | 238.2333333 | 223.4666667 |
| 95 | 11:38:57 | 71.8 | 143.2 | 160.1 | 0.448 | 238.9333333 | 223.4 |
| 96 | 11:39:02 | 72.1 | 143.1 | 160.3 | 0.45 | 238.9666667 | 223.5333333 |
| 97 | 11:39:07 | 71.8 | 142.7 | 159.7 | 0.45 | 238.1333333 | 223.6 |
| 98 | 11:39:12 | 71.8 | 142.8 | 159.9 | 0.449 | 238.1666667 | 223.7333333 |
| 99 | 11:39:17 | 71.6 | 143.1 | 160.1 | 0.447 | 238.5 | 223.7 |
| 100 | 11:39:22 | 72.9 | 142.9 | 160.3 | 0.455 | 238.8333333 | 223.7333333 |
| 101 | 11:39:27 | 73.6 | 143.1 | 160.9 | 0.457 | 239.6666667 | 223.7333333 |
| 102 | 11:39:32 | 73 | 143.1 | 160.7 | 0.454 | 239.2 | 223.9666667 |
| 103 | 11:39:37 | 73.1 | 142.9 | 160.5 | 0.455 | 239 | 223.8333333 |
| 104 | 11:39:42 | 73 | 144.2 | 161.6 | 0.452 | 240.7666667 | 223.7333333 |
| 105 | 11:39:47 | 73.3 | 143.6 | 161.3 | 0.454 | 240.4 | 223.6 |
| 106 | 11:39:52 | 73 | 142.9 | 160.5 | 0.455 | 239.1333333 | 223.7 |
| 107 | 11:39:57 | 72.5 | 142.7 | 160.1 | 0.453 | 238.7666667 | 223.4333333 |
| 108 | 11:40:02 | 72.5 | 143.2 | 160.5 | 0.452 | 239.4 | 223.4666667 |
| 109 | 11:40:07 | 73.1 | 144 | 161.5 | 0.453 | 240.6666667 | 223.6333333 |
| 110 | 11:40:12 | 73.1 | 143.6 | 161.1 | 0.454 | 240.1 | 223.6333333 |
| 111 | 11:40:17 | 73.3 | 144.7 | 162.2 | 0.452 | 241.6 | 223.7666667 |
| 112 | 11:40:22 | 72.8 | 143.2 | 160.7 | 0.453 | 238.5666667 | 224.5 |
| 113 | 11:40:27 | 73 | 143.7 | 161.2 | 0.453 | 239.0666667 | 224.7 |
| 114 | 11:40:32 | 73 | 143.6 | 161.1 | 0.453 | 239.1666667 | 224.4666667 |
| 115 | 11:40:37 | 73.1 | 143.3 | 160.9 | 0.454 | 238.7333333 | 224.5666667 |
| 116 | 11:40:42 | 72.9 | 143.1 | 160.6 | 0.454 | 238.7333333 | 224.2333333 |
| 117 | 11:40:47 | 73 | 143 | 160.6 | 0.455 | 238.9 | 224.0333333 |
| 118 | 11:40:52 | 72.9 | 142.1 | 159.7 | 0.456 | 237.6333333 | 223.9666667 |
| 119 | 11:40:57 | 72.7 | 142.8 | 160.3 | 0.454 | 238.1666667 | 224.2666667 |
| 120 | 11:41:02 | 72.8 | 143.5 | 160.9 | 0.452 | 239.1666667 | 224.1666667 |
| 121 | 11:41:07 | 72.9 | 142.9 | 160.4 | 0.454 | 238.3666667 | 224.2666667 |
| 122 | 11:41:12 | 72.8 | 141.9 | 159.5 | 0.456 | 237.0666667 | 224.3 |
| 123 | 11:41:17 | 72.4 | 143.1 | 160.3 | 0.452 | 238.3333333 | 224.2 |
| 124 | 11:41:22 | 72.9 | 143 | 160.5 | 0.454 | 238.4333333 | 224.3333333 |
| 125 | 11:41:27 | 72.8 | 142.7 | 160.2 | 0.454 | 238 | 224.3 |
| 126 | 11:41:32 | 73.3 | 143.3 | 160.9 | 0.456 | 239 | 224.3666667 |
| 127 | 11:41:37 | 72.8 | 143 | 160.4 | 0.454 | 238.6666667 | 224.0666667 |
| 128 | 11:41:42 | 73 | 142.6 | 160.3 | 0.455 | 238.0333333 | 224.4 |
| 129 | 11:41:47 | 73.3 | 143.2 | 160.9 | 0.456 | 239.0666667 | 224.2666667 |
| 130 | 11:41:52 | 72.9 | 142.6 | 160.2 | 0.455 | 238.0333333 | 224.3666667 |
| 131 | 11:41:57 | 73.3 | 143.8 | 161.4 | 0.454 | 239.8 | 224.3 |
| 132 | 11:42:02 | 73.5 | 144 | 161.6 | 0.455 | 240 | 224.4333333 |
| 133 | 11:42:07 | 73.8 | 144.7 | 162.5 | 0.454 | 241.8333333 | 223.9333333 |
| 134 | 11:42:12 | 74 | 145 | 162.7 | 0.455 | 242.3666667 | 223.7666667 |
| 135 | 11:42:17 | 73.5 | 144.6 | 162.2 | 0.453 | 241.6333333 | 223.7 |
| 136 | 11:42:22 | 73.5 | 143.6 | 161.4 | 0.455 | 240.4 | 223.7333333 |
| 137 | 11:42:27 | 73.6 | 144.3 | 162 | 0.454 | 241.4333333 | 223.6 |
| 138 | 11:42:32 | 73.7 | 144.5 | 162.2 | 0.454 | 241.6 | 223.7333333 |
| 139 | 11:42:37 | 73.6 | 144.5 | 162.2 | 0.454 | 241.6333333 | 223.7 |
| 140 | 11:42:42 | 73.1 | 142.5 | 160.2 | 0.456 | 238.5 | 223.9333333 |
| 141 | 11:42:47 | 73.1 | 143.2 | 160.8 | 0.455 | 239.1666667 | 224.0666667 |
| 142 | 11:42:52 | 73.1 | 143.7 | 161.3 | 0.453 | 239.7 | 224.2333333 |
| P Avg. = 73.16126761 Kw |  |  | Operating hours = 2100 h |  | Energy consumption = 153,638.66 kWh/year |  |  |
| 2-inch pipe need 10 second |  |  | EUI (Energy Unit Index) = (73.16126761*10)/3600 = 0.203225743 kWh/pipe |  |  |  |  |

## Appendix 6: Toshiba- high efficiency motor catalogue

Table A-10: catalogue of the suggested motor

| Output Kw | RPM | Model No. | Frame Number | Efficiency (%) |  | Power factor |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  | Full Load | 75% Load | Full Load | 75% Load |
| 0.75 | 2850 | 813-A0007 | D80 | 84.7 | 84.3 | 0.71 | 0.63 |
|  | 1445 | 813-B0007 | D90SL | 84.6 | 82.6 | 0.53 | 0.44 |
|  | 945 | 813-C0007 | D90SL | 81.1 | 81.5 | 0.65 | 0.55 |
| 1.1 | 2850 | 813-A0011 | D80 | 84.7 | 84.8 | 0.83 | 0.76 |
|  | 1445 | 813-B0011 | D90SL | 86 | 85.3 | 0.66 | 0.56 |
|  | 925 | 813-C0011 | D90LL | 81.5 | 82.6 | 0.69 | 0.60 |
| 1.5 | 2875 | 813-A0015 | D90SL | 87.4 | 88.2 | 0.87 | 0.83 |
|  | 1420 | 813-B0015 | D90LL | 86.2 | 87.1 | 0.74 | 0.66 |
|  | 945 | 813-C0015 | D100L | 85 | 85.3 | 0.70 | 0.62 |
| 2.2 | 2875 | 813-A0020 | D90LL | 88.7 | 89.4 | 0.89 | 0.84 |
|  | 1440 | 813-B0020 | D112ML | 88.3 | 88.5 | 0.76 | 0.68 |
|  | 960 | 813-C0020 | D112ML | 88.2 | 88.4 | 0.75 | 0.67 |
| 3 | 2905 | 813-A0030 | D100L | 88.5 | 88.6 | 0.88 | 0.85 |
|  | 1440 | 813-B0030 | D112ML | 90.2 | 90.4 | 0.79 | 0.72 |
|  | 960 | 813-C0030 | D132S | 89 | 89.5 | 0.73 | 0.65 |
| 4 | 2905 | 813-A0040 | D112ML | 89.4 | 90.2 | 0.88 | 0.84 |
|  | 1450 | 813-B0040 | D112ML | 89.1 | 90.2 | 0.84 | 0.80 |
|  | 965 | 813-C0040 | D132M | 88.7 | 89.5 | 0.77 | 0.71 |
| 5.5 | 2915 | 813-A0050 | D132S | 91.3 | 91.5 | 0.86 | 0.84 |
|  | 1460 | 813-B0050 | D132S | 90.5 | 90.7 | 0.83 | 0.79 |
|  | 965 | 813-C0050 | D132M | 89.6 | 90.3 | 0.76 | 0.69 |
| 7.5 | 2915 | 813-A0070 | D132S | 91.7 | 91.7 | 0.88 | 0.86 |
|  | 1455 | 813-B0070 | D132M | 91.1 | 91.5 | 0.78 | 0.73 |
|  | 970 | 813-C0070 | D160M | 91.1 | 91.9 | 0.79 | 0.74 |
| 11 | 2925 | 813-A0110 | D160M | 92.6 | 92.9 | 0.91 | 0.90 |
|  | 1465 | 813-B0110 | D160M | 92.3 | 92.4 | 0.81 | 0.77 |
|  | 970 | 813-C0110 | D160L | 91.4 | 92.2 | 0.79 | 0.74 |
| 15 | 2925 | 813-A0150 | D160M | 92.3 | 92.7 | 0.91 | 0.89 |
|  | 1465 | 813-B0150 | D160L | 93 | 93.3 | 0.82 | 0.78 |
|  | 975 | 813-C0150 | D180L | 92.1 | 92.7 | 0.82 | 0.77 |
| 18.5 | 2940 | 813-A0180 | D160L | 93.6 | 93.6 | 0.89 | 0.86 |
|  | 1470 | 813-B0180 | D180M | 93.6 | 93.8 | 0.80 | 0.77 |
|  | 975 | 813-C0180 | D200L | 92.5 | 93.3 | 0.87 | 0.83 |
| 22 | 2955 | 813-A0220 | D180M | 93.9 | 93.9 | 0.89 | 0.86 |
|  | 1480 | 813-B0220 | D180L | 94.1 | 93.7 | 0.79 | 0.74 |
|  | 980 | 813-C0220 | D200L | 93.4 | 93.8 | 0.83 | 0.78 |
| 30 | 2960 | 813-A0300 | D200L | 93.9 | 93.5 | 0.88 | 0.85 |
|  | 1480 | 813-B0300 | D200L | 94.8 | 94.7 | 0.85 | 0.81 |
|  | 980 | 813-C0300 | D225M | 94.3 | 94.7 | 0.83 | 0.80 |
| 37 | 2960 | 813-A0370 | D200L | 94.2 | 93.8 | 0.87 | 0.84 |
|  | 1480 | 813-B0370 | D225S | 94.6 | 94.5 | 0.80 | 0.75 |
|  | 985 | 813-C0370 | D250S | 94.5 | 94.8 | 0.81 | 0.78 |
| 45 | 2975 | 813-A0450 | D225M | 94.7 | 94.4 | 0.89 | 0.86 |
|  | 1480 | 813-B0450 | D225M | 95.1 | 95.3 | 0.82 | 0.80 |
|  | 985 | 813-C0450 | D250M | 94.9 | 94.9 | 0.80 | 0.75 |
| 55 | 2965 | 813-A0550 | D250S | 95.2 | 94.9 | 0.85 | 0.81 |
|  | 1480 | 813-B0550 | D250S | 95 | 95.1 | 0.85 | 0.81 |
|  | 990 | 813-C0550 | D280S | 95.5 | 95.5 | 0.81 | 0.78 |
| 75 | 2970 | 813-A0750 | D250M | 95.5 | 95.4 | 0.86 | 0.84 |
|  | 1485 | 813-B0750 | D250M | 95.6 | 95.9 | 0.84 | 0.80 |
|  | 990 | 813-C0750 | D280M | 95.6 | 95.9 | 0.78 | 0.76 |
| 90 | 2980 | 813-A0900 | D280S | 96 | 95.7 | 0.90 | 0.89 |
|  | 1485 | 813-B0900 | D280S | 95.9 | 95.9 | 0.87 | 0.85 |
|  | 985 | 813-C0900 | D315S | 95.6 | 95.8 | 0.83 | 0.80 |