## Slide 1
An-Najah National University
Faculty of Engineering
Civil Engineering Department
Design of water distribution and sewer collection systems
For Burqa village
Prepared By:
Hussein Fathi Haji
Afif Isam Aqad
Qais Nasser Abed Allkareem
Hisham Hossam Shouli
Supervisor : Dr. Numan Mizyed

## Slide 2: Outline
Introduction
Objective
Study Area
Methodology
Results (Water cad , Sewer cad , Storm cad)

## Slide 3: Introduction
Water distribution network is necessary to provide the water to the residents in the quality and quantity they need the wastewater collection system is important to improve service sanitation
Also we can use storm water to save village from disasters

## Slide 4: Objective
Studying and analyzing the existing water distribution network of Burqa village
redesign network in order to meet the future needs of the residents in Burqa
Design a new wastewater collection system network for the village
Design a new storm collection system network for the village

## Slide 5
Study Area
Topography
Location
climate
Water recourses
population

## Slide 6: Location

## Slide 7
Topography

## Slide 8: Water Resources

## Slide 9: Climate

## Slide 10
Chart: Temperature
| Jun | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec
Mean Temp | 10.4 | 11.2 | 13.4 | 17.1 | 21.4 | 24.8 | 26.1 | 26.8 | 24.8 | 22.1 | 17.3 | 12.7
Min Temp | 6.3 | 6.6 | 8.3 | 11.1 | 14.6 | 17.9 | 19.8 | 20.5 | 18.6 | 15.9 | 11.8 | 8.3
Max Temp | 14.5 | 15.9 | 18.6 | 23.1 | 28.2 | 31.7 | 32.5 | 33.2 | 31.1 | 28.4 | 22.8 | 17.1

## Slide 11
Chart: Rainfall
| JAN | FEB | MAR | APR | MAY | JUN | JUL | AUG | SEP | OCT | NOV | DEC
Rain fall Quantity (mm) | 100.3 | 96.8 | 129.1 | 57.8 | 25.7 | 0 | 0 | 0 | 0 | 4 | 160.7 | 34.1
Evaporation Quantity (mm) | 81 | 85.1 | 130.9 | 146 | 200.2 | 220.4 | 265.2 | 217.4 | 170.1 | 117.9 | 75.6 | 79.1

## Slide 12: Rainfall
Chart: Rainfall
| 1992 | 1993 | 1994 | 1995 | 1996 | 1997 | 1998 | 1999 | 2000 | 2001 | 2002 | 2003 | 2004 | 2005 | 2006 | 2007 | 2008 | 2009 | 2010 | 2011 | 2012
 | 1223 | 863 | 643 | 807 | 648 | 745 | 762 | 289 | 555 | 434 | 720 | 988 | 466 | 657 | 652 | 592 | 448 | 555 | 596 | 621 | 701

## Slide 13: Population
Population in 2007 = 3631
Rate of growth = 2.5 %
Population in 2014 = 4300
Population in 2040
=3631

## Slide 14: Methodology for distribution network
Data Collection
Prepare map by AutoCAD
Model Development
Analysis of existing and future networks
Conclusions and Recommendations
Collects maps ,population etc.
Possess maps
Use WaterCAD.
Velocity & Pressure in future state.
Improve WDN for Burqa village

## Slide 15: Design standards
1- Pressure head:
Maximum pressure: 70 m H2O
Minimum pressure: 15 m H2O
2- Velocity:
Maximum velocity: 2m/s
Minimum velocity: 0.2m/s
3- Water Demand:
120 L/c.d according to WHO
4- Pipes
For dimensioning and design of steel pipes, AWWA-C200-97 was utilized.

## Slide 16: Analysis of Existing network System

## Slide 17: Existing distribution network

## Slide 18: Data input (current supply)
Elevation from contour map
Volume of Tank = 150 m³
Supply = 420 m³/d
Loss = 20 %
Consumption = 336 m³/d

## Slide 19: Pressure of existing network (existing supply)
Chart: pressure

## Slide 20: Velocity of existing network (existing supply)
Chart: Velocity

## Slide 21: Data input (Future Demand)
Elevation from contour map
Demand = 120 L /c.d
Loss = 20 %
Average Daily Demand = 1189 m³/d
By taking
Daily peak factor = 1.5
Hourly peak factor = 2
Maximum Hourly Demand = 149 m³/h

## Slide 22: Pressure of existing network (future supply)
Chart: pressure

## Slide 23: Analysis of Proposed Changes

## Slide 24: Proposed Changes

## Slide 25: Data input (Future Demand)
Elevation from contour map
Demand = 120 L /c.d
Loss = 20 %
Average Daily Demand = 1189 m³/d
By taking
Daily peak factor = 1.5
Hourly peak factor = 2
Maximum Hourly Demand = 149 m³/h

## Slide 26: Pressure of existing network (future supply)
Chart: Pressure

## Slide 27: Velocity of existing network (future supply)
Chart: Velocity

## Slide 28: Conveyance System
Velocity = 1.3 m/s
Diameter = 6 in
Tank2
Tank1
Reservoir

## Slide 29: Pump
the loss in the conveyance line is 10 %
Peaking factor = 1.5
so we need to pump 1968.5 /d (82 /h)
The head loss = 162.5* * * L
By substituting = 17.45 m
TDH = the elevation of tank – the elevation of reservoir + head loss
=591.5 – 434.43 + 17.45 = 175 m
We select pump with 16 stages

## Slide 30: Design of wastewater collection system

## Slide 31: Design standards
1- Cover:
Maximum cover: 5 m
Minimum cover: 1 m
2- Velocity:
Maximum velocity: 3 m/s
Minimum velocity: .6 m/s
3- Slope:
Maximum slope: 15 %
Minimum slope: .5 %

## Slide 32: Data input(Sewercad)
Elevation from contour map
Water Consumption = 120 L /c.d
By taking
Wastewater generation coefficient= 0.8
peaking factor = 4
Total waste water loads= 3150 /d
For material: use PVC
Manning coefficient = 0.013
Section type = circular

## Slide 33: Result

## Slide 34: Slope (sewer network)

## Slide 35: Slope (sewer network)
Chart: Conduits number

## Slide 36: Average cover(sewer network)

## Slide 37: Cover-Average(sewer network)
Chart: Conduits number

## Slide 38: Velocity(sewer network)
Chart: Conduits number

## Slide 40: Design standards
1- Cover:
Maximum cover: 4.5m
Minimum cover: 1m
2- Velocity:
Maximum velocity: 8 m/s
Minimum velocity: 0.6 m/s
3- Slope:
Maximum slope: 12 %
Minimum slope: 0.5 %

## Slide 41: Data input

## Slide 42
Information needed for the design of storm water drainage system
Metrological and hydrological data
Rainfall intensity
Storm duration and occurrence
Return period
2. Topographical data
Elevations
Boundaries of the catchments areas
Point of collection
3. Classification of catchments areas
Run off coefficient = 0.5
4. Type of Materials
PVC
N = 0.013

## Slide 43
Q = C i A
Where;
Q = is the run-off in m3/sec
C = is the Run-off coefficient
i = is the average rainfall intensity in mm/hr,
A = is the drainage area in m2
Rational method

## Slide 44
IDF Curves
Return period =10
Duration=time of concentration

## Slide 45: Software Programs
StormCAD
Civil 3D
GIS

## Slide 46: Result

## Slide 47: Cover-average

## Slide 48: Cover-average
Chart: Conduits number

## Slide 49: Velocity

## Slide 50: Velocity
Chart: Conduits number

## Slide 51: Diameter

## Slide 52: Slope
Chart: Conduits number

## Slide 53: Excavation (Trench dimension)
Width of trench at least 70 cm
Depth of trench at least 120 cm

## Slide 54: Conclusions
Length (km) | Pipe Diameter
14.2 | 8"
14.2 | Total
Number of manholes = 512
Volume of excavation (m3) = 18000
Length (km) | Pipe Diameter
2.0 | 6"
2.2 | 4"
1.2 | 3"
13.0 | 2"
18.4 | Total
Volume of excavation (m3 )= 13000
For water network For sewer network

## Slide 55: Conclusions for storm network
Conduit Description | Length (km)
Circle - 10.0 in | 1.8
Circle - 12.0 in | 1.6
Circle - 15.0 in | 1.0
Circle - 18.0 in | 1.2
Circle - 24.0 in | 0.8
Circle - 30.0 in | 1.0
Circle - 36.0 in | 0.5
Circle - 8.0 in | 6.3
Total Length | 14.2
Number of catch basin = 512
Volume of excavation (m3) = 17000

## Slide 56: Thank you

## Slide 57: Any Questions