## Slide 1
An-Najah National University
Faculty of Engineering
Mechanical Engineering Department
Using Geothermal Energy in Mechanical Buildings System.
Supervisor : Dr. Iyad Assaf
Osaid Assaf
Omar Rizqallah
Mohammed Tumazi
Rafat Basheer

## Slide 2: Description Place project
The tower is located in the suburb of Al- Rayhan in the city of Ramallah / Palestine
rises 874 meters above sea level
within longitude 35.20 east and 31.902 north latitude
wind speed reaches 18.5 meters per second

## Slide 3: Photovoltaic (Solar cell)
Photovoltaic (PV) or Solar cell is an energy conversion system which converts the light comes from the sun into electricity.
The amount of solar radiation varies with the passage of time during the day .
solar cells can work between the hours of 6 a.m. to 6 p.m. and the value of energy generated almost remain within the normal distribution curve compared with the axis of time as shown in the following figure.

## Slide 5: How photovoltaic work?
The solar cells (PV) convert sunlight directly into electricity without the need to heat the air or water.
Photovoltaic cell made from two layers of the semiconductor material is usually silicon. These layers are positive layer p-type and negative layer n-type, and the area between them is called p/n junction.

## Slide 7: The Four General Types of Silicon Photovoltaic Cells are:
Single-crystal silicon.
15% efficient, typically expensive to make (grown as big crystal)
Poly-crystalline silicon (also known as multicrystal silicon) 10–12% efficient, cheaper to make (cast in ingots) .
Amorphous silicon (also known as thin film silicon).
(4–6)% efficient, cheapest per Watt, easily deposited on a wide range of surface type
Ribbon silicon .

## Slide 8: Advantages of Photovoltaic
low-maintenance building and operating cost.
No fuel use .
PV is modular and thus flexible in terms of size and applications .
PV is highly reliable and needs little maintenance.
Long life .
PV has virtually no environmental impact .

## Slide 9: solar thermal energy
There are many applications for the direct use of solar thermal energy like space heating and cooling .
Solar thermal heating.
There are two basic solar systems exist to produce hot water :
Active system : An active pumped system can be either an open loop or closed loop .
Passive system : convert sunlight into usable heat, or store heat for future use, without the assistance of other energy sources.

## Slide 10
Domestic water heating.
The solar thermal collector is a heat exchanger that converts radiant solar energy into heat.
Types of solar thermal collectors :
I- Flate plate collector.
This type of collector is affected by weather and its efficiency decreases if large temperature rises are demanded.

## Slide 12
II- Evacuated Tubular Collectors.

## Slide 13
III- Concentrators

## Slide 14
IV- Batch collectors

## Slide 15
Solar cooling.
Solar assisted air conditioning systems may be classified into closed or open systems.
1- Closed systems: the systems are driven by chillers(which provide chilled water) that is most used in air handling units to supply conditioned air .
2- Open systems Desiccant cooling systems are basically open cycle systems, using water as a refrigerant with direct contact with air.

## Slide 16: Inside and Outside Design condition
Parameters | Tin | To | Tun | Tg | Φin | Φout | Win | Wout
Winter | 23 | 4.7 | 13.85 | 10.7 | 50% | 68% | 9 | 3.8
Summer | 25 | 30 | 28.33 | 35 | 50% | 60% | 10 | 13

## Slide 17: Overall heat transfer coefficient, Uoverall
Uoveral depends on the construction of the unit
Uoverall is given by :-
U=
R total = Ri+ R+ Ro
R= ∑

## Slide 18: External walls construction
 | construction | Resistance [.k/w]
1 | Plaster | 0.025
2 | Cement brick | 0.078
3 | insulation | 0.75
4 | Concrete | 0.114
5 | Stone | 0.041
 | construction | 
1 | Plaster | 0.025
2 | Cement brick | 0.078
3 | insulation | 0.75
4 | Concrete | 0.114
5 | Stone | 0.041
Ri= 0.12 m­2.Co/W , Ro= 0.03 m2. Co/W
Rtot= 1.1505
U=1/Rtot = .8692

## Slide 19: Internal walls construction
 | Construction | Resistance [.k/w]
1 | Plaster | 1.2
2 | Cement brick | 0.95
 | Insulation | 0.04
 | Construction | 
1 | Plaster | 1.2
2 | Cement brick | 0.95
 | Insulation | 0.04
Ri= R0= 0.12 m­2.Co/W
Rtot= 0.0.98
U=1/Rtot = 1.02

## Slide 20: Ceiling construction
Hard Ceiling | Construction | Thickness X(m) | Thermal conductivity K | Resistance .k/w
1 | Asphalt | 0.02 | 0.71 | 0.028
2 | Concrete | 0.05 | 1.75 | 0.029
3 | Insulation | 0.02 | 0.04 | 0.5
4 | concrete | 0.06 | 1.75 | 0.034
5 | Cement brick | 0.18 | 0.95 | 0.18
6 | Plaster | 0.02 | 1.8 | 0.017
Hard Ceiling | Construction | Thickness X(m) | Thermal conductivity K | Resistance .k/w
1 | Gypsum docorate | 0.012 | 0.16 | 0.75
Hard Ceiling | Construction | Thickness X(m) | Thermal conductivity K | 
1 | Asphalt | 0.02 | 0.71 | 0.028
2 | Concrete | 0.05 | 1.75 | 0.029
3 | Insulation | 0.02 | 0.04 | 0.5
4 | concrete | 0.06 | 1.75 | 0.034
5 | Cement brick | 0.18 | 0.95 | 0.18
6 | Plaster | 0.02 | 1.8 | 0.017
Hard Ceiling | Construction | Thickness X(m) | Thermal conductivity K | 
1 | Gypsum docorate | 0.012 | 0.16 | 0.75

## Slide 21
Hard Ceiling:
Ri = 0.1 m­2.Co/W , R0= 0.02 m­2.Co/W
= 1/Rtot = 0.84 W/m2.k
Forth Ceiling:
Ri = 0.21 m­2.Co/W , R0= 0.1 m­2.Co/W
= 1/Rtot = 0.669 W/m2.k
The B.AL door which used here consists of aluminum(60% of area) & glass(40% of area)
= 2.94 W/m2.k , = 6.7 W/m2.k
= 4.44 W/m2.k

## Slide 22: summary of overall heat transfer coefficient for each element
Type | Overall heat transfer coefficient w/m2.K
Outside wall | 0.8692
Internal wall | 1.02
Ceiling | 0.669
Foor | 0.84
Glass | 6.7
Steel door | 5.8
Wood door | 2.4
Balcony door | 4.44

## Slide 23: Heating load sources :
The heating load calculation begins with the determination of heat loss through a variety of building for components and situations.
1- Walls 2- Roofs 3- Windows 4- Doors 5- Basement Walls Basement Floors 6- Infiltration Ventilation

## Slide 24: The Heat load Equation :
In summer :
Tun = Ti+2/3*( To - Ti )
In winter :
Tun = Ti+0.5*( Ti - To )
Tg= Ti+ ( rang from 5 to 10)
Parameters | Tin | To | Tun | Tg | Φin | Φout | Win | Wout
Winter | 22 | 4.7 | 31 | 9.7 | 30% | 70% | 4.9 | 3.7
Summer | 24 | 30 | 28 | 29 | 60% | 52% | 11.2 | 13.9

## Slide 25: The Heat load Equation :
Q = U* A* ( Ti - To )
Vvent = n * value of ventilation
Vinf = (ACH * inside volume *1000) /3600
Qs)vent , inf= 1.2 Vvent,inf*(Ti-To)
Ql)vent , inf = 3 Vvent,inf*(Wi-Wo).

## Slide 26: The Heat load Equation :
Qw = (Mw *cp*(Th – Tc ))/∆t
For air system :
Qbuilding = Qs)cond + Qs)v,inf + Ql)v ,inf
Qboiler = 1.1*Qw

## Slide 27
Cooling load calculation

## Slide 28: Cooling loads classified by Source :
Heat transfer (gain) through the building skin by conduction, as a result of the outdoor – indoor temperature difference.
Solar heat gain (radiation) through glass or other transparent materials.
Heat gains from Ventilation air and/or infiltration or outside air.
Internal heat gain by occupants, light, appliances, and machinery.

## Slide 29: Cooling Load equation :
1 ) For ceiling :
Q=U*A*(CLTD)corr Where:
(CLTD)corr = (CLTD + LM) K + (25.5 – Ti )+ (To – 29.4) Where : CLTD: cooling load factor K:color factor: K=1 dark color K=0.5 light color

## Slide 30: Cooling Load equation :
2) For walls : Q=U*A*(CLTD)corr Where: (CLTD)corr =(CLTD + LM) K + (25.5 – Ti )+ (To – 29.4) Where : CLTD: cooling load factor K:color factor: K=1 dark color K=0.83 medium color K=0.5 light color

## Slide 31: Cooling Load equation :
3)For glass : Heat transmitted through glass Q=A*(SHG)*(SC)*(CLF) SHG: solar heat gain SC: shading coefficient CLF: cooling load factor Convection heat gain: Q=U*A*(CLTD)corr (CLTD)corr = (CLTD)+(25.5 – Ti )+ (To – 29.4)

## Slide 32: Cooling Load equation :
4 ) For people : Qs=qs*n*CLF qL=qL*n where: Qs,QL: sensible and latent heat gain qs,qL: sensible and latent gains per person n: number of people CLF: cooling load factor

## Slide 33: Cooling Load equation :
5) For lighting :
Qs=W*CLF Where: Qs: net heat gain from lighting W:lighting capacity: (watts)

## Slide 34: Cooling Load equation :
6) For equipments :
Qs=qs*CLF QL=qL Qs,QL: sensible and latent heat gain. CLF: cooling load factor

## Slide 35: Geothermal Energy
-Introduction:
Heat from the earth can be used as an energy source in many ways form large and complex power station to small and relatively simple pumping system .This heat energy known as geothermal energy, Then thermal energy is generated and stored in the Earth and determines the temperature that converted to an energy that used for cooling and heating.

## Slide 36
-Heat Pump:
All geothermal exchange systems use devices called heat pumps. Heat pumps are extremely efficient at heating and cooling due to the fact that they move heat as opposed to generating heat. And the efficiency of heat pump is 400%.
-Type of Geothermal Exchange Systems:
1.Vertical loop system:
These type is ideal for area is limited and the depth of drilled
holes between 46 to 138 m.

## Slide 38
2-Horizental loop system:
These type are the most Popular and most effective
Of all geothermal exchange System, and require the
Depth at least 2.5m.

## Slide 40
Thanks for Your Attention