## Slide 1: Analysis and Design of Qarresh and Qutub Center
Prepared by:
Abdulrahman sawalmeh
Basil Al-maani
Reham Thaher
Supmited to:
Dr. Imad Al-Qasim

## Slide 2: Outline
Background Information.
Preliminary Design.
Project Modeling.
Model Checks.
Design.

## Slide 3: Qarresh and Qutub Center

## Slide 4: Information about building
2 blocks .
Total area = 10026 m2.
There is a structural break.
Located in Nablus.

## Slide 5: Floors and areas of the Center
Floors | Areas ( )
Second basement | 942
First basement | 910
First basement's roof | 450
Ground floor | 683
Roof's floor | 668
First floor | 710
Second floor | 732
Third floor | 752
Fourth floor | 762
Fifth floor | 750
Sixth floor | 665
Mezzanine floor | 655
Seventh floor | 495
Eighth floor | 492
Ninth floor | 865
Stairwell | 55
Total areas | 10026
Floors | 
Second basement | 942
First basement | 910
First basement's roof | 450
Ground floor | 683
Roof's floor | 668
First floor | 710
Second floor | 732
Third floor | 752
Fourth floor | 762
Fifth floor | 750
Sixth floor | 665
Mezzanine floor | 655
Seventh floor | 495
Eighth floor | 492
Ninth floor | 865
Stairwell | 55
Total areas | 

## Slide 6: Codes
1. American concrete institute (ACI 318-14).
2. International Building Code (IBC 2015).

## Slide 7: Materials
Reinforced Concrete
Structural type | Fc' ( MPa )
Slab | 24
Column | 28
Beam | 24
footing | 24

## Slide 8: Reinforcement Steel
Yielding strength (Fy) = 420MPa.
Modulus of elasticity (Es) = 200GPa

## Slide 9: Non-structural material
Material | Density KN/m3
Masonry | 26
Sand | 16
Block | 12
Plaster | 23
Tile | 26

## Slide 10
Loads:
Gravity
Lateral
Loads
Dead
Live
Soil
Seismic

## Slide 11
  Gravity Load:
I. Dead Load:
  Slab superimposed dead load= 4.5 KN/m².
II. Live Load:
  The maximum value of the live load which was obtained from table 4-1 in ASCE7-10 is 4.8 KN/m², But we used a live load value of 5 KN/m²

## Slide 12: Lateral load:
  I .Seismic Loads:
1. Mapped Spectral Response Acceleration Parameters:
Ss and S1 parameters were obtained from Spectral Response (Ss=0.375 and S1 = 0.375 ).
2. Site Coefficients and Adjusted Maximum Considered Earthquake (MCEᴿ) Spectral Response Accelerations(SMS & SM1):
By assuming Site Class is B, we obtained values of Fa and Fv from tables 11.4-1 and 11.4-2 in ASCE 7-10 where both coefficients equal 1.
SDs = SMS = = 1 × 0.375 = 0. 75
SD1 = SM1 = = 1 × 0.375 = 0.375

## Slide 13
3.Importance Factor (Ie) and Risk Category:
The risk Category was decided to be Ш from table 1.5-1 in ASCE7-10, so the Importance Factor is equal 1.25 according to table 1.5-2 in ASCE7-10.
4. Seismic Design Category:
According to the tables 11.6-1 and 11.6-2 in ASCE7-10, Since the value of SDs= 0.75, and the Risk Category is Ш. So, it’s found that the seismic design category is D.

## Slide 14
5. Design Coefficients and Factors for Seismic Force-Resisting Systems:
Since the Seismic Design Category is C, considering the type of Seismic Force-Resisting System is Intermediate reinforced concrete moment frame, from table 12.2-1 it’s found that the response modification coefficient (R=6)and over strength factor (Ωo=2.5) and deflection amplification factor(Cd=5).
6. Structure Fundamental Period:
From table 12.8-2 below, it’s found that values of Ct and x equals 0.0488 and 0.75, respectively.
Since = 39.75 m, then T= = 0.82 sec.
T=Cu*Ta = 1.45 * 0.82 = 1.19 sec.

## Slide 15: Preliminary Design

## Slide 16: Preliminary design for Block A
The structural system used is two way solid slab
Slab thickness =250 mm

## Slide 17: Beams
Beam | Dimensions (mm)
Block A | 500*700
Block B | 600*800

## Slide 18
Columns dimensions are shown in the table:
Group No. | Dimensions (mm)
G1 | 600*600
G2 | 850*850
G3 | 1100 × 1100
Columns

## Slide 19
The following figure shows the distribution of columns

## Slide 20: Seismic loading data according to Equivalent Static Method .
X-direction:

## Slide 21: Response Spectrum Function
X-direction

## Slide 22: Model Checks
Compatibility Check:
To ensure that the model will behave as one static unit.

## Slide 23
Equilibrium Checks:
To ensure that the model is satisfied Newton’s Law for statics and equilibrium objects. The checks for block A are in the figure below:
Load Type | Hand Cal. (KN) | SAP2000 Results(KN) | Difference %
SD | 20349 | 20228 | 0.6
Live | 22119 | 21987 | 0.59

## Slide 24
Equilibrium Checks:
To ensure that the model is satisfied Newton’s Law for statics and equilibrium objects. The checks for block A are in the figure below:
Load Type | Hand Cal. (KN) | SAP2000 Results(KN) | Difference %
SD | 25369 | 25223 | 0.38
Live | 27575 | 27416 | 0.384

## Slide 25: Design
After building the 3D model using SAP2000 and make the checks, then we can make the design process and preparing the detailing sheets for all members.

## Slide 26
Slab Design:
Check Slab thickness for shear:
ØVc=0.75 ×××b×d
ØVc: design shear capacity (KN).
Vu: ultimate shear at distance d from face of the support(KN) .
d: effective depth(mm)
b:width of the section(mm).
: concrete compressive strength.
Vc = 0.75* 0.6* √24 * 210 * 1000 * 10^-3 = 128.59 KN

## Slide 27
Shear Values:
Maximum value of V13 V23 in block A

## Slide 28
Shear Values:
Maximum value of V13 V23 in block B

## Slide 29
The maximum shear value of the slab equals 40 kN
ØVc = 128.59 kN > Vu=40 kN  The slab thickness is adequate to resist shear.

## Slide 30
Design for flexure in block A in X- direction

## Slide 31
Design for flexure in block A in X- direction

## Slide 32
Openings:
Minimum area of steel was added in the corners of the openings due to the concentrated load over it
Asmin =0.0018 = 450 mm2.
450/112 = 4.2  use 5Ø12

## Slide 33
The Maximum spacing between main bars According to ACI 318‐14 SECTION (7.6.5):
Smax
S =200 which is less than 750 and 450 so , using S =200 is OK

## Slide 34
Beam Design.
Design for Flexure:
The value of moment of beam ( B1) shown in Figure is taken as sample calculation for block A.

## Slide 35
For maximum positive moment:
For maximum negative moment:
ρ = 0.001
ρmin, use ρmin. use 4 mm.

## Slide 36
Cross Section for Beam:

## Slide 37
Beam Design.
Design for Flexure:
The value of moment of beam ( B3) shown in Figure is taken as sample calculation for block B

## Slide 38
For maximum positive moment:
For maximum negative moment:
ρ = 0.34% use 4 mm.

## Slide 39
Cross Section for Beam:

## Slide 40
Column Design:
According to ACI Code, a structural element with a ratio of height-to-least lateral dimension exceeding three used primarily to support compressive loads is defined as column.

## Slide 41
Column Layout:

## Slide 42
Slenderness Check
This check is required to find out whether columns are long or short.
= = 12 ≤ 34- 12 ≤ 40
Columns have no slenderness, therefore, all columns are shorts columns.

## Slide 43
𝜌 = 1%
. Use cross section (600 × 600) mm.
Use S = 200 mm for practical conditions.
Use 2 10 / 200 mm
Column 1

## Slide 46
Design of footings

## Slide 47
Calculation of footing for C8
= 9880 KN, = 300 MPa, = 12785 KN
Dimension of Footing
Area of Footing = = = 33 m2
Dimension = 5.8m*5.8m
300 =
The new dimension = 8*5 m

## Slide 48
Thickness
Check Shear ᴓ = ᴓ * * *d = 0.75 * * * 1000 * d = 661.43 d
= (L-d) =320* (6.9-d)
Then d=2.3m, h=2.4 m
Check punching shear
= - * = 12785 – (320*7.65) = 10337 KN/m
ᴓ = ᴓ * * *d
ᴓ = 34382 KN/m < , so it’s acceptable

## Slide 49
Long Direction
Moment = = = 7617.6 KN.m
ρ = × {1- )}
ρ = 0.00394
Area of steel = 0.00394 * 1000*2300 =9062
Check Area of steel
Minimum Area of steel = ρ * b * h = 0.0018 *1000* 2400
= 4320
> , so use
Use8 ᴓ38 mm/m
Use1ᴓ38 mm/123mm

## Slide 50
Short Direction
Moment = = = = 2433.6 KN.m
ρ = × {1- )}
ρ = 0.001228
Area of steel = 0.001228 * 1000*2300 =2824.5
Check Area of steel
Minimum Area of steel = ρ * b * h = 0.0018 *1000* 2400
= 4320
< , so use .
Use 4320
Use 5 ᴓ35 mm/m
Use 1 ᴓ35 mm/196mm

## Slide 53
Group | Type of foundation | Dimension | Thickness | Reinforcing
1 | Single footing | 2.5 * 4.5 m | 0.9m | 8ᴓ20/m in long direction 6ᴓ20/m in short direction
2 | Single footing | 5 * 5 m | 1.1m | 8ᴓ20 /m
3 | Single footing | 6.6 * 6.6 m | 1.3m | 7ᴓ25 /m
4 | Single footing | 6.2 * 4 m | 1.1m | 5ᴓ32/m in long direction 4ᴓ25/m in short direction
5 | Single footing رجل بطة | 5.2 * 4 m | 1.3m | 6ᴓ32/m in long direction 5ᴓ25/m in short direction
6 | Single footing رجل بطة | 8 * 5 m | 2.4m | 8ᴓ38/m in long direction 5ᴓ32/m in short direction
7 | Core footing | B=2.6m | 0.9m | 1ᴓ25 /150mm
8 | Exterior shear wall | B=3m | 0.6m | 1ᴓ20/150mm
Group | Type of foundation | Dimension | Thickness | Reinforcing
1 | Single footing | 2.5 * 4.5 m | 0.9m | 
2 | Single footing | 5 * 5 m | 1.1m | 
3 | Single footing | 6.6 * 6.6 m | 1.3m | 
4 | Single footing | 6.2 * 4 m | 1.1m | 
5 | Single footing رجل بطة | 5.2 * 4 m | 1.3m | 
6 | Single footing رجل بطة | 8 * 5 m | 2.4m | 
7 | Core footing | B=2.6m | 0.9m | 1ᴓ25 /150mm
8 | Exterior shear wall | B=3m | 0.6m | 1ᴓ20/150mm