## Slide 1
Structural Re-Design Of Al-Quds Open University (Salfit Branch)
Prepared by:
Aya Anan Ghazal Ayah Osama Braik
Under the supervision of:
Dr. Mohammad Samaaneh

## Slide 2: 3D Architectural Model Of The Project

## Slide 3: 3D Architectural Model Of The Project

## Slide 4: Outline
Introduction
1
Materials
2
Codes and Specifications
3
Loads and Load Combinations
4
5
6
Design for Gravity and Seismic Loads
7
Preliminary Dimensions of Structural Elements
Seismic Analysis

## Slide 5: Introduction

## Slide 6: ● Project Description
-One of Al-Quds Open University 19 branches.
-Educational , Social and Economical importance.
-Total area = 4887.5m²
-Total volume = 19745.54m³

## Slide 7: ● Project Description - Site Plan

## Slide 8: ● Project Description - Blocks

## Slide 9: ● Block(2) Plan View

## Slide 10: ● Floors Heights

## Slide 11: Materials

## Slide 12: ● Materials of Structural Elements:
1) Concrete:
E (MPa) | f'c (MPa) | Unit Weight (γ) (kN/m³) | Element | Material
23025.204 | 24 | 25 | Slabs, Beams | Concrete
24870.06 | 28 | 25 | Columns and Shear Walls | 
18800 | 16 | 25 | Base of Footings | Blinding Concrete
2) Reinforcing steel:
-Yield strength of steel (fy) =420MPa
-Modulus of elasticity (E) =200GPa

## Slide 13: ● Materials of Non-Structural Elements:
2) Masonry Stone {Unit weight (γ) = 27 kN/m³}
3) Tiles {Unit weight (γ) = 27 kN/m³}
4) Plastering {Unit weight (γ) = 20 kN/m³}
5) Mortar {Unit weight (γ) = 23 kN/m³}
6) Hollow Blocks {Unit weight (γ)= 12kN/m³: Partitions and External Walls

## Slide 14: Codes and Specifications

## Slide 15: ● The following codes and specifications were used:
1) American Concrete Institute Code (ACI 318-11).
2) American Society Of Civil Engineers (ASCE 7-10).
3) International Building Code (IBC-2012).
4) Jordanian Code

## Slide 16: Loads

## Slide 17: ● Expected Loads on Structure:
Lateral Loads : Earthquake
Gravity Loads 1) Dead Load: Structure own weight. 2) Live load: 5 kN/m² is used for both blocks.
Occupancy or use | Live load (kN/m²)
Computer rooms | 4.79
Corridors | 4.79
Libraries: Reading rooms | 2.87
Offices | 2.4
Dining rooms and restaurants | 4.79
Gymnasium | 4.79
Classrooms | 1.92
First floor corridors | 4.79
Stadiums and arenas with fixed seats | 2.87

## Slide 18: ● Expected Loads on Structure:
3) Super imposed dead load:
-Floor Layers = 3.1 kN/m²
-Internal partitions = 12*0.1 = 1.2 kN/m²
-Plastering = 0.02*2*20 = 0.8kN/m² Total SD on slab = 3.1+1.2+0.8 = 5.1 kN/m²

## Slide 19: ● Expected Loads on Structure:
Section in Masonry External Wall
External wall weight (Masonry)
=0.04*26+0.15*23+0.2*12+0.02*20= 6.4 kN/m²
For (3.64 meters height) = 6.4*3.64= 23.296 kN/m
For (4.16 meters height) = 6.4*4.16= 26.624 kN/m
External wall weight (Glass)
External wall weight (Glass) = 80 kg/m² = = 0.7848 kN/m²
For (3.64 meters height)= 0.7848 * 3.64 = 2.85 kN/m ≈ 3 kN/m
For (4.16 meters height) = 0.7848*4.16= 3.26 kN/m

## Slide 20: Load Combinations

## Slide 21: ● Load Combinations:
Service Load Combinations | Ultimate Load Combinations
1. D | 1. 1.4D
2. D + L | 2. 1.2D + 1.6L + 0.5(Lr or S or R)
3. D + (Lr or S or R) | 3. 1.2D + 1.6(Lr or S or R) + (L or 0.5W)
4. D + 0.75L + 0.75(Lr or S or R) | 4. 1.2D + 1.0W + L + 0.5(Lr or S or R)
5. D + (0.6W or 0.7E) | 5. 1.2D + 1.0E + L + 0.2S
6a. D + 0.75L + 0.75(0.6W) + 0.75(Lr or S or R) | 6. 0.9D + 1.0W
6b. D + 0.75L + 0.75(0.7E) + 0.75S | 7. 0.9D + 1.0E
7. 0.6D + 0.6W | 
8. 0.6D + 0.7E | 
According to the specifications ASCE7-10, the load combinations that are used in the design are given as follows:

## Slide 22: ● 3D Analysis and Design was conducted using ETABS v16.3

## Slide 23: Preliminary Dimensions of the Structural Member of of Block(2)

## Slide 24: ● Block(2) Plan View

## Slide 25
● First and Second Floor Columns Layout

## Slide 26
● Third and Fourth Floor Columns Layout

## Slide 27
Width (mm) | Depth (mm) | Column name | Column Group
700 | 700 | C21,C28,C29, C22,C18,C35,C36 | 1
500 | 500 | C1,C2,C3,C4,C5,C6,C7,C10 C11,C12,C13,C14,C15,C17, C19,C20,C30,C31,C32,C33, C34,C38 | 2
500 | 250 | C8,C9,C16,C23,C25,C26 | 3
800 | 300 | C24,C27 | 4
● Preliminary Dimensions of Columns

## Slide 28
● Slab Load Path solid slab Slab thickness = 180 mm

## Slide 29
● Preliminary Dimensions of Beams
Beam | B | H
B1 | 300 | 400
B2 | 300 | 500
B3 | 600 | 600
B4 | 400 | 500
B5 | 600 | 600
B6 | 600 | 600
B7 | 300 | 600
B8 | 400 | 500
B9 | 300 | 400
B10 | 300 | 400
B11 | 300 | 600
B12 | 600 | 600
B13 | 600 | 600
B14 | 700 | 700
B15 | 600 | 600
B16 | 700 | 700
B17 | 300 | 400
B18 | 300 | 700
B19 | 300 | 500
TB1 | 300 | 500
TB2 | 300 | 500
TB3 | 300 | 500

## Slide 30: 3D Checks of Block(2)

## Slide 31
● 3D Model

## Slide 32
Element type | M11 | M22 | M12
Beam | 0.35 | 0.35 | 0.35
Column | 0.7 | 0.7 | 0.7
One way slab | 0.25 | 0.25 | 0.25
Two way slab | 0.25 | 0.25 | 0.25
Shear Walls | 0.7 | 0.7 | 0.7
● Modifiers

## Slide 33
● 3D Checks:
-Compatibility Check

## Slide 34
● 3D Checks:
-Equilibrium Check
%of Error | ETABS Value | Manual Value | Load
0.28% | 29113.95 | 29196.5 | Dead
0% | 11141.5 | 11141.5 | Live
0% | 20023.5 | 20023.51 | Superimposed Dead
3.4% | 186.67 | 193.32 | Snow

## Slide 35
● 3D Checks:
-Stress Strain Check (Slab Check)
Wlive = 5 kN/m²
METABS = + 4.2 = 10.13 kN.m
M Manual= = = 10.35 kN.m
%Error = *100% = 2.17 <10% (OK)

## Slide 36
● 3D Checks:
-Stress Strain Check (Beams Check)
Beam ( Label B34) was chosen for this check
Tributary area of Beam(B34) = 17.2m²
M Etabs = + 46.4325 = 64.24 kN.m
M Manual = = = 60.2 kN.m
%of error = = 6.29 %<10% (OK)

## Slide 37: Seismic Analysis

## Slide 38
● Seismic Parameters
1- Risk Category : lll (ASCE7-10)
2- Mapped Acceleration Parameters
Z for Salfit = 0.15
Ss = 2.5 * Z (Israeli Code) = 0.375
S1 = 1.25 * Z (Israeli Code) = 0.1875
Seismic Zone Factor (Z) – Palestinian Seismic Hazard Map - Earth Sciences and Seismic Center (ESSEC) at An-Najah University

## Slide 39
● Seismic Parameters
3- Soil Classification:
Allowable Bearing Capacity (Qall ) = 350 kN/m²
Soil Class (B)
4- Site Coefficients Fa and FV (ASCE7-10)
Fa =1 and FV =1
5- Maximum considered earthquake spectral response accelerations adjusted for site class effects (ASCE7-10) (10% probability of exceedance):
SMS = Fa* SS = 0.375
SM1 = FV * S1 = 0.1875

## Slide 40
6- Design Spectral Acceleration parameters:
SDS = SMS= 0.375
SD1 = SM1 = 0.1875
7- Seismic Design Category
From ASCE7-10 , SDC : C
8- Importance Factor
 From ASCE7-10 (Table 1.5-2), Ie : 1.25
● Seismic Parameters

## Slide 41
● Permitted Analytical Procedures
Table 12.6-1 in ASCE7-10

## Slide 42
● Seismic Parameters
9- Response Modification Factor (R), Deflection Modification Factor (Cd) and Over-strength Factor (Ω0) :
Building Frame System coefficients - Table 12.2-1 - ASCE7-10

## Slide 43
Direction | Shear wall reactions (kN) | Total Base shear(kN) | % of load
X-direction | 3973.63 | 4513.1 | 88%
Y-direction | 3998.61 | 4513.1 | 88.6%
● Structural System Type Determination:
 The structural system is: Building frame system with ordinary reinforced concrete shear walls as assumed.
 Using Equivalent Lateral Force procedure:

## Slide 44
● Equivalent Lateral Force (ELF) Procedure:
1- Base Shear: V = Cs * W (Equation (12.8-1) in ASCE7-10) Cs(seismic response coeff)=
Cs (max) = = 0.17
Cs (min) = 0.044*SDS*Ie ≥0.01
= 0.021 ≥0.01
0.021 < Cs = 0.0937 < 0.17 (OK)

## Slide 45
● Equivalent Lateral Force (ELF) Procedure:
Base Shear: Total(W)= 49749.86 kN
Weight (Manual) (kN) | Load Pattern
26940.98 | Dead
2785.37605 | 0.25*Live
20023.50557 | SD
49749.86 | Total weight (W)
The manual value of base shear (VManual) = Cs * W = 0.0937*49749.86 = 4664.049kN
(VETABS) = 4513.029 kN
%Error = 3.34%

## Slide 46
● Response Spectrum Analysis:

## Slide 47
= 2452.5 = 735.75
● Response Spectrum Analysis:
 ELF base shear = 4513.0921 kN
In x-direction: = 0.72 < 0.85
In Y-direction: = 1.2 > 0.85
Base Shear:

## Slide 48
= 2930 (X) and 3150 (Y) = 735.75 (Both X and Y)
● Response Spectrum Analysis:
Base Shear:
In x-direction: = 0.86 > 0.85
In Y-direction: = 0.97 > 0.85

## Slide 49
● Design Checks:
Period Check: T ≤ Cu * Ta (ASCE)
Ta = Ct*hnx
Ct = 0.0488, x = 0.75
hn = 15.08 m
Ta = 0.0488*15.080.75= 0.3734 sec
Cu*Ta=1.525*0.3734=0.5694 sec
Cu*Ta > Tfundamental = 0.262  OK

## Slide 50
● Design Checks:
Period Check: Period by Rayleigh Method:
T Rayleigh=2𝝿=0.26 second
%error= =*100% =0.76% <5%  OK

## Slide 51
● Design Checks:
Drift Check:
Comparison with code limit | Inelastic Drift(y) | Inelastic Drift(x) | Story
<0.0624 m (OK) | 0.000462 | 0.000474 | Story1
<0.0546 m (OK) | 0.000618 | 0.00065 | Story2
<0.0546 m (OK) | 0.000716 | 0.000758 | Story3
<0.0546 m (OK) | 0.000702 | 0.000724 | Story4
𝞭x=

## Slide 52
● Design Checks:
Vertical irregularities:
Model was checked and there is no
Vertical irregularities in the structure.

## Slide 53
● Design Checks:
Horizontal irregularities:
The structure has only one horizontal
Irregularity type (1a) .

## Slide 54
●Modification Of Model :
CM
CR
CM
CR

## Slide 55
= 2452.5 = 735.75
● Response Spectrum Analysis:
ELF base shear = 4666.72 kN
= 0.85  OK
= 0.85  OK
Base Shear:

## Slide 56
● Design Checks:
Period Check: Cu*Ta = 1.525*0.3734 =0.5694 second
Tfundamental = Tmodel = 0.213sec
Ta > Tfundamental  OK
T Rayleigh=0.21 second
%error= =*100% = 3.33 % <5%  OK

## Slide 57
● Design Checks:
Drift Check:
𝞭x=
Story number | Elastic drift x (m) | Elastic drift y (m) | Inelastic drift x (m) | Inelastic drift y (m) | Comparison
Story1 | 0.000193 | 0.000159 | 0.000386 | 0.000318 | <0.0624>>OK
Story2 | 0.000259 | 0.000209 | 0.000518 | 0.000418 | <0.0546>>OK
Story3 | 0.000281 | 0.000224 | 0.000562 | 0.000448 | <0.0546>>OK
Story4 | 0.00026 | 0.000209 | 0.00052 | 0.000418 | <0.0546>>OK

## Slide 58
● Design Checks:
Structural irregularities:
Model was checked and there is No Vertical nor horizontal irregularities in the structure.

## Slide 59
● Comparison of ELF and Response Spectrum Distribution of Base Shear:
Fx= Cvx * V (ASCE7-10)
Cvx= (ASCE7-10)
Sum Fx | Fx (kN) | Base V (kN) | Cvx | W*hx | K | hx | Weight (kN) | story
4664.05 | 511.291 | 4664.049 | 0.1096 | 50107.63 | 1 | 4.16 | 12045.10 | 1
4152.759 | 1016.409 | 4664.049 | 0.2179 | 99610.28 | 1 | 7.8 | 12770.55 | 2
3136.35 | 1454.677 | 4664.049 | 0.3119 | 142561.5 | 1 | 11.44 | 12461.67 | 3
1681.673 | 1681.673 | 4664.049 | 0.3606 | 164807.6 | 1 | 15.08 | 10928.88 | 4
 |  |  | 1 | 457086.9 | TOTAL |  |  | 
Vertical Distribution of Seismic Forces – As per ASCE7-10:

## Slide 60
● Comparison of ELF and Response Spectrum Distribution of Base Shear:

## Slide 61
● Deflection Check (Serviceability Check):
Table of Deflection Limits – ACI318-11

## Slide 62
λΔ = Equation (9-11) in ACI318-11code)
● Deflection Check (Serviceability Check):
ξ = 2.0 represents a nominal time-dependent factor for a 5-year duration of loading.
The long term deflection(∆LT ) =∆L + ʎ*∆D + ʎT* ∆Ls
= ∆LT =2*(∆ D) + 1.25*(∆ L)
Multiplier of Long Term Deflection – ACI318-11 code

## Slide 63
● Deflection Check (Serviceability Check):
Deflection Check for Slab:

## Slide 64
Panels Number | Dead Deflection {ETABS} (mm) | Superimposed dead deflection {ETABS} (mm) | Live Deflection {ETABS} (mm) | Immediate allowable value (mm) | Long-term allowable value (mm) | Long-term value {ETABS} (mm) | Comment
1 | 4.714 | 5.168 | 5.21 | 20.11 | 30.167 | 22.77 | OK
2 | 5.791 | 6.248 | 4 | 27.5 | 41.25 | 23 | OK
3 | 3.668 | 4.897 | 3.651 | 15.6 | 23.33 | 18 | OK
Deflection Check for Slab:
● Deflection Check (Serviceability Check):

## Slide 65
Deflection Check for Beams:
● Deflection Check (Serviceability Check):
 Immediate Deflection (∆L = 3.694 mm < 55 mm) OK
∆ D = 6.065 mm and ∆ SD = 4.069mm
 Long term deflection (∆LT) =24.9 mm < 41.25 mm (Long-term Deflection is OK).

## Slide 66: Gravity and Seismic Design

## Slide 67
● Design for Gravity and Lateral Loads
The structural system is: Building frame system with ordinary reinforced concrete shear walls and ordinary frames.
The structural members that were designed are: 1- Columns 2- Beams 3- Slabs (One way and two way solid slab) 4- Shear walls 5- Footings 6- Stairs

## Slide 68
● Design for Gravity and Lateral Loads
Design of Columns
1-Sway –Non sway Check :
(Equation (10-10) in ACI318-11 code)
story | Pu | Delta (x) | Vu | Lc | Pu*delta | Vu*Lc | Q | comparison
1 | 12045.1 | 0.000193 | 4664.05 | 4.16 | 2.30 | 19402.45 | 0.0001198 | Q<0.05 (Non-sway)
2 | 12770.55 | 0.000259 | 4152.759 | 3.64 | 3.31 | 15116.00 | 0.0002188 | Q<0.05 (Non-sway)
3 | 12461.67 | 0.000281 | 3136.35 | 3.64 | 3.50 | 11416.30 | 0.0003067 | Q<0.05 (Non-sway)
4 | 10928.88 | 0.00026 | 1681.673 | 3.64 | 2.84 | 6121.30 | 0.0004642 | Q<0.05 (Non-sway)
Stability Index Determination from lateral deflection in X-direction
story | Pu | Delta (y) | Vu | Lc | Pu*delta | Vu*Lc | Q | comparison
1 | 12045.1 | 0.000159 | 4664.05 | 4.16 | 1.92 | 19402.45 | 9.87E-05 | Q<0.05 (Non-sway)
2 | 12770.55 | 0.000209 | 4152.759 | 3.64 | 2.67 | 15116.00 | 0.00017657 | Q<0.05 (Non-sway)
3 | 12461.67 | 0.000224 | 3136.35 | 3.64 | 2.80 | 11416.31 | 0.000244511 | Q<0.05 (Non-sway)
4 | 10928.88 | 0.000209 | 1681.673 | 3.64 | 2.28 | 6121.30 | 0.000373146 | Q<0.05 (Non-sway)
Stability Index Determination from lateral deflection in Y-direction

## Slide 69
● Design for Gravity and Lateral Loads
Design of Columns
2- Slenderness Check :
Sample Calculation: Column (C29)
Pu=1316.5 kN
M1= 75.2 kN.m
M2=192.6 kN.m
 K = 1 (Conservatively)
= = 19.8
34 – 12 * = 34 – 12 * = 29.4
 =19.8< 29.4 < 40  (OK)
Column is consider short.
≤ 34 – 12 * ≤ 40
(Equation (10-7) in ACI318-11 Code

## Slide 70
● Design for Gravity and Lateral Loads
Design of Columns
Vc = 0.17 * (1+ ) λ * *bw * d (Equation (11-4) in ACI318-11 code)
Vu/ᴓ | Vu/ᴓ | Vc | d | h | bw | Ag | Nu | Vu(S33) | Vu (S22) | column
35.33 | 108.00 | 105.74 | 430.00 | 500.00 | 250.00 | 125000.00 | 163500.00 | 26.50 | 81.00 | 50*25
19.33 | 8.13 | 207.77 | 730.00 | 800.00 | 300.00 | 240000.00 | 183700.00 | 14.50 | 6.10 | 30*80
78.67 | 109.47 | 253.09 | 430.00 | 500.00 | 500.00 | 250000.00 | 1080100.00 | 59.00 | 82.10 | 50*50
468.00 | 88.45 | 472.84 | 630.00 | 700.00 | 700.00 | 490000.00 | 1316500.00 | 351.00 | 66.34 | 70*70
Vc > , so minimum shear reinforcement can be used
3- Shear on columns from the seismic load

## Slide 71
Ties in the middle of column | Ties near supports | As | As | As Required | ρ | Width | Depth | Columns | Group
 |  | used | of the | (mm²) |  | (mm) | (mm) | Labels | Number
 |  | (mm²) | column |  |  |  |  |  | 
2 φ10/ 200 mm | 2 φ10/ 100 mm | 4908.74 | 16 φ20 | 4900 | 1% | 700 | 700 | C21,C28 | 1
 |  |  |  |  |  |  |  | C29,C22 | 
 |  |  |  |  |  |  |  | C18,C35 | 
 |  |  |  |  |  |  |  | C36 | 
2 φ10/ 200 mm | 2 φ10/ 100 mm | 2513.27 | 8 φ20 | 2500 | 1% | 500 | 500 | C1,C2, C3,C4 | 2
 |  |  |  |  |  |  |  | C5,C6, C7,C10 | 
 |  |  |  |  |  |  |  | C11, C12, C13,C14 | 
 |  |  |  |  |  |  |  | C15,C17 | 
 |  |  |  |  |  |  |  | C19,C20 | 
 |  |  |  |  |  |  |  | C30,C31 | 
 |  |  |  |  |  |  |  | C32,,C33 | 
 |  |  |  |  |  |  |  | C34,C38 | 
2 φ10/ 200 mm | 2 φ10/ 100 mm | 1608.5 | 8 φ16 | 1250 | 1% | 500 | 250 | C8,C9, | 3
 |  |  |  |  |  |  |  | C16,C23 | 
 |  |  |  |  |  |  |  | C25,C26 | 
2 φ10/ 200 mm | 2 φ10/ 100 mm | 2513.27 | 10 φ18 | 2400 | 1% | 800 | 300 | C24,C27 | 4
● Design for Gravity and Lateral Loads
Design of Columns

## Slide 72
● Design for Gravity and Lateral Loads
Design of Columns
Sample Design (Column C29)
Dimensions : Square (70X70)cm
L= 4.16m
Ultimate Axial (Pu)= 1316.5 kN
Axial Capacity (Ø Pn,max)= Øλ (0.85 fc` (Ag-As) +fyAs) = 7073.76 kN
Reinforcement Ratio = 1%
As = 4900 mm2 (16 Ø 20)

## Slide 73
● Design for Gravity and Lateral Loads
Design of Columns
Sample Design (Column C29)

## Slide 74
● Design for Gravity and Lateral Loads
Design of Beams
Sample calculation (B16)
From ETABS: M+= 347.8141 kN.m  ρ= 0.00332 As = 0.00332*700*640 = 1486.1 mm² (6ᴓ18) ETABS As = 1511 mm² (6ᴓ18) (OK)

## Slide 75
Beams | Width (mm) | Depth (mm) | Φ (Top steel) | Φ (Bottom Steel) | Reinforcement near supports | Reinforcement at the middle
B1 | 300 | 400 | 4ϕ12 | 4ϕ12 | 1φ10/12 | 1φ10/25
B2 | 300 | 500 | 4ϕ12 | 4ϕ12 | 1φ10/12 | 1φ10/25
B3 | 600 | 600 | 6ϕ16 | 6ϕ16 | 1φ10/20 | 1φ10/25
B4 | 400 | 500 | 4ϕ16 | 4ϕ14 | 1φ10/15 | 1φ10/25
B5 | 600 | 600 | 6ϕ16 | 6ϕ16 | 1φ10/20 | 1φ10/25
B6 | 600 | 600 | 6ϕ16 | 6ϕ16 | 1φ10/20 | 1φ10/25
B7 | 600 | 300 | 4ϕ14 | 4ϕ14 | 1φ10/12 | 1φ10/25
B8 | 400 | 500 | 4ϕ14 | 4ϕ14 | 1φ10/15 | 1φ10/25
B9 | 300 | 400 | 4ϕ12 | 4ϕ12 | 1φ10/12 | 1φ10/25
B10 | 300 | 400 | 4ϕ12 | 3ϕ12 | 1φ10/12 | 1φ10/25
B11 | 300 | 600 | 3ϕ16 | 3ϕ16 | 1φ10/20 | 1φ10/25
B12 | 600 | 600 | 6ϕ16 | 6ϕ16 | 1φ10/20 | 1φ10/25
B13 | 600 | 600 | 6ϕ25 | 6ϕ16 | 1φ10/20 | 1φ10/25
B14 | 700 | 700 | 7ϕ20 | 6ϕ18 | 1φ10/20 | 1φ10/25
B15 | 600 | 600 | 6ϕ16 | 6ϕ16 | 1φ10/20 | 1φ10/25
B16 | 700 | 700 | 7ϕ22 | 6ϕ18 | 1φ10/20 | 1φ10/25
B17 | 300 | 400 | 3ϕ12 | 3ϕ12 | 1φ10/15 | 1φ10/20
B18 | 300 | 700 | 3ϕ18 | 4ϕ16 | 1φ10/20 | 1φ10/25
B19 | 300 | 500 | 4ϕ12 | 4ϕ16 | 1φ10/20 | 1φ10/25
TB-1 | 300 | 500 | 3ϕ18 | 4ϕ12 | 1φ10/7 | 1φ10/10
TB-2 | 300 | 500 | 2ϕ25 | 4ϕ18 | 1φ10/5 | 1φ10/7
TB-3 | 300 | 500 | 3ϕ14 | 3ϕ14 | 1φ10/10 | 1φ10/22
● Design for Gravity and Lateral Loads
Design of Beams

## Slide 76
● Design for Gravity and Lateral Loads
Design of Beams
Design Key
Based on the ACI318-11 code in section (21.2.2), Beams shall have at least two of the longitudinal bars continuous along both the top and bottom faces. These bars shall be developed at the face of support.

## Slide 77
● Design for Gravity and Lateral Loads
Design of Beams
Sample Design (B6)

## Slide 78
● Design for Gravity and Lateral Loads
Design of Slab
: Slab check for shear:
ᴓVc = * * 1000*140 = 85.732 kN
All of shear values are < 85.732 kN (OK)

## Slide 79
● Design for Gravity and Lateral Loads
Slab
(Design For Moments): (X-Direction)
Positive Steel: 4∅12/m
Negative Steel: For M=13.1 kN.m or less (4∅12/m) For M= 35 kN.m (5∅14/m) For M= 30 kN.m (4∅14/m)

## Slide 80
● Design for Gravity and Lateral Loads
Slab
(Design For Moments): (Y-Direction)
Positive Steel: 4∅12/m
Negative Steel: For M = 22 kN.m or less (4∅12/m) For M = 24 kN.m (5∅12/m).

## Slide 81
● Design for Gravity and Lateral Loads
Shear wall
Sample Calculation, Shear Wall (W15) Dimensions: L=5050mm ,Thickness=300mm
Pultimate =3252.7kN ,Muy=99kN.m, Mux=1700kN.m Vux=63.9kN , Vuy=918.5kN
Check shear in x-direction: ᴓVc = * * (300-40)* = 804 kN > Vux (OK)
Vc = 1072*0.8 = 857.8 kN

## Slide 82
● Design for Gravity and Lateral Loads
Shear wall
Design for shear in y-direction {Horizontal Reinforcement}: Vs = - Vc = – 857.8 = 366.82 kN  = 0.25  = 0.00038 < 𝜌𝑡 (minimum steel ratio from ACI318-11 code ) = 0.0025  use 𝜌=0.0025 As = 0.0025 *300*5050 = 3787.5 mm²
Assume (2ᴓ12)/250 mm  = = 16.74 (17ᴓ12 in each layer ) (1 ᴓ 12 / 250 mm )

## Slide 83
● Design for Gravity and Lateral Loads
Shear wall
Design for moment Muy:
As = = = 1190.5 mm²
Design for axial force and moment around X axis {Vertical Reinforcement} Shear wall was modeled in ETABS as a column to get the interaction diagram for the shear wall. The column was assigned to concentrated force (Pu = 3252.7 kN) and (Mux= 1700 kN.m)

## Slide 84
● Design for Gravity and Lateral Loads
Shear wall
Interaction Diagram Data Representation in EXCEL Interaction Diagram from ETABS
(1700, 3252.7)
As (from Pu and Mux) = 0.0025 *300*5050 = 3787.5 mm² Total Vertical Steel = 1190.5+3787.5 = 4978 mm² For one layer  = 2489 mm² (17ᴓ14) = (1 ᴓ14 / 250 mm)

## Slide 85
● Design for Gravity and Lateral Loads
Shear wall Shear walls were assigned as piers in ETABS and they were designed as ordinary shear walls. The following table shows the values of horizontal and vertical reinforcement from ETABS
Shear Wall Group | Spacing between bars | Vertical Bars | Vertical Reinforcement (2 layers) | Spacing between bars | Horizontal Bars | Horizontal (2layers) (mm²/m) | Pier# | Wall Label
SW1 | 20 cm | 5∅12/m | 5655 | 30 cm | 4∅12/m | 750 | P1 | W9
SW1 | 20 cm | 5∅12/m | 3393 | 30 cm | 4∅12/m | 750 | P2 | W13
SW1 | 20 cm | 5∅12/m | 5429 | 30 cm | 4∅12/m | 750 | P3 | W15
SW1 | 20 cm | 5∅12/m | 1810 | 30 cm | 4∅12/m | 750 | P4 | W10
SW1 | 20 cm | 5∅12/m | 5429 | 30 cm | 4∅12/m | 750 | P5 | W11
SW2 | 18 cm | 6∅12/m | 3619 | 30 cm | 4∅12/m | 750 | P6 | W14
SW1 | 20 cm | 5∅12/m | 5881 | 30 cm | 4∅12/m | 750 | P7 | W12
SW1 | 20 cm | 5∅12/m | 3845 | 30 cm | 4∅12/m | 750 | P8 | W7
SW1 | 20 cm | 5∅12/m | 2262 | 30 cm | 4∅12/m | 750 | P9 | W21
SW1 | 20 cm | 5∅12/m | 5881 | 30 cm | 4∅12/m | 750 | P10 | W5
SW1 | 20 cm | 5∅12/m | 4072 | 30 cm | 4∅12/m | 750 | P11 | W17
SW1 | 20 cm | 5∅12/m | 4298 | 30 cm | 4∅12/m | 750 | P12 | W18
SW1 | 20 cm | 5∅12/m | 6107 | 30 cm | 4∅12/m | 750 | P13 | W4
SW2 | 18 cm | 6∅12/m | 2262 | 30 cm | 4∅12/m | 750 | P14 | W20
SW1 | 20 cm | 5∅12/m | 5429 | 30 cm | 4∅12/m | 750 | P15 | W1
SW1 | 20 cm | 5∅12/m | 4072 | 30 cm | 4∅12/m | 750 | P16 | W19
SW1 | 20 cm | 5∅12/m | 5203 | 30 cm | 4∅12/m | 750 | P17 | W3
SW1 | 20 cm | 5∅12/m | 6786 | 30 cm | 4∅12/m | 750 | P18 | W2

## Slide 86
● Design for Gravity and Lateral Loads
Shear wall

## Slide 87
● Design for Gravity and Lateral Loads
Footings
1- Single 2- Combined 3-Wall Footings

## Slide 88
● Design for Gravity and Lateral Loads
Footings: Single Footings
Single footing of column (C12)
P service = 1511 kN
P ultimate = 1768.90 kN
P ultimate(including self-weight) = 1768.9 + 0.1*1768.9 = 1945.79 kN
Area of footing:
Afooting = = = 4.32 m² (2.2*2.2 m²)
 New Afooting = 2.2 * 2.2 = 4.84 m²
qu = qu = = 402 kN/m²
L1 = (2.2-0.5)/2 = 0.85 m
L1

## Slide 89
● Design for Gravity and Lateral Loads
Footings: Single Footings
Single footing of column (C12)
L1
Thickness of footing:
Wide beam shear:
ᴓVc = * * 1000*d (1) Vu = qu * (L1-d) (2)
 From (2) and (30), d= 0.85 m
Vu,p = Pu - qu*A1 = 1214.51 kN ᴓVc,p ≤ ᴓ (0.17) * (1+ ) * * b0 * = 8579.71 kN
≤ ᴓ (0.83) * ( ) * * b0 * =87865.98 kN
≤ ᴓ (0.33) * * b0 * = 5551.58 kN > Vu,p = 1214.51 kN (OK)
Punching Shear Check:
 H = 1m

## Slide 90
● Design for Gravity and Lateral Loads
Footings: Single Footings
Design for Flexure :
Mu = = 145.23 kN.m  ρ= 0.000535 < ρmax 0.0155 (OK)
As = 454.75 mm² < As(min) = 1800 mm²  Use As min = 1800 mm² { 1ᴓ16 / 100 mm }  Shrinkage steel {1ᴓ16 / 100 mm }
Checking development length :
Ldt = = 658 mm > 300 mm (OK)
L1 = 0.85
L = 0.85 – 0.05 = 0.8 m > 0.658

## Slide 91
● Design for Gravity and Lateral Loads
Footings: Single Footings

## Slide 92
● Design for Gravity and Lateral Loads
Stairs:
Practical reinforcement for the stairs was used:

## Slide 93
THANK YOU 