## Slide 1
Graduation Project II
Analysis and Redesigned of Water Distribution Network and Design of Wastewater
collection Network for Kefel Haris village.
Amjad Hussam Abu Ya’qoub
Abdull-Raoof shehadeh
Nser Ali Bouzia
Mohammad Lahloh
Prepared By :
Supervision of Eng. Hamees Tubeileh

## Slide 2: Outline: -
✔ Introduction .
✔ Objectives and significance of the work .
✔ Study area .
✔ Methodology.
✔ Modeling, Analysis and Design with their resultd.
✔ Conclusion and recommendation .

## Slide 3: Introduction
Water take a great importance to humans in everyday life most of the activities we do need water. So that demand is continuously increasing, this means increasing the wastewater production, where wastewater constitutes about 85% of water demand .

## Slide 4: Objectives
Analyze the existing water network.
Redesign the water network in the village.
Design the Wastewater network in the village.

## Slide 5: Location

## Slide 6
Study area

## Slide 7: Study area
Location : Kefel Haris is a village that is located 4.5 km north of Salfeet city
Climate : The mean annual maximum temperature is 26.5 ºC and the mean annual minimum is 11.5 ºC.

## Slide 8: Study area
Population : The total population of the villege was 4084 capita in 2017.
Water resources : Water supply of the village is from Macorot.

## Slide 9: Analyzing the Network

## Slide 10: Modeling of WDN

## Slide 11: Network with Thiessen Polygon

## Slide 12
Using load builder being distributed the demand by proportional distribution by area .
We enter a pattern demand.

## Slide 13: WDN
Number of Elements | Elements
1 | Reservoirs
107 | Nodes
119 | Pipes

## Slide 14: WDN
Design constraints:
Pressure at junction between (20-100) m.H2O.
Velocity in pipe (0.1-3.0) m/s.

## Slide 15: Result of analysis of WDN
Pressure at minimum demand (2:00 am).

## Slide 16
Pressure at maximum demand (6:00 am).

## Slide 17
Velocities at minimum demand (2:00 am).

## Slide 18
Velocities at maximum demand (6:00 am).

## Slide 19: Redesign of WDN

## Slide 20: Data of future population
Future population in 2048 =8316

## Slide 21: WDN
Number of Elements | Elements
2 | Reservoirs
109 | Nodes
114 | Pipes

## Slide 23: Reservoirs location
Reservoir 2 coordinates
Reservoir 1&2 location

## Slide 24: Results of WDN for Design
Pressure at minimum demand (2:00 am).

## Slide 25
Pressure at maximum demand (6:00 pm).

## Slide 26
Velocity at maximum demand (6:00 am).

## Slide 27
Velocity at minimum demand (2:00 am).

## Slide 28: Reservoir volume calculations

## Slide 29: Reservoir volume calculations
Chart: volume (m^3)
Cumulative supply | 19.3 | 38.6 | 57.9 | 77.2 | 96.5 | 115.8 | 135.1 | 154.4 | 173.7 | 193 | 212.3 | 231.6 | 250.9 | 270.2 | 289.5 | 308.8 | 328.1 | 347.4 | 366.7 | 386 | 405.3 | 424.6 | 443.9 | 463.2
Cumulative Demand | 31.54 | 40.0558 | 48.5716 | 62.7646 | 76.9576 | 133.7296 | 190.5016 | 233.0806 | 275.6596 | 306.8842 | 338.1088 | 366.4948 | 394.8808 | 426.1054 | 457.33 | 491.3932 | 525.4564 | 582.2284 | 639.0004 | 675.9022 | 712.804 | 735.5128 | 758.2847 | 773.4239

## Slide 31: Design of Wastewater network

## Slide 32
WWCN
Conduites
Manholes
Outfalls
Length <=30
Diameter>=8in
Material (PVC)
Diameter
Drop Manhole
Material
Loads
Elevation
Location
Elevation
Slope

## Slide 33: Data required of Wastewater
Design period 30 years.
Future Population= 8316 capita.
138 L/C-D. water demand.
85% of produced waste water from consumed water.
20% infiltration.
Peak factor calculated by (PHF =5/)=4.
The maximum distance between manholes is 30m.
PVC circular pipes.

## Slide 34: Wastewater Generation Calculations

## Slide 35: Model of the wastewater network

## Slide 36: Manholes Elevation
Using Trex function on sewercad to find the elevation:

## Slide 37: Design constraint
Velocity between (0.6 – 3) m/s.
Cover between (1 –5) m.
Slope between (1 – 12) %.

## Slide 38
Loads on manholes
The load on each manhole = = 8.5m3/day.
The load was entered on the manholes equally through sanitary load control center in SewerCAD program.

## Slide 40: The Outfalls

## Slide 41
All of outfall tends to valley-Qana

## Slide 42: Valley-Qana

## Slide 43: Results

## Slide 44: WWCN
Elements | Manholes | Conduits | Outfall
No. of elements | 481 | 481 | 3

## Slide 45: Conduit Diameter

## Slide 46: Slope Result

## Slide 47: Velocity Result

## Slide 48: Cover Result

## Slide 49: Profile

## Slide 51: Cost estimation

## Slide 52: Cost estimation for water distribution network
Total price ($) | Unit price ($) | Quantity | Unit | 
70,000 | 200 | 350 | M^3 | new reservoir cost
31,414 | 5,9,11,16 | 4249 | M | Pipes cost
35,010 | 12 | 2917.6 | M^3 | excavation
40,855 | 12,25 | 2679 | M^3 | filling(base course &sand)
50,990 | 20 | 2549.5 | M^2 | paving cost

## Slide 53: Cost estimation for Sewer collection network
 | Unit | Quantity | Unit price ($) | Total price ($)
conduits cost | m | 13,718.6 | 8 | 109,749
excavation | m ^3 | 21230.6 | 18 | 382,150
filling (base course &sand) | m ^3 | 22591 | 12,25 | 309,305
manholes cost | number | 481 | 450 | 187,590
paving cost | m^2 | 10,288.9 | 20 | 205,778

## Slide 54: Distribute the total cost of our project to the population over a period of 30 years:

## Slide 55
Total cost of the Sewer collection network = 1,223,435 $
Total cost of the water distribution network= 228,270$.
Total cost of the Sewer collection network and water distribution network = 1,451,700 $
Capital Recovery Factor A given P (A/P) = 0.0544, with an interest rate of 3.5% and n=30 year.
A= 0.0544 * 1,451,700 = 78,973 $/year.

## Slide 57
Conclusion and Recommendation

## Slide 58
As required in the outline to use only gravity feed, which means the use reservoir at the highest point and non-use of pumps.
Because the village small, the demand on junctions was small, so we have many problems in this project such as, the flow is small in the pipes and therefore the velocity is very low.
The separation of the network into two parts led to the separation of the flow and thus the flow is low in the pipes and the velocities are low.
In some pipes the flow was in negative sign that's mean the direction of drawing pipe was inverse, so we can change it by right click on that's pipes and reversed it.

## Slide 59
We design wastewater distribution by gravity flow. As we noticed above, we have some problems related to cover (max), and the diameters, velocity and slopes of all conduits are ok, so to deal with this problem, we have to make some adjustment such as reposition the manholes or add a new manhole at middle of the conduit.
We recommend to use a PVC and a circular sewer pipe because it has many advantages like light, durable, resistant (inert material), easy and fast installation.