## Slide 1: Graduation Project 2 An Experimental Comparison of Bifacial and Monofacial PV Modules in Palestine Climate.
Students: Supervisor:
Ahmad Tabash Dr. Adel Juaidi
Luay Shareef

## Slide 2: Overview
Introduction
Methodology
Solar Module Insulation
Devices
Experimental Data Results
Conclusions

## Slide 3: Introduction
The importance of energy.
Palestine is 100% dependent on neighboring countries for fuel, and 90% for electricity.
The percentage of renewable energy from the energy consumed in Palestine is 11.7% .

## Slide 4: Energy Profile
Solar energy.
Wind energy.
Biomass energy.
Geothermal energy.

## Slide 5: Methodology
The work plan

## Slide 6: Data Sheet
Technology | Model | VOC (V) | ISC (A) | Pmp (W) | η (%)
Bifacial | PS-B72-445 | 49.69 | 11.29 | 445 | 20.5
Monofacial | PS-M72(HC) | 49.49 | 11.30 | 445 | 20.5
ا

## Slide 7: Challenges

## Slide 8: Solar Module Insulation

## Slide 9: Devices
Temperature Measurement by Using Thermocouple Sensors.

## Slide 10: Devices
Irradiance & Power Measurements by Using IV-400.

## Slide 11: Experimental Data
Date | Hour | Tmono (C°) | Tbif (C°) | IrrMono (Watt/m2) | Irr bif (Watt/m2) | Pmono (Watt) | Pbif (Watt)
27.April | 9 | 38.2 | 39.1 | 352 | 422 | 115 | 131
 | 10 | 46.4 | 48.6 | 511 | 649 | 160 | 174
 | 11 | 47.5 | 51.4 | 759 | 772 | 186 | 199
 | 12 | 40.6 | 42.6 | 561 | 641 | 145 | 177
 | 1 | 57.4 | 56.2 | 976 | 993 | 236 | 249

## Slide 12: Experimental Data
Date | Hour | Voc,mono (V) | Voc,Bi (V) | Isc,mono (A) | Isc,Bi (A) | FFmono | FFBi
27.April | 9 | 45.7 | 45.3 | 3.12 | 3.78 | 0.81 | 0.78
 | 10 | 45.4 | 44.8 | 4.43 | 5.19 | 0.8 | 0.78
 | 11 | 45.1 | 44.8 | 5.21 | 6.05 | 0.79 | 0.77
 | 12 | 45.4 | 45.3 | 3.97 | 5.2 | 0.8 | 0.78
 | 1 | 44.7 | 44.5 | 6.69 | 7.41 | 0.79 | 0.77

## Slide 13: Temperature Measurement Result
Chart: Average Daily Temperature
| 3 April | 4 April | 5 April | 6 Apri | 7 April | 10 April | 11 April | 13 April | 19 Apri | 21 April | 25 April | 27 April
Monofacial | 37.4667 | 48.125 | 41.2 | 41.36 | 49.275 | 47.05 | 50 | 43.7667 | 32.675 | 52.3333 | 51.8333 | 46.02
Bifacial | 39.8 | 49.075 | 41.975 | 44.78 | 51.475 | 50.6 | 51.95 | 46.4333 | 35.025 | 53.8167 | 54.6 | 47.58

## Slide 14: Temperature Measurement Result
Chart: Average Weekly Temperature
| 1st Week | 2nd Week | 3rd Week | 4th Week
Monofacial | 43.4853 | 46.9389 | 42.5042 | 48.9267
Bifacial | 45.421 | 49.6611 | 44.4208 | 51.09

## Slide 15: Temperature Measurement Result
Chart: Average Monthly Temperature
| April
Monofacial | 45.4638
Bifacial | 47.6482

## Slide 16: Irradiance Measurement Results
Chart: Average Daily Irradiance
| 3 April | 4 April | 5 April | 6 Apri | 7 April | 10 April | 11 April | 13 April | 19 Apri | 21 April | 25 April | 27 April
Monofacial | 484 | 926 | 767.5 | 744.2 | 854.75 | 758.25 | 925.5 | 862.3333 | 409.75 | 913.3333 | 737.3333 | 631.8
Bifacial | 444.6667 | 931 | 783 | 739.4 | 845 | 736.5 | 919 | 822.6667 | 446.25 | 917 | 736.3333 | 695.4

## Slide 17: Irradiance Measurement Results
Chart: Average Weekly Irradiance
| 1st Week | 2nd Week | 3rd Week | 4th Week
Monofacial | 755.29 | 848.6944 | 661.5417 | 684.5667
Bifacial | 748.6133 | 826.0556 | 681.625 | 715.8667

## Slide 18: Irradiance Measurement Results
Chart: Average Monthly Irradiance
| April
Monofacial | 737.5232
Bifacial | 743.0401

## Slide 19: Power Measurement Results
Chart: Average Daily Power
| 3 April | 4 April | 5 April | 6 Apri | 7 April | 10 April | 11 April | 13 April | 19 Apri | 21 April | 25 April | 27 April
Monofacial | 122 | 213.75 | 189.25 | 177.4 | 197.75 | 180 | 214 | 197.6667 | 113.75 | 233.6667 | 184 | 168.4
Bifacial | 122 | 222.75 | 199.75 | 187.6 | 206.75 | 191.75 | 222 | 219 | 129.5 | 243.6667 | 193.6667 | 186

## Slide 20: Power Measurement Results
Chart: Average Weekly Power
| 1st Week | 2nd Week | 3rd Week | 4th Week
Monofacial | 180.03 | 197.2222 | 173.7083 | 176.2
Bifacial | 187.77 | 210.9167 | 186.5833 | 189.8333

## Slide 21: Power Measurement Results
Chart: Average Monthly Power
| April
Monofacial | 181.7901
Bifacial | 193.7758

## Slide 22: I-V Measurement Results

## Slide 23: Efficiency Measurement Results
Chart: Average Monthly Effeciency
| April
Monofacial | 23.5124
Bifacial | 25.0125

## Slide 24: Conclusions
Monofacial VS Bifacial
Recommendations

## Slide 25
Thank You