## Slide 1: Structural Design of AL-Rehana Building
Prepared By:
Basel Hassan Supervisor :
Majd Barham Dr. Munther Diab
Mo’tasem Saidi
Saleh Se’bas
An-Najah National University
Faculty of Engineering
Civil Engineering Department
Graduation Project II

## Slide 2: Presentation Outline
  Introduction.
  Preliminary Design.
  3D- Modeling & Checks.
  Slabs.
  Design of columns (static).
  Dynamic analysis :
  Dynamic analysis for seismic loading
  Analysis and design of slabs (dynamic)
  Analysis and design of beams (dynamic)
  Analysis and design of columns (dynamic)
  Design of footing
  Special structural elements
  Stairs
  Tie beams

## Slide 3: Introduction
This building consists of five floors described as follows:
The ground floor has a height of 5.4 m , contains stories for commercial uses.
The remaining floors are residential floors, each floor contain two flats , each one has area of 200 .
The Parking is outside the building that is around it.

## Slide 5: Introduction
Structural material :
  Concrete:
  For slabs , beams and column the compressive strength fc = 28 Mpa.
  The unit weight of the concrete is 25kN/m3.
  Steel:
  Steel yielding strength fy = 420 Mpa.
  Concrete blocks:
  The unit weight of the concrete blocks used is 12kN/.

## Slide 6
NonStructural material :

## Slide 7: Introduction
Loads
  Dead loads:
  Static & constant loads, including the weight of structural elements (own weight)
  super imposed dead loads = 3.5 KN/m2
  Live loads:
  Non permanent loads on the structure like weight of people, furniture, water tank & the building content. = 3.5 KN/m2
  Perimeter Wall:
  The weight of the perimeter wall 18 kN/m.

## Slide 8: Introduction
Codes
  The most commonly used code in the modern world that used mainly in Palestine is ACI 318-08 which is used in this project.
  Load combination:
  U1 = 1.4(D.L)
  U2 = 1.2(D.L )+ 1.6(L.L)
  Sap2000 programm , will be used in analysis of the structure.

## Slide 9: Preliminary Design of Slabs
  In this project two slab systems are used which are:
  * One way solid slab.
  * One way ribbed slab.
  slab plan:

## Slide 10: Preliminary Design of Slabs

## Slide 11: Preliminary Design of Slabs strip 1
Solid Slab
Thickness:
h = = = 0.182 m … Use h = 0.20 m
Load :
Wo = 5 KN/m2
Wu = 15.8 KN/m2
Check Shear :
Vu = 38.7 KN
Vc = 112.4 KN ….. OK
Ribbed Slab
Thickness:
h = = = 0.237 m … Use h = 0.25 m
Load :
Wo = 4.55 KN/m2
Wu = 15.26 KN/m2
Wu (ribbed) = 15.26 ( 0.52 ) = 7.94 KN/ m
Check Shear :
Vu = 16.5 KN
Vc = 17.46 KN ….. OK

## Slide 12
Preliminary Design of Slabs strip 1
Solid Slab
Ribbed Slab

## Slide 13: Preliminary Design of Beams Beam 1
Solid Slab
Thickness
= = 0.22 m ….. Use 0.3 m
Loads :
W0 = 3.75 KN/m
Wu = 63.75 KN/m
Check Shear:
Vu = 122.4 KN
Vc = 86 KN < Vu
Vs = Vn – Vc = 48.5 KN
Use 1ø 10/120 mm
Ribbed Slab
Thickness
= = 0.22 m….. Use 0.25 m
Loads :
W0 = 3.75 KN/m
Wu = 61.27 KN/m
Check Shear:
Vu = 124.1 KN
Vc = 83.3 KN < Vu
Vs = Vn – Vc = 54.5 KN
Use 1ø 10/100 mm

## Slide 14: Preliminary Design of Beams Beam 1
Solid Slab
Ribbed Slab

## Slide 15
Structural element | modifier
Column &shear walls | 0.70
Slabs | 0.25
Beams | 0.35
3D-Modeling & Checks
Modifier values for different structural elements.

## Slide 16: 3D-Modeling & Checks

## Slide 17: 3D-Modeling & Checks Modifier calculations for ribbed slab
For Y direction :
= 0.423
= 0.631
= 0.423
= = 0.423
= = 0.631
= 0.01896
= 0.25
= = 0.01896
Weight modifier = = = 0.963
Mass modifier = 0.963
For X direction :
= 0.631
= 0.423
= 0.423
= = 0.631
= = 0.423
= 0.25
= 0.01896
= = 0.01896
Weight modifier = = = 0.963
Mass modifier = 0.963

## Slide 18: 3D-Modeling & Checks
Compatibility:
The structure works as one unit is verified.

## Slide 19: 3D-Modeling & Checks
Solid Slab
Equilibrium: (5% acceptable)
Slab weight = 9665.5 KN
Columns weight = 2145 KN
Beams weight = 4462.72 KN
Shear wall weight = 911.63 KN
External Walls = 7785 KN
Total dead load(by hand) = 24969.9 KN Total dead load (from SAP) =25107.737 KN
Difference %=[(25107.737 -24969.9)/ 25107.737] *100%=0.55% <5% so it is Ok

## Slide 20: Design of Columns (Static)
We will take the columns that have the same dimension and design them together, so there are two groups of columns which there are 20*55 & 30*55
Pu=0.8Ф[0.85f'c(Ag-As)+Fy*As]=
Ф=0.65 for tied columns.
f'c=28 Mpa
As=ρ*Ag
Assume ρ=0.01 (economical percentage of steel)
Fy=420 Mpa

## Slide 21: Design of Columns (Static) Sample Calculation
The group of (20*55):
The max. load that we found in this group is 1254.30 KN
1254.30*10^3 = 0.8*0.65 [0.85*28 ((550*200)-As)+ 420*As]
As = 521.64 mm2 use 6Ф12
For stirrups:
use Ф8 mm stirrup:
And a spacing S between the stirrups is the minimum of:
16 *db =224 mm
48 *ds =384 mm
use Ф8mm /200mm.

## Slide 22: Dynamic Analysis Dynamic analysis for seismic loading
The main methods of dynamic analysis are the response spectrum analysis and the time- history analysis. UBC 97 code and response spectrum analysis are used in this project for seismic loads.
Manual computations from UBC 97 code are use with
appropriate factors Ca, Cv, R, I, and Z.
1.Introduction

## Slide 23: Dynamic Analysis Dynamic analysis for seismic loading Main factors according to UBC 97 code: Z= seismic zone factor, for Tulkarem city (Zone 2A); Z= 0.15
2. Seismic Loads

## Slide 24
Dynamic Analysis Dynamic analysis for seismic loading
I= importance factor. From Table 16K (UBC 97), I= 1
R= numerical coefficient representative of the inherent over strength and global ductility capacity of lateral- force- resisting systems.
R = 6.5 (Dual systems concrete shear walls with IMRF) according to Table 16-N in the UBC97
Soil is rock so soil profile type SD from Table16-J (UBC 97)
Ca=acceleration seismic coefficient, from Table 16-Q (UBC 97) Ca=0.22
Cv= velocity seismic coefficient, from Table 16-R (UBC 97) Cv=0.32
2. Seismic Loads

## Slide 25
Dynamic Analysis Dynamic analysis for seismic loading
Definition of response spectrum function:

## Slide 27
For modal mass participation ratio

## Slide 28
3. Total base shear V check
Total base shear can be calculated manually by this equation:
Substitute Wd = 35010 KN, Cv = 0.32, Ca= 0.22, I=1, T =0.55 s
For R =6.5 ￫ V = 3671.4 KNVmax ( 2962KN)
So Use Vmax. = 2962 KN

## Slide 29
4. Period T Check:
The following equation is used to check T:
T= Ct (hn)3/4 where:
hn is the height of structure in meters = 4 floor *3.25m + 5.4m = 18.4 m
Ct is a constant = 0.03 , but we devide on 0.3048 to convert for foot .
Then T= 0.645 seconds.
T model 0.622 sec is nearly equal relative to 0.645 sec .

## Slide 30
When we applied 1 KN/m2 on the structure another more accurate equation is used to check T result:
By relouf method
T = 2 = 0.55 Sec

## Slide 31: Dynamic Analysis Analysis and design of slabs (dynamic) Shear force contour
Check For Shear

## Slide 32: Dynamic Analysis Analysis and design of slabs (dynamic) The maximum shear force at distance d/2 from face of support = 34.6 KN. ØVc= 0.75 × 1/6 (√28 ×170×1000) /1000 ØVc =112.4 KN Vu =34.6 KN ØVc=112>Vu=34.6 no need for shear reinforcement.

## Slide 33: Dynamic Analysis Analysis and design of slabs (dynamic)
M22 contours diagram

## Slide 34: Dynamic Analysis Analysis and design of slabs (dynamic)
Design of flexure

## Slide 35
Dynamic Analysis Analysis and design of beams (dynamic)
Third basement Beams Dimensions

## Slide 36
Dynamic Analysis Analysis and design of beams (dynamic)
Critical beam in group B1 (300*500)

## Slide 37
Dynamic Analysis Analysis and design of beams (dynamic)
Critical beam in group B2 (300*400)

## Slide 38
Dynamic Analysis Analysis and design of beams (dynamic)
Critical beam in group B3 (300*300)

## Slide 39
Dynamic Analysis Analysis and design of beams (dynamic)
This pictures show the differents in inflection points , moments and shear between static and dynamic :
Static
Dynamic

## Slide 40
Dynamic Analysis Analysis and design of columns (dynamic)

## Slide 41
Design OF Footings
Single Footing Design:
F’c =28 Mpa, Fy=420Mpa
qall=300 kN/m2
Taking footing F1 Column #6 to be calculated:
Column dimensions (55*30) cm

## Slide 42
Design OF Footings
Footings Dimension & Reinforcement

## Slide 43
SPECIAL STRUCTURAL ELEMENTS
1. Stairs Design
F’c = 28Mpa
Fy =420Mpa.
SID Load = 3kN/m2.
Live load = 4kN/m2.
# of running = 4.2/ 0.28 = 15
# of rising =2.75/0.17 = 16
# of steps for one flight = 15 steps

## Slide 44
Thickness of the stairs :
Assume simply supported slab:
hmin = 0.85*(L/20)
= 0.85*(4.2/20)
= 0.18 m …… Take h=20cm with cover 3cm
SPECIAL STRUCTURAL ELEMENTS

## Slide 45
SPECIAL STRUCTURAL ELEMENTS
2. Tie Beam design:
Tie Beam at X-direction (exterior beam):
Materials:
f’c=28 Mpa.
fy=420Mpa.
Loads:
Wall load=18KN/m.
Ultimate load from ground slab=1.2(0.1*25+3.5) + 1.6(3.5)=12.8KN/m2
Beam Dimensions:
Width=250mm.
Depth=500mm.
Flexure Design:
-For Mu=58.52 KN.m
ρ=0.00314<0.0033
As=0.0033*250*450
= 371 mm2  Use ( 3φ14 )
Since ρ for maximum moment < ρmin  use ρmin for all moments

## Slide 46
Thank You All
for your attention
