## Slide 1: Design of a wastewater collection network for Urif Village
Prepared by: Heba Daraghmeh. Mariam Sabbah.
Supervisor: Dr.Mohammad AL Masri

## Slide 2: Introduction
Water is the most important substance for humans life, people consume water and produce wastewater. The traditional way in Palestine to dispose of wastewater is cesspits which have serious environmental and economical problems.

## Slide 3: Introduction
The suitable way to dispose of wastewater is wastewater collection network.

## Slide 4: Objectives
Design a wastewater collection network for Urif Village using SewerCAD.
Estimate the cost of the construction of this network.
Determine the best location of the WWTP

## Slide 5: Methodology
Define the problem
Collect data for the study area
Preparing profiles
Training on SewerCAD
Design WWCN
Estimate the cost of WWCN
Determine the best location of WWTP
Selection of the study area

## Slide 6: Selection of the study area
Available data
The place where one of us lives
There is no WWCN in it

## Slide 7: Description of the study area
location
Topography
population
climate

## Slide 8: Location

## Slide 9: Population

## Slide 10: Climate
year | Dec | Nov | Oct | Sep | Aug | Jul | Jun | May | Apr | Mar | Feb | Jan | Month
21.9 | 16.4 | 21.6 | 25.7 | 26.6 | 28 | 29.6 | 28.1 | 25.5 | 20.8 | 16.1 | 12.1 | 12.4 | average high c
17.8 | 13.1 | 17.5 | 20.5 | 22.5 | 24.4 | 24.8 | 24 | 20.7 | 16.6 | 11.9 | 8.8 | 9 | daily mean c
13.3 | 9.3 | 13.8 | 16.4 | 17.5 | 19.1 | 18.8 | 17.4 | 15.2 | 11.8 | 8.2 | 6.1 | 6.2 | average low c
656 | 158 | 60 | 17 | 2 | 0 | 0 | 0 | 5 | 34 | 90 | 135 | 115 | average precipitation(mm)
62.7 | 69 | 54 | 62 | 73 | 62 | 65 | 50 | 47 | 55 | 66 | 75 | 74 | average relative humidity%

## Slide 11: Data collected
contour map and the roads network.
other data like population, topography and roads slope.

## Slide 12: Why SewerCad?
  SewerCad has the ability for both design and analysis of the network.
  Import and export AutoCAD , Excel and GIS files.
  Profiles can be made using it.

## Slide 13: Development of the WWCN

## Slide 14: Development of WWCN

## Slide 15: Calculation of population
Constant growth rate method.
Geometric growth phase.
Arithmetic growth phase.
Declining growth phase.

## Slide 16: Geometric growth phase
the equation is:
P(t)=Po
P(2016)=P(2007)
3545=2921
From this equation k =.0215. the population after 30 years : P(2046)=P(2016) P(2046)=3545
Then P(2046)=6756 persons. the area of Urif=110000 . the population density =6756/1100000 =.00615 c/

## Slide 17: Load per manhole
Thiessen polygon method.
Equal distribution method.
Gravity distribution method.

## Slide 18: Gravity distribution method

## Slide 19: Load calculation
Load per manhole = Population per manhole (water consumption x% of wastewater generation x PHF + infiltration x water consumption x% of wastewater generation)
where: water consumption: 125 L/c.d.
% of waste water generation= 80%.
PHF=(2-4) use 4.
Infiltration =5%.

## Slide 20: Load calculation
Load\manhole (m3\d) | Pop\manhole | Population density (c\m2) | Area (m2) | Infiltration (%) | PHF | % waste of water consumption | Water consumption (L\c.d) | LABEL
132.84 | 328 | 0.00615 | 53220 | 5 | 4 | 80 | 125 | MH-1
46.98 | 116 | 0.00615 | 18707 | 5 | 4 | 80 | 125 | MH-2
59.535 | 147 | 0.00615 | 23761 | 5 | 4 | 80 | 125 | MH-3
54.27 | 134 | 0.00615 | 21668 | 5 | 4 | 80 | 125 | MH-4
30.78 | 76 | 0.00615 | 12241 | 5 | 4 | 80 | 125 | MH-5
24.705 | 61 | 0.00615 | 9835 | 5 | 4 | 80 | 125 | MH-6

## Slide 21
Design constraints
velocity
slope
Cover depth

## Slide 22: Solving the problems of cover depth and velocity

## Slide 23: Determining the location of WWTP

## Slide 24: Determining the location of WWTP

## Slide 25: Determining the location of WWTP

## Slide 26: Criteria for choosing WWTP
weight | Constraints
10 | Environmental
15 | Economical
20 | Close to the services
15 | Not in sensitive areas
20 | Availability of infrastructure
20 | Political

## Slide 27: Criteria for choosing WWTP
So the best alternative is B3
Evaluation |  |  | Constraints
Site B2 | Site B1 | Site B3 | 
5*10 | 10*10 | 5*10 | Environmental
10*15 | 10*15 | 10*15 | economical
10*20 | 10*20 | 10*20 | Close to the services
10*15 | 10*15 | 10*15 | Not in sensitive areas
10*20 | 10*20 | 10*20 | Availability of infrastructure
5*20 | 5*20 | 10*20 | political
850 | 900 | 950 | Total

## Slide 28: Cost of constructing the WWCN
Cost
Labor
Material
Manholes
Pipes
Excavation
Pavement
Sand
Manholes
Pavement ($\m2)
Pipes ($\m)
Sand ($\ m3)

## Slide 29: Cost of material for WWCN
$ Cost | Material
50954 $ | Manholes
39116 $ | Pipes
48774 $ | Excavation
$ 48006 | Pavement
$ 14580 | Sand
$ 201430 | Material total cost

## Slide 30: Cost of labor for WWCN
$ Cost | Cost per unit | Material
4890 $ | 30 $\man | Manholes
53340 $ | 15 $\m | Pipes
$ 40005 | 15 $\m2 | Pavement
$ 1778 | 5 $\m3 | Sand
100013 $ |  | Labor total cost

## Slide 31: Results
Count | 
162 | Manholes
161 | Conduits
1 | Outfalls

## Slide 32: Results
Results of manholes:
Hydraulic Grade Line (In) (m) | Depth (Structure) (m) | Structure Type | Diameter (m) | Flow (Total Out) (m³/day) | Elevation (Invert) (m) | Elevation (Rim) (m) | Elevation (Ground) (m) | Label
523.34 | 2.46 | Circular Structure | 0.9 | 1,071.63 | 523.25 | 525.7 | 525.7 | MH-1
528.44 | 1.2 | Circular Structure | 0.9 | 938.79 | 528.35 | 529.55 | 529.55 | MH-2
532.64 | 1.2 | Circular Structure | 0.9 | 891.81 | 532.55 | 533.76 | 533.76 | MH-3
536.42 | 1.2 | Circular Structure | 0.9 | 832.27 | 536.34 | 537.54 | 537.54 | MH-4
539.93 | 1.2 | Circular Structure | 0.9 | 778.01 | 539.85 | 541.05 | 541.05 | MH-5
542.55 | 1.2 | Circular Structure | 0.9 | 747.23 | 542.47 | 543.67 | 543.67 | MH-6

## Slide 33: Results
Results of conduits:
Velocity (m/s) | Flow (m³/day) | Manning's n | Diameter (in) | Slope (%) | Invert (Stop) (m) | Invert (Start) (m) | Cover (Stop) (m) | Cover (Start) (m) | Length (Scaled) (m) | Stop Node | Start Node | Label
2.34 | 938.79 | 0.013 | 8 | 12.877 | 528.35 | 524.5 | 1 | 1 | 30 | MH-2 | MH-1 | CO-1
2.37 | 891.81 | 0.013 | 8 | 14.076 | 532.55 | 528.35 | 1 | 1 | 29.8 | MH-3 | MH-2 | CO-2
2.25 | 832.27 | 0.013 | 8 | 12.794 | 536.34 | 532.55 | 1 | 1 | 29.7 | MH-4 | MH-3 | CO-3
2.15 | 778.01 | 0.013 | 8 | 11.878 | 539.85 | 536.34 | 1 | 1 | 29.4 | MH-5 | MH-4 | CO-4
1.92 | 747.23 | 0.013 | 8 | 8.872 | 542.47 | 539.85 | 1 | 1 | 29.5 | MH-6 | MH-5 | CO-5
1.89 | 722.52 | 0.013 | 8 | 8.818 | 545.1 | 542.47 | 1 | 1 | 30 | MH-7 | MH-6 | CO-6

## Slide 34: Results
Results of outfall:
Flow (Total Out) (m³/day) | Elevation (Invert) (m) | Elevation (Rim) (m) | Elevation (Ground) (m) | Label
1,071.63 | 518.95 | 520.15 | 520.15 | OF-1

## Slide 35: Results

## Slide 36: Results

## Slide 37: Results

## Slide 38: Results

## Slide 39: Results

## Slide 40: Conclusion
We highly recommended of constructing the WWCN for its advantages
The total cost of constructing the WWCN is 301,443 $
The total length if the network conduit is 3556 m
The unit cost is 85$ per meter