## Slide 1
Water desalination system
BY Solar electric powered
Reverse osmosis
By
Safa Ateeli & Nour Hannon
Supervisor
Prof. Dr. Marwan Mahmoud

## Slide 2: Introduction
Water and energy are the major factors necessary for the development Of social and economic sectors in rural areas .Palestine has a large number Of rural villages lacking water and electricity networks connecting these Villages with electric grids of the nearest cities is nearly impossible, due to their remoteness, low population count and low Electric energy demands. On the other hand Palestine has one of the highest Solar energy potential of all the countries in the world. It enjoys over 2800 Hours of sunshine every year; with an annual average daily solar radiation Intensity amounting to 5.4kWh\m2-day .brackish water is available in very Large amount in some areas of Palestine, particularly in Jordan valley.

## Slide 3: Project Aims
This project investigates the following:
Determine the performance of reverse osmosis water desalination systems powered by solar electric energy under Palestine weather and environmental conditions.
study the system design and sizing
Determine the techno-economic feasibility of using solar electric systems

## Slide 4: Desalination
Desalination is a separation process used to reduce the dissolved salt content of saline water to a usable level.
The desalination plants presently producing fresh water from saline water are operating mainly on the processes: multistage flash (MSF), vapor compression (VC), electro dialysis(ED) and reverse osmosis (RO).

## Slide 5
Process Name | Electrical energy requirements | Thermal energy requirements
RO | 5 KWh\m3 (3500ppm) 15KWh\m3 (35,000ppm) | -
MSF | 3-5 KWh\m3 | 60-80 KWh\m3
MED | 2.3 KWh\m3 | 60-80 KWh\m3

## Slide 6: Why reverse osmosis?
RO plants have a very high space/production capacity ratio
low maintenance, nonmetallic materials are used in construction.
Energy use to process brackish water about 5KWH\m3.
The processing system is simple; the only complicating factor is finding or producing a clean supply of feed water to minimize the need for frequent cleaning of the membrane.
The technology makes minimal use of chemicals.

## Slide 7: reverse osmosis
Osmosis is the passage of water across a membrane from an area of a high concentration to an area of low concentration

## Slide 8: Reverse Osmosis modules
There are four different types of reverse osmosis modules, which are used for reverse osmosis processes :
cost & energy
Tubular
Plate & frame
Hollow fiber
Spiral

## Slide 9: schematic diagram of PV powered RO water desalination system
1-Solar Generator. 2- DC\DC Convertor. 3- Battery Block. 4-DC\AC Three Phase Inverter.
5- Transfer Pump. 6- High pressure pump. 7- Anti.Scalent pump. 8- RO Module.
9- Multi Media-Sand filter. 10-Cartridge Filter. 11- Product Water Storage.
12- Product Water pumps. 13- Regulator Valves. 14-Starting Valves.
15- Chemical Tank. 16- Water Well.

## Slide 10: System steps
The brackish water is fed by the well pump in to the raw water storage tank .
Raw water passes through sand filter and cartridge filter to remove excess turbidity or suspended solids.
The RO- modules are served by high pressure piston pumps of 1000 liters\h capacity at 7.7 bars.
The feed water is distributed across the membranes by means of transverse stream filtration and By this apart of the water is desalinated as it permeates the membranes.
The remaining brine is Drained off. The pure water flows from the modules to a storage tank.
the product water is stored in intermediate tank.

## Slide 12: Design Procedure
First: we enter the feed water data (ions (mg\l)) from Zbaidat tank into ROSA program:
Then, we specify the feature of operation as:
Recovery =65%.
Feed flow=1.53 m3\h.
Permeate flow=1.0 m3\h.
Operating temperature =25 C.
One stage in pass.
Operating time =10 h\day.
Name | Feed(mg\l) | Name | Feed(mg\l) | Name | Feed(mg\l)
NH4 | 0.00 | Sr | 0.00 | SO4 | 157.00
K | 13.10 | Ba | 0.00 | SiO2 | 21.60
Na | 483.00 | CO3 | 1.81 | Boron | 0.46
Mg | 146.00 | HCO3 | 305.00 | CO2 | 7.85
Ca | 200.00 | Cl | 36.00 | TDS | 2566.15
Feed flow
Concentrate flow
Permeate flow

## Slide 13: After that we will see ROSA system simulation as:
Name | Feed(mg\l) | Concentrate | Permeate
NH4 | 0.00 | 0.00 | 0.00
K | 13.10 | 30.46 | 3.90
Na | 483.00 | 1347.50 | 24.81
Mg | 146.00 | 413.82 | 4.05
Ca | 200.00 | 567.12 | 5.42
Sr | 0.00 | 0.00 | 0.00
Ba | 0.00 | 0.00 | 0.00
CO3 | 1.81 | 13.34 | 0.00
HCO3 | 305.00 | 834.83 | 15.50
No3 | 36.00 | 75.56 | 15.03
CL | 157.00 | 3440.50 | 43.67
SiO2 | 21.60 | 61.25 | 0.58
Boron | 0.46 | 0.59 | 0.39
CO2 | 7.85 | 12.00 | 8.75
TDS | 2566.15 | 7236.03 | 117.84

## Slide 14: After this simulation we obtain the output power of the motor equal to 0.8 KW\m3
Hydraulic pump calculation :
Efficiency (Ƞ)= output Power \ input power
Power output Hydraulic = 800*0.42 =336 W
Power input motor = 800 \ 0.75 =1066.6 W
If we take safety factor about 20%, then:
Actual Power for motor = 1279.2 W , we will take it equal 1300W
Pump specification: 1.694m3\h at 88.36m (from ROSA program)

## Slide 15: Transfers pump calculation:
Pump specification: 2.5 m3\h at 3.79 bar
2.5 m3\h at 38.63 m Head
Power output transfer pump = 2.72 * Q (m3\h)*h(m)
= 2.725*2.5*38.63 = 263.19W
Power input transfer pump= 263.19 \ 0.42 = 626.6 W
Power input motor = 626.6 \ 0.75 =835.5 W
Anti scalent pump calculation:
Its small pump, single phase so we choose its power equal to 250W.

## Slide 16: Sizing of the PV generator :
The peak power of the PV generator Power PV is obtained as follow:
Power PV = Ed \ Ƞv * Ƞr *PSH
Where,
Ed: daily energy consumption =25116 Wh\day.
Peak sun hours (PSH)=5400(annual average daily solar radiation Intensity)\1000 Peak sun hours (PSH)= 5.4 hours \ day.
Ƞv: efficiency of inverter =95%.
Ƞr: efficiency of convertor =97%.
Power PV = [(1300+836+250)\0.95] Wh \ 5.4Wh =4795 Wp.
To install this power, amono-crystalline PV module type SM55 of across area of
A pv =0.4267m2 Rated at 12 VDC and a peak power of 50Wp are selected.
The number of the necessary PV modules (N pv module) is obtained as:
N pv module = P pv \ P mpp.
N pv module =4795 \ 50 =96.
P pv actual = 96*50 = 4800Wp=4.8 KWp.

## Slide 18: Sizing the battery block :
The storage capacity of battery block for such system is considerable large. Therefore, special Lead-acid battery cells (block type) of long life time (larger than 10years), high cycling stability Rate (>1000times) and capability of standing very deep discharge should be selected.
The ampere hour Capacity (CAh) and watt hour capacity (C wh) of the battery block, necessary to cover the load Demands for a period of 1 day without sun, is obtained as follow:
C Ah = Ed \ Ƞ battery * DOD *V B
= 2511.6 Wh \ 0.85 *0.8 *48
=770 Ah
C wh = C Ah * V
=770 * 2
= 1.54 KWh\cell.
C wh total = 1.54 * 24 = 36.96 KWh.

## Slide 19: The charge regulator and inverter :
The charge regulator (CR) is necessary to protect the battery block against deep discharge and Over charge. Input\output rating of charge regulator are fixed by the output of the PV array and VB. In this case the appropriate rated power of CR is 5 KW with maximum power tracking. The Input of inverter have to be match with the battery block voltage so the appropriate rated power Is 3.2 KW, 3.8 KVA (non sinusoidal).
5KW
4.8 KWp
3.2 KW, 3.8 KVA
C wh total = 36.96 KWh

## Slide 20: ECONOMIC EVALUATION OF RO UNIT POWERED BY PV SYSTEM
First: Cost annuity
To determine the average annual cost of the water treatment system, it depends on common economic parameter. These parameters are listed below:
Plant life time is 20 years.
Operating days per year are 365 days.
Interest rate is 8%.
Capacity(M)=10m3/day
Salvage value of the units will be 5000$.

## Slide 21: Capital Cost
No | Component, material or work. | quantity | Unit price ($) | Total price ($)
1 | PV module | 4800 Wp | 2.9 | 13920
2 | Support structure for PV |  |  | 3800
3 | Converter (5KW) | 1 | 3500 | 3500
4 | Inverter (3.8KVA,3.2KW) | 1 | 2200 | 2200
5 | Batteries (36.96KWH) |  |  | 9240
6 | HPP(1300W) | 1 | 1500 | 1500
7 | Tr-P(836W) | 1 | 1000 | 1000
8 | Ans-P(250W) | 1 | 3000 | 3000
9 | RO Membranes | 8 | 2700 | 21600
10 | Multimedia fitter | 1 | 1200 | 1200

## Slide 22
11 | Cartridge filter | 1 | 1000 | 1000
12 | Piping (stainless steel) |  |  | 1200
13 | Valves(stainless steel) |  |  | 600
14 | Fresh water pump | 1 | 400 | 400
15 | Chemicals tank | 1 | 100 | 100
16 | Fresh water tank | 1 | 250 | 250
17 | Installation material and other accessories |  |  | 2200
18 | Civil works |  |  | 2000
Total system cost 68710$ |  |  |  | 

## Slide 23
Annual fixed charges (A fixed)
A fixed = (a) X (Capital Cost)
a=i(1+i)n\(1+i)n-1
A fixed = = 0.1X68710$ =6871$/year
Annual operating and maintenance costs (AO&M)
=206.13$/year
A operating = 7% * A fixed
= 7% * 6871($\year)
= 480.97 ($\year)
A maintenance =3% * A fixed =206.13$\year
Annual membrane replacement costs ( A replacement )
A replacement of membrane = 15% *( Membrane cost + filter cost )
= 15% *23800$=3570$\year
A replacement of battery =10%*battery cost =924$\year

## Slide 24
Unit production cost (A unit )
A unit = A total \ M * 365
=(11942.82$\year) \ (10m3\day) * (365day\year)
=3.27$\m3
A salvage =F(A\F 8%,20)=5000*0.02185=109.25$\year
Total annual cost (A total)
A total= A fixed + A replacement + Ao&m -A salvage
=11942.82$/year
Life Cycle Cost
The life cycle cost of the system = initial cost of the system + present worth of maintenance and operation and replacement – present worth of salvage value

## Slide 25: PW of salvage value =F(P\F 8%,20) =5000*0.214=1070$ The life cycle cost of the system = 102997.82$ AW = PW * (A\P i,n) = 102997.82 * 0.102 $ Energy consumption/year= average yearly power consumption/day X operating hours. =2511.6W \day* 10h * 356days =9167.3KWh\year So , The cost of 1 KWh from the PV generator (cost annuity)= =10505.77$\9167.3KWh \year = 1.15$/KWh

## Slide 26: Net Present Value Net Present Value and the Tariff For a project to be profitable the NPV must have appositive value .The greater the NPV the more profitable is the system.
Tariff: is the rate at which electrical energy is supplied to a consumer.
Assuming certain tariff ($\KWh), the total annual revenue (ART) as a result of energy sold can be calculated using the following equation:
ART= Tariff * ELT
Where, ELT: energy required for the load
NPV = (PWFC *ART) – LCC
Where , LCC: is the life cycle cost, PWFC: cumulative present worth factor
PWFC= (1-xn)\(1-x)
Where , X = 1+i /1+d
d:discount rate 8%
i: inflation rate (measure of decline in value of money) 5%
PWFC=14.3
ART=1.15$\KWh * 9167.3KWh=10505.77$
LCC = 102997.82$
NPV = (14.3* 10505.77) –102997.82=47234.691 > 0
project is profitable

## Slide 27: Conclusions
the tank capacity =10000 liter\day ,and the daily person needs of fresh water only for drinking = 4 liter\day ,so this tank enough for 2500 person.
The pressure output of the pump exit is directly proportional to the power input to the pump and the power received from the solar panel is also directly proportional to the solar irradiation.
The cost of 1KWh from PV generator =1.15$
The production cost from the PV-RO unit 3.2$\m3 which is cheap & economically viable.
1 m3 fresh water would required 480W PV peak power

## Slide 28
?