## Slide 1: " Assessment and Redesign For Establishment Of Manage & Development Orphans Funds in Ramallah City "
Prepared By:
Abdullah Adele
Ali Abu-Taha
Arif Asayra
Supervisor: Dr. Mutasim Baba
An-Najah National University Faculty of Engineering Building Engineering Department

## Slide 2: Contents
Introduction
Site analyses
Architectural aspects
Environmental aspects
Electromechanical aspects
Structure aspects
Quantity aspects

## Slide 3
Introduction
Managing and development orphans funs is an office building
Has 7 story with total area 3000 m^2.
it works all year round part-time at an average of 8 hours per day(8am-3pm).

## Slide 4
Site Analysis

## Slide 5: Site analysis
The site is located in Ramallah city in AL- Balo’o area, near bagdad street, Ramallah is about 850 m above sea level.
Area of the land 870 m2.

## Slide 6
Architectural Aspects

## Slide 7
comment | Existing Width | Standard Width | Existing area | Standard Area | Room
ok |  |  | 15m2 | (12-15) m2 | office
ok |  |  | 40 m2 | (20-30) m2 | Managers room
ok | 1.4-1.7 m | 1.4m |  |  | Corridors
ok | 1.3m | 1.3m |  |  | staircase
 |  |  | 1.65m2 | 1.6m2 | Water closet
ok |  |  | 4.5m2 | 3m2 | Kitchen
ok |  |  | 72m2 | 50-60 m2 | Meeting room

## Slide 8
Basement 1 and 2 still as they are
Basement 1
Basement 2
Architectural Aspects
Project plans

## Slide 9: Architectural Aspects
Old design for ground floor
New design for ground floor

## Slide 10: Architectural Aspects
Old design for first floor
New design for first floor

## Slide 11
Third floor
Second floor
Architectural Aspects

## Slide 12
Fifth floor
Forth floor
Architectural Aspects

## Slide 13: Architectural Aspects parking aspect
Project consents 13 parking in basements
And 22 in site.
35 and standard needs 30 parking

## Slide 14
Architectural Aspects
Project elevations
SE
NE

## Slide 15
Architectural Aspects
NW
SW

## Slide 16
Architectural Aspects
Section 1
Section 2

## Slide 17
Environmental Aspects

## Slide 18: Environmental Aspects
Shading.
Solar analysis.
Daylight.

## Slide 19: Shading
shadows from building in 21/7 at 9:00 am

## Slide 20: Shadows from building in 21/1 at 9:00 am

## Slide 21: shading on the building from others
The closest building is about 20m apart
Occur shading on the building at 3:00 pm .
From Western North

## Slide 22: shading on the building from others
The closest building is about 12m apart
Occur shading on the building after noon.
From Southern West

## Slide 23: Solar analysis
This figure show the total of solar insolation that are on the building.
In the Summer season

## Slide 24: In the Winter season:

## Slide 25: Envelope construction details for the building:
External Wall layers:
U-value =1.11 w/m2-k

## Slide 26
Internal Wall layers:

## Slide 27
Celling

## Slide 28
Lighting
Rooms that higher than range will be treated by later mentioned, while rooms with less than range will be treated with artificial lighting until we obtained the required amount of artificial and natural lighting.
Lighting analysis through the "Revit" program will be based on the principle of day light Factor, the rate of day light Factor (2% - 6%) , and we will obtain the day light factor for all room by "Revit" program, and we will compare the results before and after the simulation.

## Slide 29: These figures shown the ground floor that Lack of natural lighting in the internal rooms and staircase, and the gradual natural lighting irregular
.
before after
Before
After

## Slide 30: In the previous analysis, we have done interior glass partition, and to solve the problem of the staircase, it was made from glass to achieve natural lighting

## Slide 31: These figures shown the 5th floor that the extremely glare in the nearly of opening glass, In addition to natural lighting higher than the required.
before
after

## Slide 32: In the previous analysis we found that in some areas near the glass opening have high light and radiation, this was addressed by placing vertical louvers on the facades that are exposed to large rays, also modified the specifications of the glass by reducing the ratio of glass transparent to light. louvers, made of wood and louvers tilted on the facades at a 65-degree angle until to achieve the shading and property lighting

## Slide 33: Simulation by design builder
1- Cooling load calculation

## Slide 34: 1- Cooling load calculation

## Slide 35: 2- Heating load calculation

## Slide 36: 2- Heating load calculation

## Slide 37: 2- Heating load calculation

## Slide 38: 3- CFD

## Slide 39: 4- Total consumption Energy:

## Slide 40: Electromechanical aspect 1- HVAC system
VRF System

## Slide 41: Selection unit: The outdoor unit capacity 50 kW. The we need five outdoor units with capacity in roof of the building

## Slide 42: Collector

## Slide 43: indoor unit:

## Slide 44: Result :

## Slide 45: Distribution of Diffuser

## Slide 46
Smoke detector
Fire suppression systems
Fire hoses
Sprinkler system
Manual fire alarm station
Fire extinguishers
2-Fire safety systems

## Slide 47
Basement

## Slide 48
First Floor
Fire extinguishers

## Slide 49
The total Dfu’s = 101 Dfu’s
3- Drainage system
Calculation Of Dfu’s for our Project :
2
Drainage system pipe

## Slide 50
First Floor

## Slide 51
4- Elevators
the number of elevators that should be used in the building 2 elevators, capacity for each elevator 2500/400

## Slide 52
5-Electrical Design
Electrical
Design
Control panel
Socket Distribution
Artificial Lighting

## Slide 53
Socket Distribution

## Slide 54
In corridor
In bathroom & staircase
In office
In the Parking
Specifications of luminaires:

## Slide 55
Lighting Distribution

## Slide 58
Standards aspects
Spaces | Illuminance | Uniformity
Office | 500 | 0.6
General maneger office | 400 | 0.8
Corridor | 200 | 0.4
Bathroom | 100 | 0.6
Design
Spaces | Illuminance | Uniformity
Office | 644 | 0.55
Meeting | 457 | 0.55
Corridor | 265 | 0.6
Bedrooms | 181 | 0.47

## Slide 59: All system

## Slide 60
6-Water system

## Slide 61
Fixture type | Occupancy | Type | Weight in fixture unit | No. of units | Total (FU's)
Water closest | Public | Flush tank | 5 | 11 | 55
Lavatory | Public | Faucet | 2 | 11 | 22
Kitchen sink | Public | Faucet | 3 | 2 | 6
Total (FU's) | 83 |  |  |  | 
Total fixture unit and pipe diameters
Fixture type | Occupancy | Type | Weight in fixture unit | No. of units | Total (FU's)
Water closest | Public | Flush tank | 5 | 5 | 25
Lavatory | Public | Faucet | 2 | 7 | 14
Kitchen sink | Public | Faucet | 3 | 1 | 3
Total (FU's) | 42 |  |  |  | 

## Slide 62
Second Floor

## Slide 63
Water supply network result

## Slide 64
7- Acoustical Aspect
Acoustical Aspect
Architectural analysis
Electroacoustic design

## Slide 65
Architectural analysis
Office Plan
Frequency | 125Hz | 250Hz | 500Hz | 1000Hz | 2000Hz | 4000Hz
RT60 (second) | 1.2 | 1.1 | 0.95 | 0.81 | 0.73 | 0.78
A- Reverberation Time RT60:
Standard: 0.60 < RT60 < 1.20
B- Articulation Loss AL%
Recommended: AL % < 20 %
Frequency | 125 Hz | 250 Hz | 500 Hz | 1000 Hz | 2000 Hz | 4000 Hz
AL% | 15 | 14 | 12 | 7 | 7 | 7

## Slide 66
Gypsum board wall
C- Sound transmission class (STC) Standard = 38 dB
Block wall
D- Impact sound transmission (IIC) Standard = 40 dB
Ceiling

## Slide 67
Electroacoustic design
Corridor plan
Speaker type

## Slide 68
Speakers distribution

## Slide 69
Structural Aspects

## Slide 70
Structural Aspects
Limitation for design :
1- fc=28 MPa. For columns and shear wall and 24MPa for slabs and beams .
2- Fy= 420MPa. For all structural element of project.
3- Number of floors are 7 and Floors height= 3.65 m. and 2.8 for basements.
4- Live load = 5 𝐾𝑁/𝑚^2 .
5- SI.Dead load = 4 𝐾𝑁/𝑚^2
6- External wall load = 20 KN/m
Standards/Codes:
→ The American concrete institute code ACI 318-0.
→ The Uniform Building Code -UBC-97
for seismic design and its load combinations

## Slide 71
Structural Aspects
Slab used is one way ribbed slab.
With thickness 35cm.
And solid slab for basement 2 with thickness 25 cm
Simulation software is Etab 2016

## Slide 72
Structural Aspects
Beam used are hidden
Beam | Dimensions(mm)
Main | (900*350)
secondary | (600*350)

## Slide 73: Structural Aspects
one type of columns with dimension (600*600)

## Slide 74
Structural Aspects
Compatibility check
all members move with each other, so it is ok.
Model checks

## Slide 75
Structural Aspects
2. Equilibriums check
Equilibrium check |  |  | 
Load case | Etab | Manually | Error(%)
Dead | 27486.65 | 27061.2 | 1.54
Live | 13594.75 | 13600 | 0.03
SID | 17510.04 | 17510.1 | 0.039
Wall | 8072.14 | 7356 | 8.87
Weight of building manually should be equal Weight from Etab with percent of error less than 10%

## Slide 76
Structural Aspects
3. Stress-strain check(Columns)
Columns stress strain checks |  |  | 
Column | Etab | Manually | Error(%)
C1 | 1418.8 | 1351.024 | 4.77
C2 | 3040.4 | 2931.28 | 3.58
C3 | 4137.3 | 3754.93 | 9.24
To check the load distribution process correctly

## Slide 77
Structural Aspects
Stress-strain check(Beams)
Beams stress strain checks |  |  | 
Beam | Etab | Manually | Error(%)
B1 | 126.09 | 116.77 | 7.97
B2 | 641.14 | 603.61 | 6.21
B3 | 248.78 | 254.3 | 2.16

## Slide 78
Structural Aspects
Stress-strain check(Spans)
Spans stress strain checks |  |  | 
Span | Etab | Manually | Error(%)
span1 | 67.27 | 62.87 | 6.53
span2 | 68.71 | 62.875 | 8.49
span3 | 20.775 | 22.635 | 8.95

## Slide 79
Structural Aspects
Deflection check
Allowed limits:
Immediate Deflection = 17 mm
Long–term Deflection = 25 mm
Deflection from ETAB = 14 mm
SO , it is OK

## Slide 80
Structural Aspects
Seismic analysis
Seismic zone : 2A with (Z = 0.15)
Soil profile : SD.
Acceleration-dependent seismic coefficients Ca=0.22.
Velocity-dependent seismic coefficients Cv= 0.32.
Importance factor I=1.
Force reduction factor R=5.5

## Slide 81
Structural Aspects
Seismic load checks
Period check
T manually = 1.4*(0.0488(28) ^ (3/4)) = 0.832 sec
T etabs = 0.9 sec ok, because other checks ok.
Story | Height | Dis_x | Dis_y | Dis_x | Dis_y | Delta-x(mm) | Delta-y(mm) | Delta limit(mm)
0 |  | 0 | 0 |  |  |  |  | 
1 | 2800 | 0.119 | 0.203 | 0.119 | 0.203 | 0.45815 | 0.78155 | 56
2 | 4200 | 0.192 | 0.355 | 0.073 | 0.152 | 0.28105 | 0.5852 | 84
3 | 3640 | 2.015 | 2.082 | 1.823 | 1.727 | 7.01855 | 6.64895 | 72.8
4 | 3640 | 4.83 | 3.35 | 2.815 | 1.268 | 10.83775 | 4.8818 | 72.8
5 | 3640 | 7.788 | 6.845 | 2.958 | 3.495 | 11.3883 | 13.45575 | 72.8
6 | 3640 | 10.609 | 9.271 | 2.821 | 2.426 | 10.86085 | 9.3401 | 72.8
7 | 3640 | 13.23 | 11.68 | 2.621 | 2.409 | 10.09085 | 9.27465 | 72.8
8 | 3640 | 16.76 | 14.74 | 3.53 | 3.06 | 13.5905 | 11.781 | 72.8
ΔM (Drift) =0.7 * R * Δ s
Drift limitation = 2 % times story height.
2. Drift check

## Slide 82
3. Modal mass participate ratio check (MPMR) check
Structural Aspects
The MMPR check according to UBC code must be greater than 90% to use response spectrum analysis.
Case | Mode | Period | UX | UY | Sum UX | Sum UY
 |  | sec |  |  |  | 
Modal | 29 | 0.035 | 0.0216 | 0.1028 | 0.765 | 0.8657
Modal | 30 | 0.033 | 0.0935 | 0.0336 | 0.8585 | 0.8993
Modal | 31 | 0.032 | 0.0408 | 0.0019 | 0.8993 | 0.9011
Modal | 32 | 0.031 | 0.0106 | 0.0023 | 0.9099 | 0.9035
Modal | 33 | 0.03 | 0.0001 | 4.87E-06 | 0.91 | 0.9035
Modal | 35 | 0.028 | 0.0004 | 0.0001 | 0.9112 | 0.9042

## Slide 83
4. Base shear check
Structural Aspects
Axis | T | T_LIMIT | T_used | V_mannual | V_Etab | Old Scale factor | New ,S.F
X | 1.028 | 0.84 | 0.84 | 3627.84814 | 2413.516 | 1783 | 2681
Y | 0.854 | 0.84 | 0.84 | 3627.84814 | 2927.375 | 1783 | 2210
For this check make sure base shear from response spectrum cases equal or more than base shear from equivalent static method through modifying scale factor.

## Slide 84
Design of structural elements
Structural Aspects
1. Slabs :
Ribbed slab
Solid slab

## Slide 85
Structural Aspects
Design of structural elements
1. Slabs :

## Slide 86
Structural Aspects
Design of structural elements
1. Slabs :

## Slide 87
Structural Aspects
Design of structural elements
2. Beams :
beam | positin | As | As(min) | As used | Bar used | Area bar | # of bars | spacing
M.B.2 | (-) left | 1858 | 899.1 | 1858 | 16 | 200.96 | 10 | 76
 | (+) | 1157 | 899.1 | 1157 | 16 | 200.96 | 6 | 149
 | (-) right | 2187 | 899.1 | 2187 | 16 | 200.96 | 11 | 67

## Slide 88
Structural Aspects
Design of structural elements
3. Columns:
12∅20
3∅10/15cm

## Slide 89
Structural Aspects
Design of structural elements
4. Shear walls

## Slide 90
Structural Aspects
Design of structural elements
4. Mat foundation

## Slide 91
Structural Aspects
Design of structural elements
4. Mat foundation

## Slide 92
Structural Aspects
Design of structural elements
5. Staires

## Slide 93
Cost Estimation
Project Total cost = 3,380,980 NIS .
Project total area = 3000 m^2
Cost /unit = 1127 NIS / M^2