## Slide 1: An-Najah National University Building Engineering Department
Design of Primary School
Presented By: Supervisor:
Mohammad Ghannam Eng. Fadi Fatayer
Obadah Hamdan
Mousa Al-Atrash Date: May 20, 2019

## Slide 2: Presentation Outline
Architectural Design
Structural Design
Environmental Design
Mechanical Design
Safety and Security Design
Radial Design
Electrical Design
Quantity Surveying and Cost Estimation

## Slide 3: Architectural Design

## Slide 4: Architectural Spaces (Ground Floor)
Space | Number | Area
Teachers Room | 1 | 75
W.C 1 | 1 | 18
W.C 2 | 1 | 22
Multipurpose Hall | 1 | 118
Meeting Room | 1 | 48
W.C 3 | 1 | 38
Kitchen | 1 | 10
Manager Room | 1 | 5
Secretary Room | 1 | 15
Reception | 1 | 12
Classroom | 3 | 26

## Slide 5: Architectural Spaces (First Floor)
Space | Number | Area
Initiative room | 1 | 75
W.C 1 | 1 | 18
W.C 2 | 1 | 22
Library | 1 | 118
Cafeteria | 1 | 48
Classroom | 3 | 46
Science Lab | 1 | 76

## Slide 6: Architectural Spaces (Second Floor)
Space | Number | Area
Initiative room | 1 | 75
W.C 1 | 1 | 18
W.C 2 | 1 | 22
Cafeteria | 1 | 48
Classroom | 3 | 46
Computer Lab | 1 | 76

## Slide 7: Architectural Spaces (Third Floor)
Space | Number | Area
Initiative room | 1 | 75
W.C 1 | 1 | 18
W.C 2 | 1 | 22
Cafeteria | 1 | 48
Classroom | 3 | 46
Art Room | 1 | 76

## Slide 8: Site Plan

## Slide 9: Ground Floor

## Slide 10: First Floor

## Slide 11: Second Floor

## Slide 12: Third Floor

## Slide 13: Western Elevation

## Slide 14: Eastern Elevation

## Slide 15: Northern Elevation

## Slide 16: Southern Elevation

## Slide 17: Section A-A

## Slide 18: Section B-B

## Slide 23: Structural Design

## Slide 24: Codes and Structural System
Codes
ACI 318-14 for reinforced concrete design
UBC 97 for seismic design and its load combinations
ASCE 7 for load combinations
Structural System
One Way Ribbed Slab

## Slide 25: Structural Design Data
Loads
Dead Loads
Superimposed Load = 6.2 kN/m2
Live Load = 5 kN/m2
Wall Load = 26.2 kN/m2
Seismic Load
Materials
Compressive Strength of Concrete = 24 MPa
Yield Strength of Steel= 420 MPa
Soil Bearing Capacity = 250 kN/m2

## Slide 26: Structural Design Data
Sections Dimensions
Member | Width | Depth
Slab | 30 cm Thickness | 
Main Beam (Group One) | 70 cm | 60 cm
Main Beam (Group Two) | 75 cm | 35 cm
Secondary Beam | 45 cm | 30 cm
Column | 60 cm | 40 cm
Shear Wall | 30 cm Thickness | 

## Slide 27: Structural Design Data
Seismic Analysis Parameters
Seismic Zone: 2B (Z=0.2)
Soil Profile: Sc
Acceleration Seismic Coefficients Ca = 0.24
Velocity Seismic Coefficient Cv = 0.32
Importance Factor I = 1.5
Force Reduction Factor R = 5.5

## Slide 28: Building Blocks

## Slide 29: Model Checking
Compatibility Check (Block 1)

## Slide 30: Model Checking
Compatibility Check (Block 2)

## Slide 31: Model Checking
Compatibility Check (Block 3)

## Slide 32: Model Checking
Equilibrium Check (Block 1)
Load | Manual (kN) | ETABS (kN) | Error % | Assessment
Dead Load | 10940 | 10479 | 4.39 % | OK
Live Load | 4513.6 | 4553.96 | 0.88 % | OK
Superimposed Load | 11285.5 | 11113.8 | 1.5 % | OK

## Slide 33: Model Checking
Equilibrium Check (Block 2)
Load | Manual (kN) | ETABS (kN) | Error % | Assessment
Dead Load | 10009.8 | 10408.04 | 3.86 % | OK
Live Load | 6327.6 | 6225.6 | 0.13 % | OK
Superimposed Load | 14069.4 | 14018.045 | 0.36 % | OK

## Slide 34: Model Checking
Equilibrium Check (Block 3)
Load | Manual (kN) | ETABS (kN) | Error % | Assessment
Dead Load | 12973.6 | 13168 | 1.4 % | OK
Live Load | 6397 | 7112.22 | 2.4 % | OK
Superimposed Load | 15283.1 | 14633 | 4.4 % | OK

## Slide 35: Model Checking
Internal Forces Check (Block 1)
Element | Manual (kN.m) | ETABS (kN.m) | Error % | Assessment
Beam 1 | 311 | 288.2 | 7.9 % | OK
Beam 2 | 748.8 | 720.9 | 3.9 % | OK
Column 1 | 417.19 | 397.9 | 4.8 % | OK
Column 2 | 2324.34 | 2492.23 | 6.75 % | OK
Slab 1 | 32.18 | 33.1 | 2.7 % | OK

## Slide 36: Model Checking
Internal Forces Check (Block 2)
Element | Manual (kN.m) | ETABS (kN.m) | Error % | Assessment
Beam 1 | 205.9 | 188.8 | 9 % | OK
Beam 2 | 838.9 | 759.2 | 4 % | OK
Column 1 | 955.9 | 959.3 | 0.44 % | OK
Column 2 | 1760.8 | 1813.5 | 2.9 % | OK
Slab 1 | 32.18 | 27.4 | 5.5 % | OK

## Slide 37: Model Checking
Internal Forces Check (Block 3)
Element | Manual (kN.m) | ETABS (kN.m) | Error % | Assessment
Beam 1 | 1006.8 | 944.5 | 1.3 % | OK
Beam 2 | 643.7 | 663 | 2 % | OK
Column 1 | 1012.2 | 1034.3 | 2.17 % | OK
Column 2 | 2854.4 | 2778.1 | 2.75 % | OK
Slab 1 | 1719.4 | 1674.5 | 2.7 % | OK

## Slide 38: Model Checking
Deflection Check
Block No. | Deflection (mm) | Limit (mm) | Assessment
Block 1 | 9.37 | 33.6 | OK
Block 2 | 20.5 | 34.88 | OK
Block 3 | 30.34 | 41.33 | OK

## Slide 39: Model Checking
Period Check
Block No. | TManual (sec) | TETABS (sec) | Assessment
Block 1 | 0.597 | 0.729 | OK (Small Difference)
Block 2 | 0.597 | 0.572 | OK (TETABS < TManual)
Block 3 | 0.597 | 0.767 | OK (Small Difference)

## Slide 40: Model Checking
Base Shear Check
Block No. | Base Shear | Manual (kN) | ETABS (kN) | Assessment
Block 1 | Vx | 4145.8 | 4156.01 | V Manual < V ETABS OK
 | Vy | 4331.6 | 4331.6 | V Manual ≤ V ETABS OK
Block 2 | Vx | 4204.4 | 4204.41 | V Manual ≤ V ETABS OK
 | Vy | 4512.76 | 4729.38 | V Manual < V ETABS OK
Block 3 | Vx | 4602.7 | 4602.72 | V Manual ≤ V ETABS OK
 | Vy | 5152.1 | 5243.5 | V Manual < V ETABS OK

## Slide 41: Model Checking
Drift Check
Block No. | Story | Δmx (mm) | Δmy (mm) | Limitation (mm) | Assessment
Block 1 | GF | 6.0 | 28.1 | 90 | OK
 | F1 | 3.6 | 13.9 | 90 | OK
 | F2 | 7.7 | 19.2 | 90 | OK
 | F3 | 8.1 | 17.3 | 90 | OK
Block 2 | GF | 5.1 | 4.5 | 90 | OK
 | F1 | 8.4 | 8.1 | 90 | OK
 | F2 | 10.7 | 10.4 | 90 | OK
 | F3 | 10.4 | 10.5 | 90 | OK
Block 3 | GF | 20.7 | 2.6 | 90 | OK
 | F1 | 31.8 | 4.0 | 90 | OK
 | F2 | 28.7 | 12.5 | 90 | OK
 | F3 | 32.8 | 9.1 | 90 | OK

## Slide 42: Design and Reinforcement
Slab Layout (Block 1)

## Slide 43: Design and Reinforcement
Slab Layout (Block 2)

## Slide 44: Design and Reinforcement
Slab Layout (Block 3)

## Slide 45: Design and Reinforcement
Slab Detailing

## Slide 46: Design and Reinforcement
Column Detailing

## Slide 47: Design and Reinforcement
Beam Detailing

## Slide 48: Design and Reinforcement
Footing Detailing

## Slide 49: Environmental Design

## Slide 50: Thermal Design
U-Value for Building Envelope
Component | U-value (W/m2.k)
External Wall | 0.491
Internal Wall | 1.188
Floor | 0.508
Roof | 0.456
Windows | 1.761

## Slide 51: Thermal Design
3D Model in DesignBuilder

## Slide 52: Thermal Design
Shading
Louvers System

## Slide 53: Thermal Design
Shading
In Summer Day
21 June at 8 AM
21 June at 12 PM

## Slide 54: Thermal Design
Shading
In Winter Day
21 January at 8 AM
21 January at 12 PM

## Slide 55: Thermal Design
Comfort PMV-Set

## Slide 56: Thermal Design
 | Total energy (kWh) | Energy per total building area (kWh/m2) | Energy per conditioned building area (kWh/ m2)
Total Site Energy | 985766.94 | 57.75 | 57.75
Net Site Energy | 985766.94 | 57.75 | 57.75
Total Source Energy | 239653.31 | 114.52 | 114.52
Net Source Energy | 239653.31 | 114.52 | 114.52
Heating and Cooling Loads
Total Cooling Load = 131.44 kW
Total Heating Load = 130.72 kW
Site and Source Energy

## Slide 57: Thermal Design
Comfort and Setpoint Not Met Summery
 | Facility (Hrs)
Time setpoint not met during occupied heating | 70
Time setpoint not met during occupied cooling | 65
Time not comfortable based on simple ASHREAE 55-2004 | 750

## Slide 58: Acoustical Design
Absorption Coefficient
Element | Finish Material | Absorption Coefficient (α) |  |  |  |  |  |  |  | 
 |  | 63 Hz | 125 Hz | 250 Hz | 500 Hz | 1000 Hz | 2000 Hz | 4000 Hz | 8000 Hz | 16000 Hz
Walls | Plaster | 0.03 | 0.04 | 0.05 | 0.06 | 0.08 | 0.04 | 0.06 | 0.05 | 0.06
Floor | Tile | 0.01 | 0.02 | 0.06 | 0.14 | 0.37 | 0.6 | 0.65 | 0.6 | 0.7
Roof | Plaster Decorative Panels | 0.1 | 0.2 | 0.22 | 0.18 | 0.15 | 0.15 | 0.16 | 0.15 | 0.16
Doors | Hollow Core Plywood | 0.44 | 0.41 | 0.35 | 0.25 | 0.2 | 0.15 | 0.15 | 0.13 | 0.12
Windows | Double Glaze 6 mm | 0.12 | 0.10 | 0.06 | 0.04 | 0.03 | 0.03 | 0.03 | 0.04 | 0.04

## Slide 59: Acoustical Design
Ecotect Model

## Slide 60: Acoustical Design
Room | Room Volume (m3) | Occupancy | RT60 Range (At 500 Hz) | Recommended Range | Assessment
Classroom | 231.76 | 30 | 0.51 – 0.57 | 0.4 – 0.8 | OK
Teachers Room | 373.75 | 22 | 0.63 – 0.67 | 0.4 – 0.7 | OK
Manager Room | 82.20 | 2 | 0.55 – 0.56 | 0.4 – 0.6 | OK
Meeting Room | 194.11 | 25 | 0..50 – 0.56 | 0.4 – 0.7 | OK
Multipurpose Hall | 585.13 | 66 | 1.48 – 1.81 | 1.4 – 1.9 | OK
Science Lab | 370.92 | 32 | 0.60 – 0.65 | 0.4 – 0.7 | OK
Reverberation Time (RT60)

## Slide 61: Acoustical Design
Type | STC Value (dB) | Assessment
Classroom External Wall (Without Windows) | 44 | OK
Classroom External Wall (With Windows) | 39 | OK
Library External Wall (Without Windows) | 44 | OK
Library External Wall (With Windows) | 38 | OK
Wall (Between Classroom and Corridor) | 39 | OK
Wall (Between Classroom and other Classroom) | 40 | OK
Wall (Between Manager Room and Secretary Room) | 40 | OK
Sound Transmission Class (STC)

## Slide 62: Acoustical Design
Impact Insulation Class (IIC)
Type | IIC Value (dB) | Assessment
Floor | 46 | OK
Art Room Roof | 69 | OK

## Slide 63: Acoustical Design
Loud Speakers
Used Type: PRO-180RPC In-ceiling Speakers

## Slide 64: Acoustical Design
Speakers Distribution in Corridors

## Slide 65: Acoustical Design
Speakers Distribution in Cafeteria and Multipurpose Hall
Cafeteria
Multipurpose Hall

## Slide 66: Mechanical Design

## Slide 67: Water Supply System
 | Ground Floor | First Floor | Second Floor | Third Floor
Number of F.U in Zone 1 | 36 | 32 | 32 | 32
Number of F.U in Zone 2 | 44.5 | 41.5 | 27 | 27
Number of F.U in Floor | 81.5 | 73.5 | 59 | 59
Total F.U in All Floors = 273 |  |  |  | 
Fixture Unit

## Slide 68: Water Supply System
 | Ground Floor | First Floor | Second Floor | Third Floor
Vertical pipes | 2″ | 2″ | 2.5″ | 3″
Horizontal pipes | 1″ | 1″ | 1.5″ | 1.5″
Branches pipes | 0.75″ | 0.75″ | 1″ | 1″
Total losses | 9 | 4.6 | 0.88 | 0.75
Allow losses | 13.9 | 7.9 | 1.47 | 0.8 Psi (Use pump 6 Psi)
Assessments | OK | OK | OK | OK
Pipes Diameter and Losses

## Slide 69: Water Supply System
Water Supply System Plan (Third Floor)

## Slide 70: Drainage System
Floor | No. of Fixtures | DFU
Ground Floor | 13 W.C, 6 Lav, 2 Kitchen, 10 Drinking | 45 W.C, 6 Lav, 4 Kitchen, 5 Drinking
First Floor | 11 W.C, 11 Lav, 10 Drinking | 44 W.C, 11 Lav, 5 Drinking
Second Floor | 11 W.C, 5 Lav | 44 W.C, 5 Lav
Third Floor | 11 W.C, 5 Lav | 44 W.C, 5 Lav
Total | 46 W.C, 27 Lav, 2 Kitchen , 20 Drinking | 177 W.C, 27 Lav, 4 Kitchen, 10 Drinking
Total DFU`s = 218 |  | 
Total DFU’s

## Slide 71: Drainage System
Information about pipes in the system
Pipe | Diameter | Slope | Type of Pipe
Vent | 4" | 0%(90°) | PVC
Drainage | 4" | 1% | PVC
Stack | 4" | 0%(90°) | PVC
Sewer | 2" | 1% | PVC

## Slide 72: Drainage System
Manholes Plan

## Slide 73: Drainage System
Rain Water Plan

## Slide 74: Elevators Design
Required Number N' = 2
Car Capacity = 2500 lb.
Car Speed = 350 fpm.
Car Passenger Capacity P = 13

## Slide 75: Elevators Design
Elevators Location

## Slide 76: Safety and Security Design

## Slide 77: Firefighting System
Fire Extinguishers
Hose Stations
Sprinklers

## Slide 78: Firefighting System
Automatic Sprinkler System
Level Hazard and Coverage Area
Hazard | Low | Moderate | High
Coverage area (m2) | 21 m2 | 12 m2 | 9.3 m2
Distance (m) | 4.6 m | 3.6 m | 3.6 m

## Slide 79: Firefighting System
Sprinkler Distribution in Library

## Slide 80: Emergency Fire Protection System
Fire Fighting Systems Plan (Ground Floor)

## Slide 81: Emergency Egress System
Emergency Stairs

## Slide 82: Emergency Egress System
Emergency Exit Signs

## Slide 83: Emergency Egress System
Emergency Exit Signs in Ground Floor

## Slide 84: Emergency Egress System
Emergency Egress Route in Third Floor

## Slide 85: Radial Design

## Slide 86: Radial System
Radiator Selection
Used Type: Soft line H P+-Brag box from Stelrad Company

## Slide 87: Radial System
Radiators and Power in Each Floor
Floor | Number of Radiators | Actual Qrad (Watt)
Ground Floor | 39 | 52734
First Floor | 24 | 32963
Second Floor | 25 | 32692
Third Floor | 25 | 34169

## Slide 88: Radial System
Radiators Distribution in Ground Floor

## Slide 89: Radial System
Radiators Distribution in First Floor

## Slide 90: Radial System
Radiators Distribution in Second Floor

## Slide 91: Radial System
Radiators Distribution in Third Floor

## Slide 92: Electrical Design

## Slide 93: Lighting Design
Daylight Factor
Facility | Standard DF % | Average DF in School % | Decision
Classroom | 2 – 4 | 2.474 | OK
Computer lab | 3 – 5 | 3.197 | OK
Library | 3 – 5 | 3.2 | OK
Teachers room | 2 – 4 | 2.3 | OK
Meeting room | 2 – 4 | 3.84 | OK
Manager room | 2 – 4 | 4 | OK
Multipurpose | 3 – 5 | 3.67 | OK
Cafeteria | 3 – 5 | 3.49 | OK

## Slide 94: Lighting Design
Luminaires Types

## Slide 95: Lighting Design
Illuminance
Room | Illuminance (Lux) | UGR
Classroom | 464 | OK
Library | 437 | OK
Computer Lab | 436 | OK
Manager Room | 275 | OK
Teachers Room | 303 | OK
Cafeteria | 382 | OK
Meeting Room | 313 | OK
Multipurpose Hall | 422 | OK
Initiative Classroom | 345 | OK

## Slide 96: Lighting Design
3D Rendering from DIALux
Classroom
Library
Computer Lab

## Slide 97: Lighting Design
3D Rendering from DIALux
Manager Room
Teachers Room
Cafeteria

## Slide 98: Lighting Design
3D Rendering from DIALux
Meeting Room
Multipurpose Hall
Initiative Classroom

## Slide 99: Lighting Design
Luminaires Distribution
Classroom
Library

## Slide 100: Lighting Design
Luminaires Distribution
Computer Lab
Manager Room
Teachers Room

## Slide 101: Lighting Design
Luminaires Distribution
Cafeteria
Meeting Room

## Slide 102: Lighting Design
Luminaires Distribution
Multipurpose Hall
Initiative Classroom

## Slide 103: Lighting Design
Lighting Power
Floor | Total Power Lighting (W) | Total Loads (amp)
Ground floor | 4043.1 | 88
First floor | 3719.1 | 76
Second floor | 3179.1 | 120
Third floor | 3179.1 | 58
Total | 14111.4 | 342

## Slide 104: Electrical Loads
Power Plan (Third Floor)

## Slide 105: Electrical Loads
Main Distribution board (Second Floor)

## Slide 106: Electrical Loads
Distribution board for UPS (Second Floor)

## Slide 107: Quantity Surveying and Cost Estimation

## Slide 108: Cost Estimation
Total Direct Project Cost | 5,540,958
Total Building Area = 3150 m2
Direct Unit Cost = 5540958/3150
= 1759 NIS/m2
Direct Unit Cost = 350 JOD/m2

## Slide 109: Done! Thanks a Lot